{"text_format":"3","workbook":"xls","n_sheets":5,"sheets":["cover","Introduction","C7000 common","C7000IOC","C7000AT"],"not_rendered":{"images":1,"macros":1,"external_links":1,"defined_names":35,"comments":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"cover","index":0,"n_rows":48,"n_cols":1,"rows_kept":48,"flags":["formulas_cached_only"]}
[]
[]
[]
[" "]
[" "]
[]
[]
[]
[]
[]
[]
["GmbH Klimatechnik"]
[]
["StulzComptrolProtocol"]
[]
["universal-datapoint-list"]
{"$rows_empty":30}
["Release V1.14beta"]
[">2005 February 16th"]

{"sheet":"Introduction","index":1,"n_rows":24,"n_cols":1,"rows_kept":24,"flags":["formulas_cached_only"]}
[]
["This document describes a universal datapointlist."]
["The goal is to establish a few commands in stulz-protocol to read and write all the data."]
["The commands should allow to read a definable block of several values (similar to MODBUS), instead only one or a fixed block."]
["The adressing should respect the grown architecture of the different controller systems (mibs, units, modules)."]
["Maybe it can be a hierarchical adressing; and an intrinsic node is adressed by 0s in the lower-level parts or by a relevance-mask."]
["Checksum and password (variable format) should be part of the commands. "]
["Maybe the adress can have variable length and password is included there if necessary/desired."]
["It should be evaluated, if it is useful to fit it in the OSI-stack to avoid overhead in low-level-systems."]
["Adressing can be done by one length-byte and the following bytes. Each following byte contains the adress of one level."]
["E.g. an IO-board of C6000 is adressed with 4bytes for the length, MIB, Controller and itself."]
["For broadcasting the value 255 should be used for the byte of that level."]
["U.u. ist es sinnvoll neben der Unterscheidung analoge/digitale Daten, auch noch eine Kategorie Ganzzahldaten einzufuegen (integer, float, bit) !?"]
["The datapointlist now contains all relevant data, but must be tidied a little."]
[]
["The combined list uses a different concept: It is organised in bytes strictly; i.e. each data must be adressed in bytes."]
["Requests can ask for other datatypes to make it easier to calculate the requested number, Subadress for the bit can be used in bit-requests."]
["The meaning can be different and has to be interpreted by the type-information etc."]
[]
["For desired actions there should not be special commands but only determined adresses (digital datapoints for actions/status)."]
[]
[]
[]
["So far, nothing has been implemented!"]

{"sheet":"C7000 common","index":2,"n_rows":5048,"n_cols":15,"rows_kept":5048,"flags":["formulas_cached_only"]}
["These datapoint-adresses (0..999) should be equally used in all different unit-types!!"]
[{"$nulls":3}," ",null,"input","word",null,null,"r","r"]
[{"$nulls":3}," ",null,"output","byte",null,null,"w","w"]
[{"$nulls":3}," ",null,"internal","bit",null,null,"rw","rw"]
[{"$nulls":3}," ",null,null,"string",null,null,"--","--"]
[{"$nulls":3}," ",null,null,"float"]
[null,"DP-","( Bit-)sub-","MODBUS-",null,null,"data-",null,null,"bus-","BMS-"]
[null,"Adress","adress","Adresse","Description","source-type","type","allowed range","mapped meaning","access","access","comment","menus in AT","Modbus-function","WIB-Access"]
[null,0," ",0,"hardware type (controller type)","internal","byte","--","--","r","r","C6000, C7000AT etc.","Overview; Info->system","3, (4)","r"]
[null,1," ",2,"unit-type","internal","byte","0-255","see comment","r","r","DX, CW, GE, Ecocool, etc","Info->system","3, (4)","r"]
[null,2," ",4,"HW-version","internal","byte",null,null,"r","r","just a revision-ID (e.g V1.00)","Info->system","3, (4)"]
[null,3," ",6,"SW-version","internal","word",null,null,"r","r","just a revision-ID (e.g V1.00)","Info->system","3, (4)","r"]
[null,4," ",8,"number of modules","internal","byte","--","--","--","--","used in old units","not available",null,"--"]
[null,5," ",10,"Bus-ID","internal","byte","0..31","0..31","rw","r",null,"statusline","3, (4)","r"]
[null,6," ",12,"global adress","internal","word","whole","positve","rw","r",null,"statusline","3, (4)","rw"]
[null,7," ",14]
[null,8,0,8,"general error","internal","bit","0/1","ok/error","r","r","substitutes red LED","LED, flash. Icon in overview","1, (2)"]
[null,9,0,9,"error on bus","internal","bit","0/1","ok/error","r","--","at least one of the busmembers has an error"]
[null,10,0,10,null,null,"bit","0/1"]
[null,11,0,11,null,null,"bit","0/1"]
[null,12,0,12,null,null,"bit","0/1"]
[null,13,0,13,null,null,"bit","0/1"]
[null,14,0,14,null,null,"bit","0/1"]
[null,15,0,15,null,null,"bit","0/1"]
[null,16," ",32]
[null,17," ",34]
[null,18," ",36]
[null,19," ",38]
[null,20," ",40]
[null,21," ",42]
[null,22," ",44]
[null,23," ",46]
[null,24," ",48]
[null,25," ",50]
[null,26," ",52]
[null,27," ",54]
[null,28," ",56]
[null,29," ",58]
[null,30," ",60]
[null,31," ",62]
[null,32," ",64]
[null,33," ",66]
[null,34," ",68]
[null,35," ",70]
[null,36," ",72,"iobus type of unit 0","internal","byte",null,null,"r","--"]
[null,37," ",74,"iobus type of unit 1","internal","byte",null,null,"r","--"]
[null,38," ",76,"iobus type of unit 2","internal","byte",null,null,"r","--"]
[null,39," ",78,"iobus type of unit 3","internal","byte",null,null,"r","--"]
[null,40," ",80,"iobus type of unit 4","internal","byte",null,null,"r","--"]
[null,41," ",82,"iobus type of unit 5","internal","byte",null,null,"r","--"]
[null,42," ",84,"iobus type of unit 6","internal","byte",null,null,"r","--"]
[null,43," ",86,"iobus type of unit 7","internal","byte",null,null,"r","--"]
[null,44," ",88,"iobus type of unit 8","internal","byte",null,null,"r","--"]
[null,45," ",90,"iobus type of unit 9","internal","byte",null,null,"r","--"]
[null,46," ",92,"iobus type of unit 10","internal","byte",null,null,"r","--"]
[null,47," ",94,"iobus type of unit 11","internal","byte",null,null,"r","--"]
[null,48," ",96,"iobus type of unit 12","internal","byte",null,null,"r","--"]
[null,49," ",98,"iobus type of unit 13","internal","byte",null,null,"r","--"]
[null,50," ",100,"iobus type of unit 14","internal","byte",null,null,"r","--"]
[null,51," ",102,"iobus type of unit 15","internal","byte",null,null,"r","--"]
[null,52," ",104,"iobus type of unit 16","internal","byte",null,null,"r","--"]
[null,53," ",106,"iobus type of unit 17","internal","byte",null,null,"r","--"]
[null,54," ",108,"iobus type of unit 18","internal","byte",null,null,"r","--"]
[null,55," ",110,"iobus type of unit 19","internal","byte",null,null,"r","--"]
[null,56," ",112,"iobus type of unit 20","internal","byte",null,null,"r","--"]
[null,57," ",114,"iobus type of unit 21","internal","byte",null,null,"r","--"]
[null,58," ",116,"iobus type of unit 22","internal","byte",null,null,"r","--"]
[null,59," ",118,"iobus type of unit 23","internal","byte",null,null,"r","--"]
[null,60," ",120,"iobus type of unit 24","internal","byte",null,null,"r","--"]
[null,61," ",122,"iobus type of unit 25","internal","byte",null,null,"r","--"]
[null,62," ",124,"iobus type of unit 26","internal","byte",null,null,"r","--"]
[null,63," ",126,"iobus type of unit 27","internal","byte",null,null,"r","--"]
[null,64," ",128,"iobus type of unit 28","internal","byte",null,null,"r","--"]
[null,65," ",130,"iobus type of unit 29","internal","byte",null,null,"r","--"]
[null,66," ",132,"iobus type of unit 30","internal","byte",null,null,"r","--"]
[null,67," ",134,"iobus type of unit 31","internal","byte",null,null,"r","--"]
[null,68," ",136,"iobus reliability of unit 0","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,69," ",138,"iobus reliability of unit 1","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,70," ",140,"iobus reliability of unit 2","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,71," ",142,"iobus reliability of unit 3","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,72," ",144,"iobus reliability of unit 4","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,73," ",146,"iobus reliability of unit 5","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,74," ",148,"iobus reliability of unit 6","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,75," ",150,"iobus reliability of unit 7","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,76," ",152,"iobus reliability of unit 8","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,77," ",154,"iobus reliability of unit 9","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,78," ",156,"iobus reliability of unit 10","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,79," ",158,"iobus reliability of unit 11","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,80," ",160,"iobus reliability of unit 12","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,81," ",162,"iobus reliability of unit 13","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,82," ",164,"iobus reliability of unit 14","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,83," ",166,"iobus reliability of unit 15","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,84," ",168,"iobus reliability of unit 16","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,85," ",170,"iobus reliability of unit 17","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,86," ",172,"iobus reliability of unit 18","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,87," ",174,"iobus reliability of unit 19","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,88," ",176,"iobus reliability of unit 20","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,89," ",178,"iobus reliability of unit 21","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,90," ",180,"iobus reliability of unit 22","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,91," ",182,"iobus reliability of unit 23","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,92," ",184,"iobus reliability of unit 24","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,93," ",186,"iobus reliability of unit 25","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,94," ",188,"iobus reliability of unit 26","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,95," ",190,"iobus reliability of unit 27","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,96," ",192,"iobus reliability of unit 28","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,97," ",194,"iobus reliability of unit 29","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,98," ",196,"iobus reliability of unit 30","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,99," ",198,"iobus reliability of unit 31","internal","byte","0..255","MSB:latest;LSB:oldest","r","r","implemented as shift-register"]
[null,100," ",200,"iobus state of unit 0","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,101," ",202,"iobus state of unit 1","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,102," ",204,"iobus state of unit 2","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,103," ",206,"iobus state of unit 3","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,104," ",208,"iobus state of unit 4","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,105," ",210,"iobus state of unit 5","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,106," ",212,"iobus state of unit 6","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,107," ",214,"iobus state of unit 7","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,108," ",216,"iobus state of unit 8","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,109," ",218,"iobus state of unit 9","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,110," ",220,"iobus state of unit 10","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,111," ",222,"iobus state of unit 11","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,112," ",224,"iobus state of unit 12","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,113," ",226,"iobus state of unit 13","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,114," ",228,"iobus state of unit 14","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,115," ",230,"iobus state of unit 15","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,116," ",232,"iobus state of unit 16","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,117," ",234,"iobus state of unit 17","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,118," ",236,"iobus state of unit 18","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,119," ",238,"iobus state of unit 19","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,120," ",240,"iobus state of unit 20","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,121," ",242,"iobus state of unit 21","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,122," ",244,"iobus state of unit 22","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,123," ",246,"iobus state of unit 23","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,124," ",248,"iobus state of unit 24","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,125," ",250,"iobus state of unit 25","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,126," ",252,"iobus state of unit 26","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,127," ",254,"iobus state of unit 27","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,128," ",256,"iobus state of unit 28","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,129," ",258,"iobus state of unit 29","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,130," ",260,"iobus state of unit 30","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,131," ",262,"iobus state of unit 31","internal","byte","0..1","PASSIVE/ACTIVE","r","r","not of type bit to allow further states in future"]
[null,132," ",264]
[null,"..."," ",2]
[null,999," ",1998]
{"$rows_empty":2452}
["DP8500..DP11699 formerly defined for sequencing data, but never implemented => reusable"]
[]
[]
[null,8500]
[null,8501]
{"$rows_empty":2447}
[{"$nulls":4},"emergency operation active"]

{"sheet":"C7000IOC","index":3,"n_rows":4131,"n_cols":18,"rows_kept":4131,"flags":["formulas_cached_only"]}
[{"$nulls":3}," ",null,"input","word",{"$nulls":3},"r","r","read only",null,null,"r","r"]
[{"$nulls":3}," ",null,"output","byte",{"$nulls":3},"w","w","write only",null,null,"w","w"]
[{"$nulls":3}," ",null,"internal","bit",{"$nulls":3},"rw","rw","read and write",null,null,"rw","rw"]
[{"$nulls":3}," ",null,"redirected input","string20",{"$nulls":3},"--","--","no access allowed",null,null,"--","--"]
[{"$nulls":3}," ",null,"redirected output","float",{"$nulls":3},"r(w0)","r(w0)","readable and resetting allowed",null,null,"r(w0)","r(w0)"]
[null,"DP-","( Bit-)sub-","MODBUS-","C7000IOC",null,"data-",null,"allowed",null,"bus-","BMS-",null,null,"Modbus-"]
[null,"Adress","adress","Adresse","Description","source-type","type",null," range","mapped meaning","access","access","comment","menus in AT","Functions","WIB Access","WIB am 01.03.","Problem?"]
[null,0," ",0]
[{"$nulls":3}," ","see combined list C7000 common"]
[null,999,null,1998]
[null,null," "," "]
[null,1000," ",1000,"PC-STOP (monitoring)","internal(bus)","bit","PC- STOP （监测）","0 / 1","maybe on / unit off","rw","rw",null,"statusline","1, (2), 5","rw","rw"]
[null,1001,1,1001,"REMOTE STOP (contact)","internal(input)","bit","远程STOP （接触）","0 / 1","maybe on / unit off","r","r",null,"statusline","1, (2)","r","r"]
[null,1002,2,1002,"LOCAL STOP ","internal(key)","bit","LOCAL STOP","0 / 1","maybe on / unit off","rw","r","write access is used, if red on-off-key is pressed","statusline","1, (2)","r","r"]
[null,1003,3,1003,"TIMER-STOP (weekly oper.)","internal","bit","TIMER -STOP（每周歌剧院）。","0 / 1","maybe on / unit off","r","r",null,"statusline","1, (2)","r","r"]
[null,1004,4,1004,"SEQ. Stop (0=No, 1=Yes)","internal","bit","SEQ 。停止（0 =否，1 =是）","0 / 1","maybe on / unit off","rw","r",null,"statusline","1, (2)","r"]
[null,1005,5,1005,"WARM UP STOP","internal","bit","热身停止","0 / 1","maybe on / unit off","r","r","only valid with CW-Systems ","statusline","1, (2)","r","r","not accessible, TMO"]
[null,1006,6,1006,"Remote UPS","internal(bus)","bit","远程UPS","0 / 1","inactive/active","rw","rw",null,"statusline","1, (2), 5"]
[null,1007,7,1007,"Local UPS","internal(input)","bit","本地UPS","0 / 1","inactive/active","r","r",null,"statusline","2, (1)","r","r"]
[null,1008,0,1008,"G/CW-mode; G:1, CW:0","internal","bit","G / CW模式; G：1 ，CW： 0","0 / 1","CW/G","r","r",null,"statusline","1, (2), 5","r","r","not accessible, TMO"]
[null,1009,1,1009,"manual operation","internal","bit","手动操作",0,"reset","w","w","writing 0 resets manop-activations of all components","statusline",5,null,null,"not accessible"]
[null,1010,2,1010,"common alarm","internal","bit","常见的报警","0 / 1","no alarm / alarm","r","r",null,"LED","2, (1)","r","r"]
[null,1011,3,1011,"reset all alarms","internal","bit","重置所有警报",1,"reset","w","w",null,"RESET-key",5,"w","w","Not the fire alarm(local stop)"]
[null,1012,4,1012,"manual operation raw output","internal","bit","手工操作的原始输出","0 / 1","inactive/active","r","r","enables direct setting of output-signals via service-port","not available","1, (2)"," "," ","not accessible, TMO"]
[null,1013,5,1013,"Unit on / off","internal","bit","单元的开/关","0 / 1","off/on","r","r","combined state (conclusion of 1000 .. 1005)",null,"2, (1)","r","r"]
[null,1014,6,1014,"maintenance necessary","internal","bit","维护必要的","0 / 1","reqired / no","r","r","will be reset by DP1015",null,"2, (1)","r"]
[null,1015,7,1015,"maintenance done","internal","bit","维修完成",1,"resets maintenace","w","--"]
[null,1016," ",2032,"unit year","internal","byte","单位年","0..99","2000..2099","r","r",null,"not available",null,"r"]
[null,1017," ",2034,"unit month","internal","byte","单位月","1..12",null,"r","r",null,"not available",null,"r"]
[null,1018," ",2036,"unit day","internal","byte","单位天","1..31",null,"r","r",null,"not available",null,"r"]
[null,1019," ",2038,"unit hour","internal","byte","单位小时","0..23",null,"r","r",null,"statusline",null,"r"]
[null,1020," ",2040,"unit minute","internal","byte","单位分钟","0..59",null,"r","r",null,"statusline",null,"r",null,"access twice to get up to date value"]
[null,1021,null,2042,"unit second","internal","byte","单位第二","0..59",null,"r","r",null,"not available",null,"r"]
[null,1022,0,1022,"unit temperature phys. unit","internal","bit","单位温度物理。单位","0/1","Celsius/Fahrenheit","rw","r",null,"not available","1, (2)","r","r"]
[null,1023,1,1023,"unit winter mode","internal","bit","单位冬季模式","0/1","Summer / Winter","r","r",null,"statusline?","2, (1)","r","r"]
[null,1024,2,1024,"day/night-mode","internal","bit","日/夜模式","0/1","day / night","r","r","current state of weekly program","statusline","2, (1)","r","r"]
[null,1025,3,1025,null,null,"bit"]
[null,1026,4,1026,null,null,"bit"]
[null,1027,5,1027,null,null,"bit"]
[null,1028,6,1028,null,null,"bit"]
[null,1029,7,1029,null,null,"bit"]
[null,1030," ",2060,"IOC service language","internal","byte","国际奥委会服务语言","0/1","English / German","rw","r",null,"not available","3, (4)"]
[null,1031," ",2062,"LT display language","internal","byte","LT显示语言","0/1","English / German","rw","r",null,"not available","3, (4)"]
[null,1032,0,1032,"unit firmware-options, byte 1, option 0","internal","bit","设备固件选项，第1个字节，选项0","0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1033,1,1033,"unit firmware-options","internal","bit","设备固件选项","0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1034,2,1034,"unit firmware-options","internal","bit","设备固件选项","0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1035,3,1035,"unit firmware-options","internal","bit","设备固件选项","0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1036,4,1036,"unit firmware-options","internal","bit","设备固件选项","0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1037,5,1037,"unit firmware-options","internal","bit","设备固件选项","0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1038,6,1038,"unit firmware-options","internal","bit","设备固件选项","0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1039,7,1039,"unit firmware-options","internal","bit","设备固件选项","0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1040,0,1040,"unit firmware-options, byte 2, option 8","internal","bit","设备固件选项， 2个字节，选项8","0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1041,1,1041,"unit firmware-options","internal","bit","设备固件选项","0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1042,2,1042,"unit firmware-options","internal","bit","设备固件选项","0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1043,3,1043,"unit firmware-options","internal","bit","设备固件选项","0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1044,4,1044,"unit firmware-options","internal","bit","设备固件选项","0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1045,5,1045,"unit firmware-options","internal","bit","设备固件选项","0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1046,6,1046,"unit firmware-options","internal","bit","设备固件选项","0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1047,7,1047,"unit firmware-options","internal","bit","设备固件选项","0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1048,0,1048,"unit firmware-options, byte 3, option 16","internal","bit","设备固件选项，第3个字节，选项16","0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1049,1,1049,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1050,2,1050,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1051,3,1051,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1052,4,1052,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1053,5,1053,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1054,6,1054,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1055,7,1055,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1056,0,1056,"unit firmware-options, byte 4, option 24","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1057,1,1057,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1058,2,1058,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1059,3,1059,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1060,4,1060,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1061,5,1061,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1062,6,1062,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1063,7,1063,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1064,0,1064,"unit firmware-options, byte 5, option 32","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1065,1,1065,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1066,2,1066,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1067,3,1067,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1068,4,1068,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1069,5,1069,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1070,6,1070,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1071,7,1071,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1072,0,1072,"unit firmware-options, byte 6, option 40","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1073,1,1073,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1074,2,1074,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1075,3,1075,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1076,4,1076,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1077,5,1077,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1078,6,1078,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1079,7,1079,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1080,0,1080,"unit firmware-options, byte 7, option 48","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1081,1,1081,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1082,2,1082,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1083,3,1083,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1084,4,1084,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1085,5,1085,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1086,6,1086,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1087,7,1087,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1088,0,1088,"unit firmware-options, byte 8, option 56","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1089,1,1089,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1090,2,1090,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1091,3,1091,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1092,4,1092,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1093,5,1093,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1094,6,1094,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1095,7,1095,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1096,0,1096,"unit firmware-options, byte 9, option 64","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1097,1,1097,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1098,2,1098,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1099,3,1099,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1100,4,1100,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1101,5,1101,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1102,6,1102,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1103,7,1103,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1104,0,1104,"unit firmware-options, byte 10, option 72","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1105,1,1105,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1106,2,1106,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1107,3,1107,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1108,4,1108,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1109,5,1109,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1110,6,1110,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1111,7,1111,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1112,0,1112,"unit firmware-options, byte 11, option 80","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1113,1,1113,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1114,2,1114,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1115,3,1115,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1116,4,1116,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1117,5,1117,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1118,6,1118,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1119,7,1119,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1120,0,1120,"unit firmware-options, byte 12, option 88","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1121,1,1121,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1122,2,1122,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1123,3,1123,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1124,4,1124,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1125,5,1125,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1126,6,1126,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1127,7,1127,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1128,0,1128,"unit firmware-options, byte 13, option 96","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1129,1,1129,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1130,2,1130,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1131,3,1131,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1132,4,1132,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1133,5,1133,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1134,6,1134,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1135,7,1135,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1136,0,1136,"unit firmware-options, byte 14, option 104","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1137,1,1137,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1138,2,1138,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1139,3,1139,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1140,4,1140,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1141,5,1141,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1142,6,1142,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1143,7,1143,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1144,0,1144,"unit firmware-options, byte 15, option 112","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1145,1,1145,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1146,2,1146,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1147,3,1147,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1148,4,1148,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1149,5,1149,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1150,6,1150,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1151,7,1151,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1152,0,1152,"unit firmware-options, byte 16, option 120","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1153,1,1153,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1154,2,1154,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1155,3,1155,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1156,4,1156,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1157,5,1157,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1158,6,1158,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1159,7,1159,"unit firmware-options","internal","bit",null,"0/1",null,"r","r",null,"Info->system","2, (1)",null,null,"not implemented"]
[null,1160," ",2320,"unit last maintenance year","internal","byte","单位最后维护一年","0..99","2000..2099","rw","r",null,"Service->data->maintenance","3, (4)"]
[null,1161," ",2322,"unit last maintenance month","internal","byte","单位最后维护月份","1..12",null,"rw","r",null,"Service->data->maintenance","3, (4)"]
[null,1162," ",2324,"unit last maintenance day","internal","byte","单位最后维护日","1..31",null,"rw","r",null,"Service->data->maintenance","3, (4)"]
[null,1163," ",2326,"unit maintenance intervall","internal","byte","单位维护intervall的","1..255","1month..255months","rw","r",null,"Service->data->maintenance","3, (4)"]
[null,1164," ",2328,"unit runtime unit","internal","UI32","机组运行单元","0..0xFFFFFFFF","hours","r(w0)","r",null,"Info->runtime; Service->data->runtimes","3, (4)","r","r"]
[null,1165," ",2330,"unit stoptime unit","internal","UI32","单位停止时间单位","0..0xFFFFFFFF","hours","r(w0)","r",null,"Info->runtime; Service->data->runtimes","3, (4)","r","r"]
[null,1166," ",2332,"unit runtime cooling","internal","UI32","机组运行时冷却","0..0xFFFFFFFF","hours","r(w0)","r",null,"Info->runtime; Service->data->runtimes","3, (4)","r","r"]
[null,1167," ",2334,"unit runtime heating","internal","UI32","机组运行时加热","0..0xFFFFFFFF","hours","r(w0)","r",null,"Info->runtime; Service->data->runtimes","3, (4)","r","r"]
[null,1168," ",2336,"unit runtime humidification","internal","UI32","机组运行加湿","0..0xFFFFFFFF","hours","r(w0)","r",null,"Info->runtime; Service->data->runtimes","3, (4)","r","r"]
[null,1169," ",2338,"unit runtime dehumidification","internal","UI32","机组运行除湿","0..0xFFFFFFFF","hours","r(w0)","r",null,"Info->runtime; Service->data->runtimes","3, (4)","r","r"]
[null,1170," ",2340,"unit temperature","internal","word","单位温度","-1000..1000","-100,0..100,0°C","r","r",null,"Info->actual/setpoint","4, (3)","r","r"]
[null,1171," ",2342,"unit humidity","internal","word","单位湿度","0..1000","0..100,0%rF","r","r",null,"Info->actual/setpoint","4, (3)","r","r"]
[null,1172," ",2344,"unit emergency temperature","internal","word","单位紧急温的","0..400","0..40,0°C","rw","r",null,"Control->temperature","3, (4)",null,null,"not accessible, TMO"]
[null,1173," ",2346,"unit setpoint temperature day","internal","word","单位设定值温度日","50..350","5,0..35,0°C","rw","rw",null,"Info->actual/setpoint; Control->temperature","3, (4), 16","rw","rw"]
[null,1174," ",2348,"unit setpoint temperature night","internal","word","单位给定温度之夜","50..350","5,0..35,0°C","rw","rw",null,"Info->actual/setpoint; Control->temperature","3, (4), 16","rw","rw"]
[null,1175," ",2350,"unit setpoint temperature corrected","internal","word","单位设定点温度校正","-1000..1000","-100,0..100,0°C","r","r",null,"Info->actual/setpoint; Control->temperature","3, (4)"]
[null,1176," ",2352,"unit setpoint humidity","internal","word","单位给定的湿度","50..900","5,0..90,0%rF","rw","rw",null,"Info->actual/setpoint; Control->humidity","3, (4), 16","rw","rw"]
[null,1177," ",2354,"unit setpoint humidity 2","internal","word","单位设定点湿度",null,null,"rw","rw","so far unused","Info->actual/setpoint; Control->humidity","3, (4), 16",null,null,"not accessible"]
[null,1178," ",2356,"unit setpoint humidity corrected","internal","word","单位给定的湿度修正","0..1000","0..100,0%rF","r","r",null,"Info->actual/setpoint; Control->humidity","3, (4)"]
[null,1179," ",2358,"unit temperature setpoint day shift","internal","byte","单元的温度设定值白班","-127..+127","-12.7K..+12.7K","rw","rw","so far unused","not available"," "," "," ","not accessible"]
[null,1180," ",2360,"unit temperature setpoint night shift","internal","byte","单元的温度设定值晚班","-127..+127","-12.7K..+12.7K","rw","rw","so far unused","not available"," "," "," ","not accessible"]
[null,1181," ",2362,"unit humidity setpoint day shift","internal","byte","单位湿度设定值白班","-127..+127","-12.7%..+12.7%","rw","rw","so far unused","not available"," "," "," ","not accessible"]
[null,1182," ",2364,"unit humidity setpoint night shift","internal","byte","单位湿度设定值晚班","-127..+127","-12.7%..+12.7%","rw","rw","so far unused","not available"," "," "," ","not accessible"]
[null,1183," ",2366,"unit control type","internal","byte","单元控制型","1..4","room, supply, room (sup.lim), \nsup. (room lim.)","rw","r",null,"Service->general->control-type","3, (4)","rw","rw"]
[null,1184," ",2368,"limited control: start temperature","internal","word","限制：线型控制范围温度","0..400","0..40,0°C","rw","r",null,"Service->general->parameters","3, (4)"," "," "]
[null,1185," ",2370,"limited control: lineary range temperature","internal","word","有限的控制：开始湿度","0..200","0,0K..20,0K","rw","r",null,"Service->general->parameters","3, (4)"," "," "]
[null,1186," ",2372,"limited control: start humidity","internal","word","限制：线型控制范围湿度","0..900","0,0..90,0%rF","rw","r",null,"Service->general->parameters","3, (4)"," "," "]
[null,1187," ",2374,"limited control: lineary range humidity","internal","word","单位冬季模式starttemp","0..200","0,0%..20,0%","rw","r",null,"Service->general->parameters","3, (4)"," "," "]
[null,1188," ",2376,"unit winter-mode starttemp","internal","word","单位冬季模式滞后","50..350","5,0..35,0°C","rw","r",null,"Service->general->parameters","3, (4)","rw"," "]
[null,1189," ",2378,"unit winter-mode hysteresis","internal","word","单位不可或缺的因素","10..99","1,0..9,9K","rw","r",null,"Service->general->parameters","3, (4)","rw"," "]
[null,1190," ",2380,"unit integral factor","internal","byte","单位水温1","0..10","0..10%","rw","r",null,"Service->general->parameters","3, (4)"," "," "]
[null,1191," ",2382,"unit water temperature 1","redirected input","word","机组回风温度","-1000..1000","-100,0..100,0°C","r","r",null,"Info->actual/setpoint","4, (3)","r","r"]
[null,1192," ",2384,"unit return air temperature","redirected input","word","机组送风温度","-1000..1000","-100,0..100,0°C","r","r",null,"Info->actual/setpoint","4, (3)","r","r"]
[null,1193," ",2386,"unit supply air temperature","redirected input","word","机组回风湿度","-1000..1000","-100,0..100,0°C","r","r",null,"Info->actual/setpoint","4, (3)","r","r"]
[null,1194," ",2388,"unit return air humidity","redirected input","word","单位供应空气湿度","0..1000","0,0..100,0%rF","r","r",null,"Info->actual/setpoint","4, (3)","r","r"]
[null,1195," ",2390,"unit supply air humidity","redirected input","word","单元外部空气温度","0..1000","0,0..100,0%rF","r","r",null,"Info->actual/setpoint","4, (3)","r","r"]
[null,1196," ",2392,"unit outside air temperature","redirected input","word","单位外面的空气湿度","-1000..1000","-100,0..100,0°C","r","r",null,"Info->actual/setpoint","4, (3)","r","r"]
[null,1197," ",2394,"unit outside air humidity","redirected input","word","机组冷却优先","0..1000","0,0..100,0%rF","r","r",null,"Info->actual/setpoint","4, (3)"]
[null,1198," ",2396,"unit cooling priority","internal","byte","外界温度压力","0..2","GE / CW / DX","rw","r",null,null,"3, (4)","rw","rw"]
[null,1199," ",2398,"outside temperature for pressure ","internal","word","压力梯度","50..350","5,0..35,0°C","rw","r",null,null,"3, (4)"]
[null,1200," ",2400,"gradient for pressure ","internal","word","键盘控制单元","0..200","0,0..20,0","rw","r",null,null,"3, (4)"]
[null,1201," ",2402,"keypad control unit","internal","byte","机组水温2","0..31","bus-adr","rw","r",null,"not available","3, (4)"," "," "]
[null,1202," ",2404,"unit water temperature 2","redirected input","word",null,"-1000..1000","-100,0..100,0°C","r","r",null,"Info->actual/setpoint","4, (3)","r","r"]
[{"$nulls":3}," "]
["defaultconfigurations",null,null," "]
[null,1250,null,1250,"loaddefault dx1","internal","bit",null,1,null,"w","--",{"$nulls":3}," "," "]
[null,1251,null,1251,"loaddefault dx2","internal","bit",null,1,null,"w","--",{"$nulls":3}," "," "]
[null,1252,null,1252,"loaddefault cw","internal","bit",null,1,null,"w","--",{"$nulls":3}," "," "]
[null,1253,null,1253,"loaddefault cw2","internal","bit",null,1,null,"w","--",{"$nulls":3}," "," "]
[null,1254,null,1254,"loaddefault agcw1","internal","bit",null,1,null,"w","--",{"$nulls":3}," "," "]
[null,1255,null,1255,"loaddefault agcw2","internal","bit",null,1,null,"w","--",{"$nulls":3}," "," "]
[null,1256,null,1256,"loaddefault ge11","internal","bit",null,1,null,"w","--",{"$nulls":3}," "," "]
[null,1257,null,1257,"loaddefault ge12","internal","bit",null,1,null,"w","--",{"$nulls":3}," "," "]
[null,1258,null,1258,"loaddefault ge21","internal","bit",null,1,null,"w","--",{"$nulls":3}," "," "]
[null,1259,null,1259,"loaddefault ge22","internal","bit",null,1,null,"w","--",{"$nulls":3}," "," "]
[{"$nulls":3}," "]
[null,1292,null,2584,"Password control digit 1","internal","byte",null,"0..9",null,"-","-"]
[null,1293,null,2586,"Password control digit 2","internal","byte",null,"0..9",null,"-","-"]
[null,1294,null,2588,"Password control digit 3","internal","byte",null,"0..9",null,"-","-"]
[null,1295,null,2590,"Password control digit 4","internal","byte",null,"0..9",null,"-","-"]
[]
[null,1296,null,2592,"Password service digit 1","internal","byte",null,"0..9",null,"-","-"]
[null,1297,null,2594,"Password service digit 2","internal","byte",null,"0..9",null,"-","-"]
[null,1298,null,2596,"Password service digit 3","internal","byte",null,"0..9",null,"-","-"]
[null,1299,null,2598,"Password service digit 4","internal","byte",null,"0..9",null,"-","-"]
[{"$nulls":3}," "]
[{"$nulls":3}," "]
["weekly program",null,null," "]
[null,1300,0,1300,"unit weekly programm; monday 0:00..0:59","internal","bit",null,"0/1","off,day,night","rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1301," ",1301,"unit weekly programm; monday 0:00..0:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1302," ",1302,"unit weekly programm; monday 1:00..1:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1303," ",1303,"unit weekly programm; monday 1:00..1:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1304," ",1304,"unit weekly programm; monday 2:00..2:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1305," ",1305,"unit weekly programm; monday 2:00..2:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1306," ",1306,"unit weekly programm; monday 3:00..3:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1307," ",1307,"unit weekly programm; monday 3:00..3:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1308,0,1308,"unit weekly programm; monday 4:00..4:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1309," ",1309,"unit weekly programm; monday 4:00..4:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1310," ",1310,"unit weekly programm; monday 5:00..5:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1311," ",1311,"unit weekly programm; monday 5:00..5:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1312," ",1312,"unit weekly programm; monday 6:00..6:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1313," ",1313,"unit weekly programm; monday 6:00..6:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1314," ",1314,"unit weekly programm; monday 7:00..7:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1315," ",1315,"unit weekly programm; monday 7:00..7:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1316,0,1316,"unit weekly programm; monday 8:00..8:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1317," ",1317,"unit weekly programm; monday 8:00..8:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1318," ",1318,"unit weekly programm; monday 9:00..9:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1319," ",1319,"unit weekly programm; monday 9:00..9:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1320," ",1320,"unit weekly programm; monday 10:00..10:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1321," ",1321,"unit weekly programm; monday 10:00..10:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1322," ",1322,"unit weekly programm; monday 11:00..11:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1323," ",1323,"unit weekly programm; monday 11:00..11:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1324,0,1324,"unit weekly programm; monday 12:00..12:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1325," ",1325,"unit weekly programm; monday 12:00..12:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1326," ",1326,"unit weekly programm; monday 13:00..13:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1327," ",1327,"unit weekly programm; monday 13:00..13:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1328," ",1328,"unit weekly programm; monday 14:00..14:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1329," ",1329,"unit weekly programm; monday 14:00..14:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1330," ",1330,"unit weekly programm; monday 15:00..15:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1331," ",1331,"unit weekly programm; monday 15:00..15:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1332,0,1332,"unit weekly programm; monday 16:00..16:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1333," ",1333,"unit weekly programm; monday 16:00..16:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1334," ",1334,"unit weekly programm; monday 17:00..17:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1335," ",1335,"unit weekly programm; monday 17:00..17:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1336," ",1336,"unit weekly programm; monday 18:00..18:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1337," ",1337,"unit weekly programm; monday 18:00..18:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1338," ",1338,"unit weekly programm; monday 19:00..19:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1339," ",1339,"unit weekly programm; monday 19:00..19:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1340,0,1340,"unit weekly programm; monday 20:00..20:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1341," ",1341,"unit weekly programm; monday 20:00..20:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1342," ",1342,"unit weekly programm; monday 21:00..21:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1343," ",1343,"unit weekly programm; monday 21:00..21:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1344," ",1344,"unit weekly programm; monday 22:00..22:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1345," ",1345,"unit weekly programm; monday 22:00..22:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1346," ",1346,"unit weekly programm; monday 23:00..23:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1347," ",1347,"unit weekly programm; monday 23:00..23:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1348,0,1348,"unit weekly programm; tuesday 0:00..0:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1349," ",1349,"unit weekly programm; tuesday 0:00..0:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1350," ",1350,"unit weekly programm; tuesday 1:00..1:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1351," ",1351,"unit weekly programm; tuesday 1:00..1:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1352," ",1352,"unit weekly programm; tuesday 2:00..2:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1353," ",1353,"unit weekly programm; tuesday 2:00..2:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1354," ",1354,"unit weekly programm; tuesday 3:00..3:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1355," ",1355,"unit weekly programm; tuesday 3:00..3:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1356,0,1356,"unit weekly programm; tuesday 4:00..4:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1357," ",1357,"unit weekly programm; tuesday 4:00..4:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1358," ",1358,"unit weekly programm; tuesday 5:00..5:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1359," ",1359,"unit weekly programm; tuesday 5:00..5:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1360," ",1360,"unit weekly programm; tuesday 6:00..6:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1361," ",1361,"unit weekly programm; tuesday 6:00..6:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1362," ",1362,"unit weekly programm; tuesday 7:00..7:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1363," ",1363,"unit weekly programm; tuesday 7:00..7:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1364,0,1364,"unit weekly programm; tuesday 8:00..8:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1365," ",1365,"unit weekly programm; tuesday 8:00..8:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1366," ",1366,"unit weekly programm; tuesday 9:00..9:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1367," ",1367,"unit weekly programm; tuesday 9:00..9:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1368," ",1368,"unit weekly programm; tuesday 10:00..10:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1369," ",1369,"unit weekly programm; tuesday 10:00..10:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1370," ",1370,"unit weekly programm; tuesday 11:00..11:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1371," ",1371,"unit weekly programm; tuesday 11:00..11:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1372,0,1372,"unit weekly programm; tuesday 12:00..12:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1373," ",1373,"unit weekly programm; tuesday 12:00..12:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1374," ",1374,"unit weekly programm; tuesday 13:00..13:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1375," ",1375,"unit weekly programm; tuesday 13:00..13:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1376," ",1376,"unit weekly programm; tuesday 14:00..14:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1377," ",1377,"unit weekly programm; tuesday 14:00..14:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1378," ",1378,"unit weekly programm; tuesday 15:00..15:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1379," ",1379,"unit weekly programm; tuesday 15:00..15:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1380,0,1380,"unit weekly programm; tuesday 16:00..16:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1381," ",1381,"unit weekly programm; tuesday 16:00..16:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1382," ",1382,"unit weekly programm; tuesday 17:00..17:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1383," ",1383,"unit weekly programm; tuesday 17:00..17:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1384," ",1384,"unit weekly programm; tuesday 18:00..18:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1385," ",1385,"unit weekly programm; tuesday 18:00..18:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1386," ",1386,"unit weekly programm; tuesday 19:00..19:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1387," ",1387,"unit weekly programm; tuesday 19:00..19:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1388,0,1388,"unit weekly programm; tuesday 20:00..20:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1389," ",1389,"unit weekly programm; tuesday 20:00..20:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1390," ",1390,"unit weekly programm; tuesday 21:00..21:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1391," ",1391,"unit weekly programm; tuesday 21:00..21:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1392," ",1392,"unit weekly programm; tuesday 22:00..22:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1393," ",1393,"unit weekly programm; tuesday 22:00..22:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1394," ",1394,"unit weekly programm; tuesday 23:00..23:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1395," ",1395,"unit weekly programm; tuesday 23:00..23:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1396,0,1396,"unit weekly programm; wednesday 0:00..0:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1397," ",1397,"unit weekly programm; wednesday 0:00..0:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1398," ",1398,"unit weekly programm; wednesday 1:00..1:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1399," ",1399,"unit weekly programm; wednesday 1:00..1:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1400," ",1400,"unit weekly programm; wednesday 2:00..2:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1401," ",1401,"unit weekly programm; wednesday 2:00..2:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1402," ",1402,"unit weekly programm; wednesday 3:00..3:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1403," ",1403,"unit weekly programm; wednesday 3:00..3:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1404,0,1404,"unit weekly programm; wednesday 4:00..4:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1405," ",1405,"unit weekly programm; wednesday 4:00..4:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1406," ",1406,"unit weekly programm; wednesday 5:00..5:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1407," ",1407,"unit weekly programm; wednesday 5:00..5:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1408," ",1408,"unit weekly programm; wednesday 6:00..6:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1409," ",1409,"unit weekly programm; wednesday 6:00..6:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1410," ",1410,"unit weekly programm; wednesday 7:00..7:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1411," ",1411,"unit weekly programm; wednesday 7:00..7:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1412,0,1412,"unit weekly programm; wednesday 8:00..8:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1413," ",1413,"unit weekly programm; wednesday 8:00..8:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1414," ",1414,"unit weekly programm; wednesday 9:00..9:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1415," ",1415,"unit weekly programm; wednesday 9:00..9:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1416," ",1416,"unit weekly programm; wednesday 10:00..10:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1417," ",1417,"unit weekly programm; wednesday 10:00..10:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1418," ",1418,"unit weekly programm; wednesday 11:00..11:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1419," ",1419,"unit weekly programm; wednesday 11:00..11:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1420,0,1420,"unit weekly programm; wednesday 12:00..12:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1421," ",1421,"unit weekly programm; wednesday 12:00..12:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1422," ",1422,"unit weekly programm; wednesday 13:00..13:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1423," ",1423,"unit weekly programm; wednesday 13:00..13:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1424," ",1424,"unit weekly programm; wednesday 14:00..14:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1425," ",1425,"unit weekly programm; wednesday 14:00..14:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1426," ",1426,"unit weekly programm; wednesday 15:00..15:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1427," ",1427,"unit weekly programm; wednesday 15:00..15:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1428,0,1428,"unit weekly programm; wednesday 16:00..16:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1429," ",1429,"unit weekly programm; wednesday 16:00..16:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1430," ",1430,"unit weekly programm; wednesday 17:00..17:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1431," ",1431,"unit weekly programm; wednesday 17:00..17:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1432," ",1432,"unit weekly programm; wednesday 18:00..18:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1433," ",1433,"unit weekly programm; wednesday 18:00..18:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1434," ",1434,"unit weekly programm; wednesday 19:00..19:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1435," ",1435,"unit weekly programm; wednesday 19:00..19:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1436,0,1436,"unit weekly programm; wednesday 20:00..20:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1437," ",1437,"unit weekly programm; wednesday 20:00..20:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1438," ",1438,"unit weekly programm; wednesday 21:00..21:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1439," ",1439,"unit weekly programm; wednesday 21:00..21:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1440," ",1440,"unit weekly programm; wednesday 22:00..22:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1441," ",1441,"unit weekly programm; wednesday 22:00..22:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1442," ",1442,"unit weekly programm; wednesday 23:00..23:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1443," ",1443,"unit weekly programm; wednesday 23:00..23:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1444,0,1444,"unit weekly programm; thursday 0:00..0:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1445," ",1445,"unit weekly programm; thursday 0:00..0:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1446," ",1446,"unit weekly programm; thursday 1:00..1:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1447," ",1447,"unit weekly programm; thursday 1:00..1:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1448," ",1448,"unit weekly programm; thursday 2:00..2:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1449," ",1449,"unit weekly programm; thursday 2:00..2:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1450," ",1450,"unit weekly programm; thursday 3:00..3:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1451," ",1451,"unit weekly programm; thursday 3:00..3:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1452,0,1452,"unit weekly programm; thursday 4:00..4:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1453," ",1453,"unit weekly programm; thursday 4:00..4:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1454," ",1454,"unit weekly programm; thursday 5:00..5:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1455," ",1455,"unit weekly programm; thursday 5:00..5:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1456," ",1456,"unit weekly programm; thursday 6:00..6:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1457," ",1457,"unit weekly programm; thursday 6:00..6:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1458," ",1458,"unit weekly programm; thursday 7:00..7:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1459," ",1459,"unit weekly programm; thursday 7:00..7:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1460,0,1460,"unit weekly programm; thursday 8:00..8:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1461," ",1461,"unit weekly programm; thursday 8:00..8:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1462," ",1462,"unit weekly programm; thursday 9:00..9:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1463," ",1463,"unit weekly programm; thursday 9:00..9:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1464," ",1464,"unit weekly programm; thursday 10:00..10:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1465," ",1465,"unit weekly programm; thursday 10:00..10:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1466," ",1466,"unit weekly programm; thursday 11:00..11:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1467," ",1467,"unit weekly programm; thursday 11:00..11:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1468,0,1468,"unit weekly programm; thursday 12:00..12:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1469," ",1469,"unit weekly programm; thursday 12:00..12:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1470," ",1470,"unit weekly programm; thursday 13:00..13:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1471," ",1471,"unit weekly programm; thursday 13:00..13:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1472," ",1472,"unit weekly programm; thursday 14:00..14:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1473," ",1473,"unit weekly programm; thursday 14:00..14:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1474," ",1474,"unit weekly programm; thursday 15:00..15:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1475," ",1475,"unit weekly programm; thursday 15:00..15:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1476,0,1476,"unit weekly programm; thursday 16:00..16:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1477," ",1477,"unit weekly programm; thursday 16:00..16:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1478," ",1478,"unit weekly programm; thursday 17:00..17:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1479," ",1479,"unit weekly programm; thursday 17:00..17:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1480," ",1480,"unit weekly programm; thursday 18:00..18:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1481," ",1481,"unit weekly programm; thursday 18:00..18:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1482," ",1482,"unit weekly programm; thursday 19:00..19:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1483," ",1483,"unit weekly programm; thursday 19:00..19:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1484,0,1484,"unit weekly programm; thursday 20:00..20:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1485," ",1485,"unit weekly programm; thursday 20:00..20:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1486," ",1486,"unit weekly programm; thursday 21:00..21:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1487," ",1487,"unit weekly programm; thursday 21:00..21:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1488," ",1488,"unit weekly programm; thursday 22:00..22:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1489," ",1489,"unit weekly programm; thursday 22:00..22:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1490," ",1490,"unit weekly programm; thursday 23:00..23:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1491," ",1491,"unit weekly programm; thursday 23:00..23:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1492,0,1492,"unit weekly programm; friday 0:00..0:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1493," ",1493,"unit weekly programm; friday 0:00..0:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1494," ",1494,"unit weekly programm; friday 1:00..1:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1495," ",1495,"unit weekly programm; friday 1:00..1:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1496," ",1496,"unit weekly programm; friday 2:00..2:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1497," ",1497,"unit weekly programm; friday 2:00..2:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1498," ",1498,"unit weekly programm; friday 3:00..3:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1499," ",1499,"unit weekly programm; friday 3:00..3:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1500,0,1500,"unit weekly programm; friday 4:00..4:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1501," ",1501,"unit weekly programm; friday 4:00..4:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1502," ",1502,"unit weekly programm; friday 5:00..5:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1503," ",1503,"unit weekly programm; friday 5:00..5:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1504," ",1504,"unit weekly programm; friday 6:00..6:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1505," ",1505,"unit weekly programm; friday 6:00..6:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1506," ",1506,"unit weekly programm; friday 7:00..7:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1507," ",1507,"unit weekly programm; friday 7:00..7:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1508,0,1508,"unit weekly programm; friday 8:00..8:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1509," ",1509,"unit weekly programm; friday 8:00..8:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1510," ",1510,"unit weekly programm; friday 9:00..9:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1511," ",1511,"unit weekly programm; friday 9:00..9:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1512," ",1512,"unit weekly programm; friday 10:00..10:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1513," ",1513,"unit weekly programm; friday 10:00..10:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1514," ",1514,"unit weekly programm; friday 11:00..11:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1515," ",1515,"unit weekly programm; friday 11:00..11:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1516,0,1516,"unit weekly programm; friday 12:00..12:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1517," ",1517,"unit weekly programm; friday 12:00..12:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1518," ",1518,"unit weekly programm; friday 13:00..13:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1519," ",1519,"unit weekly programm; friday 13:00..13:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1520," ",1520,"unit weekly programm; friday 14:00..14:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1521," ",1521,"unit weekly programm; friday 14:00..14:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1522," ",1522,"unit weekly programm; friday 15:00..15:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1523," ",1523,"unit weekly programm; friday 15:00..15:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1524,0,1524,"unit weekly programm; friday 16:00..16:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1525," ",1525,"unit weekly programm; friday 16:00..16:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1526," ",1526,"unit weekly programm; friday 17:00..17:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1527," ",1527,"unit weekly programm; friday 17:00..17:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1528," ",1528,"unit weekly programm; friday 18:00..18:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1529," ",1529,"unit weekly programm; friday 18:00..18:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1530," ",1530,"unit weekly programm; friday 19:00..19:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1531," ",1531,"unit weekly programm; friday 19:00..19:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1532,0,1532,"unit weekly programm; friday 20:00..20:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1533," ",1533,"unit weekly programm; friday 20:00..20:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1534," ",1534,"unit weekly programm; friday 21:00..21:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1535," ",1535,"unit weekly programm; friday 21:00..21:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1536," ",1536,"unit weekly programm; friday 22:00..22:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1537," ",1537,"unit weekly programm; friday 22:00..22:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1538," ",1538,"unit weekly programm; friday 23:00..23:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1539," ",1539,"unit weekly programm; friday 23:00..23:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1540,0,1540,"unit weekly programm; saturday 0:00..0:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1541," ",1541,"unit weekly programm; saturday 0:00..0:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1542," ",1542,"unit weekly programm; saturday 1:00..1:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1543," ",1543,"unit weekly programm; saturday 1:00..1:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1544," ",1544,"unit weekly programm; saturday 2:00..2:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1545," ",1545,"unit weekly programm; saturday 2:00..2:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1546," ",1546,"unit weekly programm; saturday 3:00..3:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1547," ",1547,"unit weekly programm; saturday 3:00..3:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1548,0,1548,"unit weekly programm; saturday 4:00..4:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1549," ",1549,"unit weekly programm; saturday 4:00..4:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1550," ",1550,"unit weekly programm; saturday 5:00..5:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1551," ",1551,"unit weekly programm; saturday 5:00..5:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1552," ",1552,"unit weekly programm; saturday 6:00..6:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1553," ",1553,"unit weekly programm; saturday 6:00..6:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1554," ",1554,"unit weekly programm; saturday 7:00..7:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1555," ",1555,"unit weekly programm; saturday 7:00..7:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1556,0,1556,"unit weekly programm; saturday 8:00..8:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1557," ",1557,"unit weekly programm; saturday 8:00..8:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1558," ",1558,"unit weekly programm; saturday 9:00..9:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1559," ",1559,"unit weekly programm; saturday 9:00..9:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1560," ",1560,"unit weekly programm; saturday 10:00..10:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1561," ",1561,"unit weekly programm; saturday 10:00..10:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1562," ",1562,"unit weekly programm; saturday 11:00..11:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1563," ",1563,"unit weekly programm; saturday 11:00..11:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1564,0,1564,"unit weekly programm; saturday 12:00..12:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1565," ",1565,"unit weekly programm; saturday 12:00..12:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1566," ",1566,"unit weekly programm; saturday 13:00..13:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1567," ",1567,"unit weekly programm; saturday 13:00..13:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1568," ",1568,"unit weekly programm; saturday 14:00..14:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1569," ",1569,"unit weekly programm; saturday 14:00..14:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1570," ",1570,"unit weekly programm; saturday 15:00..15:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1571," ",1571,"unit weekly programm; saturday 15:00..15:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1572,0,1572,"unit weekly programm; saturday 16:00..16:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1573," ",1573,"unit weekly programm; saturday 16:00..16:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1574," ",1574,"unit weekly programm; saturday 17:00..17:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1575," ",1575,"unit weekly programm; saturday 17:00..17:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1576," ",1576,"unit weekly programm; saturday 18:00..18:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1577," ",1577,"unit weekly programm; saturday 18:00..18:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1578," ",1578,"unit weekly programm; saturday 19:00..19:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1579," ",1579,"unit weekly programm; saturday 19:00..19:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1580,0,1580,"unit weekly programm; saturday 20:00..20:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1581," ",1581,"unit weekly programm; saturday 20:00..20:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1582," ",1582,"unit weekly programm; saturday 21:00..21:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1583," ",1583,"unit weekly programm; saturday 21:00..21:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1584," ",1584,"unit weekly programm; saturday 22:00..22:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1585," ",1585,"unit weekly programm; saturday 22:00..22:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1586," ",1586,"unit weekly programm; saturday 23:00..23:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1587," ",1587,"unit weekly programm; saturday 23:00..23:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1588,0,1588,"unit weekly programm; sunday 0:00..0:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1589," ",1589,"unit weekly programm; sunday 0:00..0:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1590," ",1590,"unit weekly programm; sunday 1:00..1:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1591," ",1591,"unit weekly programm; sunday 1:00..1:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1592," ",1592,"unit weekly programm; sunday 2:00..2:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1593," ",1593,"unit weekly programm; sunday 2:00..2:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1594," ",1594,"unit weekly programm; sunday 3:00..3:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1595," ",1595,"unit weekly programm; sunday 3:00..3:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1596,0,1596,"unit weekly programm; sunday 4:00..4:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1597," ",1597,"unit weekly programm; sunday 4:00..4:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1598," ",1598,"unit weekly programm; sunday 5:00..5:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1599," ",1599,"unit weekly programm; sunday 5:00..5:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1600," ",1600,"unit weekly programm; sunday 6:00..6:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1601," ",1601,"unit weekly programm; sunday 6:00..6:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1602," ",1602,"unit weekly programm; sunday 7:00..7:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1603," ",1603,"unit weekly programm; sunday 7:00..7:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1604,0,1604,"unit weekly programm; sunday 8:00..8:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1605," ",1605,"unit weekly programm; sunday 8:00..8:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1606," ",1606,"unit weekly programm; sunday 9:00..9:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1607," ",1607,"unit weekly programm; sunday 9:00..9:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1608," ",1608,"unit weekly programm; sunday 10:00..10:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1609," ",1609,"unit weekly programm; sunday 10:00..10:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1610," ",1610,"unit weekly programm; sunday 11:00..11:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1611," ",1611,"unit weekly programm; sunday 11:00..11:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1612,0,1612,"unit weekly programm; sunday 12:00..12:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1613," ",1613,"unit weekly programm; sunday 12:00..12:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1614," ",1614,"unit weekly programm; sunday 13:00..13:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1615," ",1615,"unit weekly programm; sunday 13:00..13:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1616," ",1616,"unit weekly programm; sunday 14:00..14:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1617," ",1617,"unit weekly programm; sunday 14:00..14:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1618," ",1618,"unit weekly programm; sunday 15:00..15:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1619," ",1619,"unit weekly programm; sunday 15:00..15:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1620,0,1620,"unit weekly programm; sunday 16:00..16:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1621," ",1621,"unit weekly programm; sunday 16:00..16:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1622," ",1622,"unit weekly programm; sunday 17:00..17:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1623," ",1623,"unit weekly programm; sunday 17:00..17:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1624," ",1624,"unit weekly programm; sunday 18:00..18:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1625," ",1625,"unit weekly programm; sunday 18:00..18:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1626," ",1626,"unit weekly programm; sunday 19:00..19:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1627," ",1627,"unit weekly programm; sunday 19:00..19:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1628,0,1628,"unit weekly programm; sunday 20:00..20:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1629," ",1629,"unit weekly programm; sunday 20:00..20:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1630," ",1630,"unit weekly programm; sunday 21:00..21:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1631," ",1631,"unit weekly programm; sunday 21:00..21:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1632," ",1632,"unit weekly programm; sunday 22:00..22:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1633," ",1633,"unit weekly programm; sunday 22:00..22:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1634," ",1634,"unit weekly programm; sunday 23:00..23:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[null,1635," ",1635,"unit weekly programm; sunday 23:00..23:59","internal","bit",null,"0/1",null,"rw","rw",null,"Info->day/night; Control->day/night","1, (2)"," "," ","not accessible"]
[{"$nulls":3}," "]
[null,1700," ",3400,"common alarm DOUT","internal","byte",null,"0..31",null,"rw","r","added","Service->equipment->auxports","3, (4)"]
[null,1701," ",3402,"winter mode DOUT","internal","byte",null,"0..31",null,"rw","r","added","Service->equipment->auxports","3, (4)"]
[null,1702," ",3404,"remote on/off DIN","internal","byte",null,"0..42",null,"rw","r","added","Service->equipment->auxports","3, (4)"]
[null,1703," ",3406,"ups DIN","internal","byte",null,"0..42",null,"rw","r","added","Service->equipment->auxports","3, (4)"]
[null,1704," ",3408,"fire alarm DIN","internal","byte",null,"0..42",null,"rw","r","added","Service->equipment->auxports","3, (4)"]
[null,1705," ",3410,"water alarm DIN","internal","byte",null,"0..42",null,"rw","r","added","Service->equipment->auxports","3, (4)"]
[null,1706," ",3412,{"$nulls":9},"Service->equipment->auxports"]
[null,1707," ",3414,"phase alarm DIN","internal","byte",null,"0..42",null,"rw","r","added","Service->equipment->auxports","3, (4)"]
[null,1708," ",3416,"CW-disable/DX-enable DIN","internal","byte",null,"0..42",null,"rw","r","added","Service->equipment->auxports","3, (4)"]
[null,1709," ",3418,"temperature AOUT","internal","byte",null,"0..20",null,"rw","r","added","Service->equipment->auxports","3, (4)"]
[null,1710," ",3420,"humidity AOUT","internal","byte",null,"0..20",null,"rw","r","added","Service->equipment->auxports","3, (4)"]
[null,1711," ",3422,"fire alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,1712," ",3424,"fire alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,1713," ",3426,"water alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,1714," ",3428,"water alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,1715," ",3430,"phase alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,1716," ",3432,"phase alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[]
[null,1742,0,1742,"fire alarm common alarm","internal","bit",null,"0/1",null,"rw","r","added","Service->general->upsmode","1, (2)",null,null,"not accessible"]
[null,1743,1,1743,"water alarm common alarm","internal","bit",null,"0/1",null,"rw","r","added","Service->general->upsmode","1, (2)",null,null,"not accessible"]
[null,1744,2,1744,"phase alarm common alarm","internal","bit",null,"0/1",null,"rw","r","added","Service->general->upsmode","1, (2)",null,null,"not accessible"]
[null,1745,3,1745,null,"internal","bit",null,"0/1",null,"rw","r","added","Service->general->upsmode","1, (2)"]
[null,1746,4,1746,null,"internal","bit",null,"0/1",null,"r","r","added",null,"2, (1)"]
[null,1747,5,1747,null,"internal","bit",null,"0/1",null,"r","r","added",null,"2, (1)"]
[null,1748,6,1748,null,"internal","bit",null,"0/1",null,"r","r","added",null,"2, (1)"]
[null,1749,7,1749,null,"internal","bit",null,"0/1",null,"r","r","added",null,"2, (1)"]
[null,1750,0,1750,"ups action cooling","internal","bit",null,"0/1",null,"rw","r","added","Service->general->upsmode","1, (2)"]
[null,1751,1,1751,"ups action heating","internal","bit",null,"0/1",null,"rw","r","added","Service->general->upsmode","1, (2)"]
[null,1752,2,1752,"ups action humidification","internal","bit",null,"0/1",null,"rw","r","added","Service->general->upsmode","1, (2)"]
[null,1753,3,1753,"ups action dehumidification","internal","bit",null,"0/1",null,"rw","r","added","Service->general->upsmode","1, (2)"]
[null,1754,4,1754,"unit cooling","internal","bit",null,"0/1",null,"r","r","added",null,"2, (1)"]
[null,1755,5,1755,"unit heating","internal","bit",null,"0/1",null,"r","r","added",null,"2, (1)"]
[null,1756,6,1756,"unit humidification","internal","bit",null,"0/1",null,"r","r","added",null,"2, (1)"]
[null,1757,7,1757,"unit dehumidification","internal","bit",null,"0/1",null,"r","r","added",null,"2, (1)"]
[null,1758," ",3516,"number of EDIO","internal","byte",null,"0..4","0..4","r","r",null,"Info->system","4, (3)"]
[null,1759," ",3518,"number of EAIO","internal","byte",null,"0..4","0..4","r","r",null,"Info->system","4, (3)"]
[null,1760," ",3520,"type of EBUS","internal","byte",null,"0..1","0: none; 1: RS485","r","r",null,"Info->system","4, (3)"]
[null,1761,null,3522,"number of compressors","internal","byte",null,"0..2",null,"r","r",{"$nulls":3},"r","r","not accessible"]
[null,1762,null,3524,"number of suction valve","internal","byte",null,"0..2",null,"r","r",{"$nulls":3},"r","r","not accessible"]
[null,1763,null,3526,"number of drycoolers","internal","byte",null,"0..4",null,"r","r",{"$nulls":3},"r","r","not accessible"]
[null,1764,null,3528,"number of pumps","internal","byte",null,"0..4",null,"r","r",{"$nulls":3},"r","r","not accessible"]
[null,1765,null,3530,"number of e-heatings","internal","byte",null,"0..4",null,"r","r",{"$nulls":3},"r","r","not accessible"]
[null,1766,null,3532,"number of humidifiers","internal","byte",null,"0..3",null,"r","r",{"$nulls":3},"r","r","not accessible"]
[null,1767,null,3534,"number of fans","internal","byte",null,"0..3",null,"r","r",{"$nulls":3},"r","r","not accessible"]
[null,1768,null,3536,"number of louvers","internal","byte",null,"0..3",null,"r","r",{"$nulls":3},"r","r","not accessible"]
[null,1769,null,3538,"number of sensors","internal","byte",null,"0..21",null,"r","r",{"$nulls":3},"r","r","not accessible"]
[null,1770,null,3540,"number of ext alarm in","internal","byte",null,"0..10",null,"r","r",{"$nulls":3},"r",null,"not accessible"]
[null,1771,null,3542,"number of ge/cw valves","internal","byte",null,"0..1",null,"r","r",{"$nulls":3},"r","r","not accessible"]
[null,1772,null,3544,"number of hotgas reheat","internal","byte",null,"0..1",null,"r","r",{"$nulls":3},"r","r","not accessible"]
[null,1773,null,3546,"number of pww heatings","internal","byte",null,"0..1",null,"r","r",{"$nulls":3},"r","r","not accessible"]
[null,1774,null,3548,"number of dehumidifiers","internal","byte",null,"0..1",null,"r","r",{"$nulls":3},"r","r","not accessible"]
[{"$nulls":3}," "]
["unit raw data (IO-states):",null,null," "]
[null,1800,0,1800,"DIN1","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1801,1,1801,"DIN2","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1802,2,1802,"DIN3","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1803,3,1803,"DIN4","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1804,4,1804,"DIN5","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1805,5,1805,"DIN6","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1806,6,1806,"DIN7","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1807,7,1807,"DIN8","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1808,0,1808,"DIN9","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1809,1,1809,"DIN10","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1810,2,1810,"DIN11","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1811,3,1811,"DIN12","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1812,4,1812,"DIN13","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1813,5,1813,"DIN14","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1814,6,1814,"DIN15","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1815,7,1815,"DIN16","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1816,0,1816,"DIN17","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1817,1,1817,"DIN18","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1818,2,1818,"DIN19","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1819,3,1819,"DIN20","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1820,4,1820,"DIN21","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1821,5,1821,"DIN22","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1822,6,1822,"DIN23","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1823,7,1823,"DIN24","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1824,0,1824,"DIN25","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1825,1,1825,"DIN26","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1826,2,1826,"DIN27","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1827,3,1827,"DIN28","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1828,4,1828,"DIN29","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1829,5,1829,"DIN30","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1830,6,1830,"DIN31","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1831,7,1831,"DIN32","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1832,0,1832,"DIN33","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1833,1,1833,"DIN34","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1834,2,1834,"DIN35","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1835,3,1835,"DIN36","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1836,4,1836,"DIN37","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1837,5,1837,"DIN38","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1838,6,1838,"DIN39","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1839,7,1839,"DIN40","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1840," ",1840,"DIN41","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1841,1,1841,"DIN42","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1842,2,1842,"DIN43","input","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","2, (1)",null,null,"not implemented"]
[null,1843,3,1843,"DOUT1","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1844,4,1844,"DOUT2","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1845,5,1845,"DOUT3","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1846,6,1846,"DOUT4","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1847,7,1847,"DOUT5","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1848,0,1848,"DOUT6","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1849,1,1849,"DOUT7","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1850,2,1850,"DOUT8","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1851,3,1851,"DOUT9","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1852,4,1852,"DOUT10","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1853,5,1853,"DOUT11","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1854,6,1854,"DOUT12","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1855,7,1855,"DOUT13","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1856,0,1856,"DOUT14","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1857,1,1857,"DOUT15","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1858,2,1858,"DOUT16","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1859,3,1859,"DOUT17","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1860,4,1860,"DOUT18","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1861,5,1861,"DOUT19","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1862,6,1862,"DOUT20","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1863,7,1863,"DOUT21","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1864,0,1864,"DOUT22","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1865,1,1865,"DOUT23","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1866,2,1866,"DOUT24","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1867,3,1867,"DOUT25","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1868,4,1868,"DOUT26","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1869,5,1869,"DOUT27","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1870,6,1870,"DOUT28","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1871,7,1871,"DOUT29","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1872,0,1872,"DOUT30","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[null,1873,1,1873,"DOUT31","output","bit",null,"0 / 1","inactive/active","r","r","is influenced by components' configurations","Info->state->rawdata","1, (2)",null,null,"not implemented"]
[{"$nulls":3}," "]
[null,1900,null,3800,"AIN1","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1901,null,3802,"AIN2","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1902,null,3804,"AIN3","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1903,null,3806,"AIN4","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1904,null,3808,"AIN5","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1905,null,3810,"AIN6","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1906," ",3812,"AIN7","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1907," ",3814,"AIN8","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1908," ",3816,"AIN9","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1909," ",3818,"AIN10","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1910," ",3820,"AIN11","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1911," ",3822,"AIN12","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1912," ",3824,"AIN13","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1913," ",3826,"AIN14","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1914," ",3828,"AIN15","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1915," ",3830,"AIN16","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1916," ",3832,"AIN17","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1917," ",3834,"AIN18","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1918," ",3836,"AIN19","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1919," ",3838,"AIN20","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1920," ",3840,"AIN21","input","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","4, (3)",null,null,"not implemented"]
[null,1921," ",3842,"AOUT1","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[null,1922," ",3844,"AOUT2","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[null,1923," ",3846,"AOUT3","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[null,1924," ",3848,"AOUT4","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[null,1925," ",3850,"AOUT5","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[null,1926," ",3852,"AOUT6","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[null,1927," ",3854,"AOUT7","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[null,1928," ",3856,"AOUT8","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[null,1929," ",3858,"AOUT9","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[null,1930," ",3860,"AOUT10","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[null,1931," ",3862,"AOUT11","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[null,1932," ",3864,"AOUT12","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[null,1933," ",3866,"AOUT13","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[null,1934," ",3868,"AOUT14","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[null,1935," ",3870,"AOUT15","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[null,1936," ",3872,"AOUT16","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[null,1937," ",3874,"AOUT17","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[null,1938," ",3876,"AOUT18","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[null,1939," ",3878,"AOUT19","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[null,1940," ",3880,"AOUT20","output","word",null,"0..4095",null,"r","r","is influenced by components' configurations","Info->state->rawdata","3, (4)",null,null,"not implemented"]
[{"$nulls":3}," "]
[null,2000," ",4000,"config. Of DIN1","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2001," ",4002,"config. Of DIN2","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2002," ",4004,"config. Of DIN3","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2003," ",4006,"config. Of DIN4","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2004," ",4008,"config. Of DIN5","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2005," ",4010,"config. Of DIN6","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2006," ",4012,"config. Of DIN7","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2007," ",4014,"config. Of DIN8","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2008," ",4016,"config. Of DIN9","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2009," ",4018,"config. Of DIN10","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2010," ",4020,"config. Of DIN11","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2011," ",4022,"config. Of DIN12","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2012," ",4024,"config. Of DIN13","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2013," ",4026,"config. Of DIN14","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2014," ",4028,"config. Of DIN15","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2015," ",4030,"config. Of DIN16","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2016," ",4032,"config. Of DIN17","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2017," ",4034,"config. Of DIN18","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2018," ",4036,"config. Of DIN19","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2019," ",4038,"config. Of DIN20","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2020," ",4040,"config. Of DIN21","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2021," ",4042,"config. Of DIN22","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2022," ",4044,"config. Of DIN23","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2023," ",4046,"config. Of DIN24","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2024," ",4048,"config. Of DIN25","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2025," ",4050,"config. Of DIN26","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2026," ",4052,"config. Of DIN27","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2027," ",4054,"config. Of DIN28","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2028," ",4056,"config. Of DIN29","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2029," ",4058,"config. Of DIN30","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2030," ",4060,"config. Of DIN31","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2031," ",4062,"config. Of DIN32","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2032," ",4064,"config. Of DIN33","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2033," ",4066,"config. Of DIN34","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2034," ",4068,"config. Of DIN35","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2035," ",4070,"config. Of DIN36","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2036," ",4072,"config. Of DIN37","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2037," ",4074,"config. Of DIN38","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2038," ",4076,"config. Of DIN39","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2039," ",4078,"config. Of DIN40","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2040," ",4080,"config. Of DIN41","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2041," ",4082,"config. Of DIN42","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2042," ",4084,"config. Of DIN43","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2043," ",4086,"config. Of DOUT1","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2044," ",4088,"config. Of DOUT2","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2045," ",4090,"config. Of DOUT3","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2046," ",4092,"config. Of DOUT4","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2047," ",4094,"config. Of DOUT5","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2048," ",4096,"config. Of DOUT6","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2049," ",4098,"config. Of DOUT7","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2050," ",4100,"config. Of DOUT8","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2051," ",4102,"config. Of DOUT9","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2052," ",4104,"config. Of DOUT10","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2053," ",4106,"config. Of DOUT11","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2054," ",4108,"config. Of DOUT12","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2055," ",4110,"config. Of DOUT13","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2056," ",4112,"config. Of DOUT14","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2057," ",4114,"config. Of DOUT15","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2058," ",4116,"config. Of DOUT16","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2059," ",4118,"config. Of DOUT17","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2060," ",4120,"config. Of DOUT18","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2061," ",4122,"config. Of DOUT19","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2062," ",4124,"config. Of DOUT20","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2063," ",4126,"config. Of DOUT21","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2064," ",4128,"config. Of DOUT22","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2065," ",4130,"config. Of DOUT23","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2066," ",4132,"config. Of DOUT24","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2067," ",4134,"config. Of DOUT25","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2068," ",4136,"config. Of DOUT26","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2069," ",4138,"config. Of DOUT27","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2070," ",4140,"config. Of DOUT28","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2071," ",4142,"config. Of DOUT29","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2072," ",4144,"config. Of DOUT30","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2073," ",4146,"config. Of DOUT31","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2074," ",4148,"config. Of AIN1","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2075," ",4150,"config. Of AIN2","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2076," ",4152,"config. Of AIN3","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2077," ",4154,"config. Of AIN4","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2078," ",4156,"config. Of AIN5","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2079," ",4158,"config. Of AIN6","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2080," ",4160,"config. Of AIN7","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2081," ",4162,"config. Of AIN8","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2082," ",4164,"config. Of AIN9","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2083," ",4166,"config. Of AIN10","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2084," ",4168,"config. Of AIN11","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2085," ",4170,"config. Of AIN12","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2086," ",4172,"config. Of AIN13","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2087," ",4174,"config. Of AIN14","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2088," ",4176,"config. Of AIN15","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2089," ",4178,"config. Of AIN16","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2090," ",4180,"config. Of AIN17","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2091," ",4182,"config. Of AIN18","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2092," ",4184,"config. Of AIN19","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2093," ",4186,"config. Of AIN20","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2094," ",4188,"config. Of AIN21","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2095," ",4190,"config. Of AOUT1","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2096," ",4192,"config. Of AOUT2","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2097," ",4194,"config. Of AOUT3","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2098," ",4196,"config. Of AOUT4","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2099," ",4198,"config. Of AOUT5","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2100," ",4200,"config. Of AOUT6","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2101," ",4202,"config. Of AOUT7","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2102," ",4204,"config. Of AOUT8","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2103," ",4206,"config. Of AOUT9","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2104," ",4208,"config. Of AOUT10","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2105," ",4210,"config. Of AOUT11","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2106," ",4212,"config. Of AOUT12","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2107," ",4214,"config. Of AOUT13","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2108," ",4216,"config. Of AOUT14","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2109," ",4218,"config. Of AOUT15","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2110," ",4220,"config. Of AOUT16","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2111," ",4222,"config. Of AOUT17","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2112," ",4224,"config. Of AOUT18","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2113," ",4226,"config. Of AOUT19","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[null,2114," ",4228,"config. Of AOUT20","internal","byte",{"$nulls":3},"r","r","is influenced by components' configurations","not available","4, (3)",null,null,"not implemented"]
[{"$nulls":3}," "]
["unit configuration and data:",null,null," "]
[null,2200,0,2200,"airflow 1","redirected input","bit","气流1","0 / 1","ok/alarm","r","r","usually unused and substituted by fan-failure","alarm/event-window","2, (1)","r","r"]
[null,2201,1,2201,"airflow 2","redirected input","bit","气流2","0 / 1","ok/alarm","r","r","usually unused and substituted by fan-failure","alarm/event-window","2, (1)","r"]
[null,2202,2,2202,"airflow 3","redirected input","bit","气流3","0 / 1","ok/alarm","r","r","usually unused and substituted by fan-failure","alarm/event-window","2, (1)","r"]
[null,2203,3,2203,"highpressure 1","redirected input","bit","高压1","0 / 1","ok/alarm","r","r","wrong here (combined with compressor-failure), unused","alarm/event-window","2, (1)","r","r"]
[null,2204,4,2204,"highpressure 2","redirected input","bit","高压2","0 / 1","ok/alarm","r","r","wrong here (combined with compressor-failure), unused","alarm/event-window","2, (1)","r","r"]
[null,2205,5,2205,"highpressure 3","redirected input","bit","高压3","0 / 1","ok/alarm","r","r","wrong here (combined with compressor-failure), unused","alarm/event-window","2, (1)","r",null,"not accessible, TMO"]
[null,2206,6,2206,"water detector","redirected input","bit","水份测定仪","0 / 1","ok/alarm","r","r",null,"alarm/event-window","2, (1)","r","r"]
[null,2207,7,2207,"Phasecheck","redirected input","bit","Phasecheck","0 / 1","ok/alarm","r","r",null,"alarm/event-window","2, (1)","r","r","not accessible, TMO"]
[null,2208,0,2208,"fire/smoke","redirected input","bit","火/烟","0 / 1","ok/alarm","r","r",null,"alarm/event-window","2, (1)","r","r","then: local stop, no reset over bms possible"]
[null,2209,1,2209,null,null,"bit"]
[null,2210,2,2210,null,null,"bit"]
[null,2211,3,2211,null,null,"bit"]
[null,2212,4,2212,null,null,"bit"]
[null,2213,5,2213,null,null,"bit"]
[null,2214,6,2214,null,null,"bit"]
[null,2215,7,2215,null,null,"bit"]
[null,2216,0,2216,"return air temp. too high alarm","internal","bit","回风温度。过高报警","0 / 1","ok/alarm","r","r",null,"alarm/event-window","2, (1)","r","r"]
[null,2217,1,2217,"return air humid. too high alarm","internal","bit","返回空气湿润。过高报警","0 / 1","ok/alarm","r","r",null,"alarm/event-window","2, (1)","r","r"]
[null,2218,2,2218,"supply air temp. too high alarm","internal","bit","供应空气温度。过高报警","0 / 1","ok/alarm","r","r",null,"alarm/event-window","2, (1)","r","r"]
[null,2219,3,2219,"supply air humid. too high alarm","internal","bit","供应空气湿润。过高报警","0 / 1","ok/alarm","r","r",null,"alarm/event-window","2, (1)","r","r"]
[null,2220,4,2220,"water temp. too high alarm","internal","bit","水温。过高报警","0 / 1","ok/alarm","r","r",null,"alarm/event-window","2, (1)","r","r"]
[null,2221,5,2221,"return air temp. too low alarm","internal","bit","回风温度。过低报警","0 / 1","ok/alarm","r","r",null,"alarm/event-window","2, (1)","r","r"]
[null,2222,6,2222,"return air humid. too low alarm","internal","bit","返回空气湿润。过低报警","0 / 1","ok/alarm","r","r",null,"alarm/event-window","2, (1)","r","r"]
[null,2223,7,2223,"supply air temp. too low alarm","internal","bit","供应空气温度。过低报警","0 / 1","ok/alarm","r","r",null,"alarm/event-window","2, (1)","r","r"]
[null,2224,0,2224,"supply air humid. too low alarm","internal","bit","供应空气湿润。过低报警","0 / 1","ok/alarm","r","r",null,"alarm/event-window","2, (1)","r","r"]
[null,2225,1,2225,"water temp. too low alarm","internal","bit","水温。过低报警","0 / 1","ok/alarm","r","r",null,"alarm/event-window","2, (1)","r","r"]
[null,2226,2,2226,"freeze alarm","internal","bit","冻结报警","0 / 1","ok/alarm","r","r",null,"alarm/event-window","2, (1)","r","r","not accessible, TMO"]
[null,2227,3,2227,null,null,"bit"]
[null,2228,4,2228,null,null,"bit"]
[null,2229,5,2229,null,null,"bit"]
[null,2230,6,2230,null,null,"bit"]
[null,2231,7,2231,null,null,"bit"]
[null,2232," ",4464,"unit evaporation temperature 1","redirected input","word","机组蒸发温度1","-1000..1000","-100,0..100,0°C","r","r",null,"Info->state->cooling","4, (3)","r"]
[null,2233," ",4466,"unit evaporation pressure 1","redirected input","word","单元蒸发压力1","0..1000","0,0..100,0bar","r","r",null,"Info->state->cooling","4, (3)","r","r","Niederdruck!!"]
[null,2234," ",4468,"unit condensation temperature 1","redirected input","word","单位冷凝温度1","-1000..1000","-100,0..100,0°C","r","r",null,"Info->state->cooling","4, (3)","r"]
[null,2235," ",4470,"unit condensation pressure 1","redirected input","word","单元冷凝压力1","0..1000","0,0..100,0bar","r","r",null,"Info->state->cooling","4, (3)","r","r","Hochdruck!!"]
[null,2236," ",4472,"unit electronic-expansion-valve 1","redir. Output","word","单元的电子膨胀阀1",null,null,"r","r","so far not used","Info->state->cooling","4, (3)","r",null,"not accessible"]
[null,2237," ",4474,"unit electronic-expansion-valve 2","redir. Output","word","单元的电子膨胀阀2",null,null,"r","r","so far not used","Info->state->cooling","4, (3)","r",null,"not accessible"]
[null,2238," ",4476,"unit freecooling-valve","redir. Output","word","单位自然冷却阀",null,null,"r","r","so far not used","Info->state->cooling","4, (3)","r",null,"not accessible"]
[null,2239," ",4478,"limit; return air temp. too high alarm","internal","word","限制;回风温度。过高报警","150..400","15,0..40,0°C","rw","r",null,"Control->temperature","3, (4)"]
[null,2240," ",4480,"limit; return air temp. too low alarm","internal","word","限制;回风温度。过低报警","0..200","0,0..20,0°C","rw","r",null,"Control->temperature","3, (4)"]
[null,2241," ",4482,"limit; supply air temp. too high alarm","internal","word","限制送风温度。过高报警","50..400","5,0..40,0°C","rw","r",null,"Control->temperature","3, (4)"]
[null,2242," ",4484,"limit; supply air temp. too low alarm","internal","word","限制送风温度。过低报警","0..200","0,0..20,0°C","rw","r",null,"Control->temperature","3, (4)"]
[null,2243," ",4486,"limit; water temp. too high alarm","internal","word","限制水的温度。过高报警","100.500","10,0..50,0°C","rw","r",null,"Control->temperature","3, (4)"]
[null,2244," ",4488,"limit; water temp. too low alarm","internal","word","限制水的温度。过低报警","-200.300","-20,0..30,0°C","rw","r",null,"Control->temperature","3, (4)"]
[null,2245," ",4490,"limit; return air humid. too high alarm","internal","word","限制，收益空气湿润。过高报警","500..1000","50,0..100,0%rF","rw","r",null,"Control->humidity","3, (4)"]
[null,2246," ",4492,"limit; return air humid. too low alarm","internal","word","限制，收益空气湿润。过低报警","0..500","0,0..50,0%rF","rw","r",null,"Control->humidity","3, (4)"]
[null,2247," ",4494,"limit; supply air humid. too high alarm","internal","word","限制供应空气湿润。过高报警","500..1000","50,0..100,0%rF","rw","r",null,"Control->humidity","3, (4)"]
[null,2248," ",4496,"limit; supply air humid. too low alarm","internal","word","限制供应空气湿润。过低报警","0..500","0,0..50,0%rF","rw","r",null,"Control->humidity","3, (4)"]
[null,2249," ",4498,"lowpressure winterdelay","internal","word","低压winterdelay","0..300","seconds","rw","r",null,null,"3, (4)","rw"]
[null,2250," ",4500,"unit condensation pressure 2","redirected input","word","单元冷凝压力","0..1000","0,0..100,0bar","r","r",null,"Info->state->cooling","4, (3)","r","r"]
[null,2251," ",4502,"unit overload switch on","internal","word","单位过载开关","0..99","0,0..9,9K","rw","r",4409,"Control->components->cooling->compressors","3, (4)","rw",null,"not accessible"]
[null,2252," ",4504,"limit; return air temp. too high alarm priorities","internal","byte","限制;回风温度。过高的报警优先级","0..31",null,"rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2253," ",4506,"limit; return air temp. too high alarm delay","internal","byte","限制;回风温度。过高的报警延迟","0..100","seconds","rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2254," ",4508,"limit; return air temp. too low alarm priorities","internal","byte","限制;回风温度。过低的报警优先级","0..31",null,"rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2255," ",4510,"limit; return air temp. too low alarm delay","internal","byte","限制;回风温度。过低的报警延迟","0..100","seconds","rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2256," ",4512,"limit; supply air temp. too high alarm priorities","internal","byte","限制送风温度。过高的报警优先级","0..31",null,"rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2257," ",4514,"limit; supply air temp. too high alarm delay","internal","byte","限制送风温度。过高的报警延迟","0..100","seconds","rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2258," ",4516,"limit; supply air temp. too low alarm priorities","internal","byte","限制送风温度。过低的报警优先级","0..31",null,"rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2259," ",4518,"limit; supply air temp. too low alarm delay","internal","byte","限制送风温度。过低的报警延迟","0..100","seconds","rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2260," ",4520,"limit; water temp. too high alarm priorities","internal","byte","限制水的温度。过高的报警优先级","0..31",null,"rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2261," ",4522,"limit; water temp. too high alarm delay","internal","byte","限制水的温度。过高的报警延迟","0..100","seconds","rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2262," ",4524,"limit; water temp. too low alarm priorities","internal","byte","限制水的温度。过低的报警优先级","0..31",null,"rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2263," ",4526,"limit; water temp. too low alarm delay","internal","byte","限制水的温度。过低的报警延迟","0..100","seconds","rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2264," ",4528,"limit; return air humid. too high alarm priorities","internal","byte","限制，收益空气湿润。过高的报警优先级","0..31",null,"rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2265," ",4530,"limit; return air humid. too high alarm delay","internal","byte","限制，收益空气湿润。过高的报警延迟","0..100","seconds","rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2266," ",4532,"limit; return air humid. too low alarm priorities","internal","byte","限制，收益空气湿润。过低的报警优先级","0..31",null,"rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2267," ",4534,"limit; return air humid. too low alarm delay","internal","byte","限制，收益空气湿润。过低的报警延迟","0..100","seconds","rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2268," ",4536,"limit; supply air humid. too high alarm priorities","internal","byte","限制供应空气湿润。过高的报警优先级","0..31",null,"rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2269," ",4538,"limit; supply air humid. too high alarm delay","internal","byte","限制供应空气湿润。过高的报警延迟","0..100","seconds","rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2270," ",4540,"limit; supply air humid. too low alarm priorities","internal","byte","限制供应空气湿润。过低的报警优先级","0..31",null,"rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2271," ",4542,"limit; supply air humid. too low alarm delay","internal","byte","限制供应空气湿润。过低的报警延迟","0..100","seconds","rw","r",null,"Control->components->heating","3, (4)",null,null,"not accessible"]
[null,2272," ",4544,"unit condensation temperature 2","redirected input","word","单元冷凝温度2","-1000..1000","-100,0..100,0°C","r","r",null,"Info->state->cooling","4, (3)","r"]
[null,2273," ",4546,"unit evaporation pressure 2","redirected input","word","单元蒸发压力2","0..1000","0,0..100,0bar","r","r",null,"Info->state->cooling","4, (3)","r","r","Niederdruck!!"]
[null,2274," ",4548,"unit evaporation temperature 2","redirected input","word","单元蒸发温度2","-1000..1000","-100,0..100,0°C","r","r",null,"Info->state->cooling","4, (3)","r"]
[]
[null,2284,0,2284,"limit; return air temp. too high common alarm","internal","bit","限制;回风温度。过高的公共报警","0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)",null,null,"not accessible"]
[null,2285,1,2285,"limit; return air temp. too low common alarm","internal","bit","限制;回风温度。过低的共同报警","0 / 1",null,"rw","r",null,"alarm/event-window; Info->state->sensors","2, (1)",null,null,"not accessible"]
[null,2286,2,2286,"limit; supply air temp. too high common alarm","internal","bit","限制送风温度。过高的公共报警","0 / 1",null,"rw","r",null,"alarm/event-window; Info->state->sensors","2, (1)",null,null,"not accessible"]
[null,2287,3,2287,"limit; supply air temp. too low common alarm","internal","bit","限制送风温度。过低的共同报警","0 / 1",null,"rw","r",null,"Control->Components->sensors","1, (2)",null,null,"not accessible"]
[null,2288,4,2288,"limit; water temp. too high common alarm","internal","bit","限制水的温度。过高的公共报警","0 / 1",null,"rw","r",null,"Control->Components->sensors","1, (2)",null,null,"not accessible"]
[null,2289,5,2289,"limit; water temp. too low common alarm","internal","bit","限制水的温度。过低的共同报警","0 / 1",null,"rw","r",{"$nulls":5},"not accessible"]
[null,2290,6,2290,"limit; return air humid. too high common alarm","internal","bit","限制，收益空气湿润。过高的公共报警","0 / 1",null,"rw","r",{"$nulls":5},"not accessible"]
[null,2291,7,2291,"limit; return air humid. too low common alarm","internal","bit","限制，收益空气湿润。过低的共同报警","0 / 1",null,"rw","r",{"$nulls":5},"not accessible"]
[null,2292,0,2292,"limit; supply air humid. too high common alarm","internal","bit","限制供应空气湿润。过高的公共报警","0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)",null,null,"not accessible"]
[null,2293,1,2293,"limit; supply air humid. too low common alarm","internal","bit","限制供应空气湿润。过低的共同报警","0 / 1",null,"rw","r",null,"alarm/event-window; Info->state->sensors","2, (1)",null,null,"not accessible"]
[null,2294,2,2294,null,"internal","bit",null,"0 / 1",null,"rw","r",null,"alarm/event-window; Info->state->sensors"]
[null,2295,3,2295,null,"internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors",null," "]
[null,2296,4,2296,null,"internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors",null," "]
[null,2297,5,2297,null,"internal","bit",null,"0 / 1",null,"rw","r"]
[null,2298,6,2298,null,null,"bit"]
[null,2299,7,2299,null,null,"bit"]
[{"$nulls":3}," "]
["components of unit:",null,null," "]
["Sensor 1",null,null," "]
[null,2300,0,2300,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"]
[null,2301,1,2301,"sensor limit alarm","internal","bit",null,"0 / 1","ok/alarm","r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"]
[null,2302,2,2302,"sensor defect alarm","internal","bit",null,"0 / 1","ok/alarm","r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"]
[null,2303,3,2303,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "]
[null,2304,4,2304,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "]
[null,2305,5,2305,"sensor manual operation active","internal","bit",null,"0 / 1",null,"rw","r",{"$nulls":5},"not accessible"]
[null,2306,6,2306,null,null,"bit"]
[null,2307,7,2307,null,null,"bit"]
[null,2308," ",4616,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"]
[null,2309," ",4618,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"]
[null,2310," ",4620,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2311," ",4622,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,2312," ",4624,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,2313," ",4626,"sensor min phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,2314," ",4628,"sensor max phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,2315," ",4630,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2316," ",4632,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2317," ",4634,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2318," ",4636,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2319," ",4638,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2320," ",4640,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,2321," ",4642,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,2322," ",4644,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,2323," ",4646,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 2",null,null," ",{"$nulls":11}," "," "]
[null,2400,0,2400,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,2401,1,2401,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,2402,2,2402,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,2403,3,2403,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,2404,4,2404,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,2405,5,2405,"sensor manual operation active",null,"bit",{"$nulls":8}," "," ","not accessible"]
[null,2406,6,2406,null,null,"bit",{"$nulls":8}," "," "]
[null,2407,7,2407,null,null,"bit",{"$nulls":8}," "," "]
[null,2408," ",4816,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2409," ",4818,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2410," ",4820,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2411," ",4822,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,2412," ",4824,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,2413," ",4826,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,2414," ",4828,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,2415," ",4830,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2416," ",4832,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2417," ",4834,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2418," ",4836,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2419," ",4838,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2420," ",4840,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,2421," ",4842,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,2422," ",4844,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,2423," ",4846,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 3",null,null," ",{"$nulls":11}," "," "]
[null,2500,0,2500,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,2501,1,2501,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,2502,2,2502,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,2503,3,2503,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,2504,4,2504,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,2505,5,2505,"sensor manual operation active",null,"bit",{"$nulls":8}," "," ","not accessible"]
[null,2506,6,2506,null,null,"bit",{"$nulls":8}," "," "]
[null,2507,7,2507,null,null,"bit",{"$nulls":8}," "," "]
[null,2508," ",5016,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2509," ",5018,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2510," ",5020,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2511," ",5022,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,2512," ",5024,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,2513," ",5026,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,2514," ",5028,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,2515," ",5030,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2516," ",5032,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2517," ",5034,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2518," ",5036,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2519," ",5038,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2520," ",5040,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,2521," ",5042,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,2522," ",5044,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,2523," ",5046,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 4",null,null," ",{"$nulls":11}," "," "]
[null,2600,0,2600,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,2601,1,2601,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,2602,2,2602,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,2603,3,2603,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,2604,4,2604,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,2605,5,2605,"sensor manual operation active",null,"bit",{"$nulls":8}," "," ","not accessible"]
[null,2606,6,2606,null,null,"bit",{"$nulls":8}," "," "]
[null,2607,7,2607,null,null,"bit",{"$nulls":8}," "," "]
[null,2608," ",5216,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2609," ",5218,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2610," ",5220,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2611," ",5222,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,2612," ",5224,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,2613," ",5226,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,2614," ",5228,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,2615," ",5230,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2616," ",5232,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2617," ",5234,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2618," ",5236,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2619," ",5238,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2620," ",5240,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,2621," ",5242,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,2622," ",5244,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,2623," ",5246,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 5",null,null," ",{"$nulls":11}," "," "]
[null,2700,0,2700,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,2701,1,2701,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,2702,2,2702,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,2703,3,2703,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,2704,4,2704,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,2705,5,2705,"sensor manual operation active",null,"bit",{"$nulls":8}," "," ","not accessible"]
[null,2706,6,2706,null,null,"bit",{"$nulls":8}," "," "]
[null,2707,7,2707,null,null,"bit",{"$nulls":8}," "," "]
[null,2708," ",5416,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2709," ",5418,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2710," ",5420,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2711," ",5422,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,2712," ",5424,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,2713," ",5426,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,2714," ",5428,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,2715," ",5430,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2716," ",5432,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2717," ",5434,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2718," ",5436,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2719," ",5438,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2720," ",5440,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,2721," ",5442,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,2722," ",5444,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,2723," ",5446,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 6",null,null," ",{"$nulls":11}," "," "]
[null,2800,0,2800,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,2801,1,2801,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,2802,2,2802,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,2803,3,2803,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,2804,4,2804,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,2805,5,2805,"sensor manual operation active",null,"bit",{"$nulls":8}," "," ","not accessible"]
[null,2806,6,2806,null,null,"bit",{"$nulls":8}," "," "]
[null,2807,7,2807,null,null,"bit",{"$nulls":8}," "," "]
[null,2808," ",5616,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2809," ",5618,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2810," ",5620,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2811," ",5622,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,2812," ",5624,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,2813," ",5626,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,2814," ",5628,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,2815," ",5630,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2816," ",5632,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2817," ",5634,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2818," ",5636,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2819," ",5638,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2820," ",5640,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,2821," ",5642,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,2822," ",5644,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,2823," ",5646,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 7",null,null," ",{"$nulls":11}," "," "]
[null,2900,0,2900,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,2901,1,2901,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,2902,2,2902,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,2903,3,2903,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,2904,4,2904,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,2905,5,2905,"sensor manual operation active",null,"bit",{"$nulls":8}," "," ","not accessible"]
[null,2906,6,2906,null,null,"bit",{"$nulls":8}," "," "]
[null,2907,7,2907,null,null,"bit",{"$nulls":8}," "," "]
[null,2908," ",5816,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2909," ",5818,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2910," ",5820,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2911," ",5822,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,2912," ",5824,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,2913," ",5826,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,2914," ",5828,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,2915," ",5830,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,2916," ",5832,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2917," ",5834,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2918," ",5836,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2919," ",5838,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,2920," ",5840,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,2921," ",5842,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,2922," ",5844,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,2923," ",5846,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 8",null,null," ",{"$nulls":11}," "," "]
[null,3000,0,3000,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,3001,1,3001,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3002,2,3002,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3003,3,3003,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3004,4,3004,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3005,5,3005,"sensor manual operation active",null,"bit",{"$nulls":8}," "," ","not accessible"]
[null,3006,6,3006,null,null,"bit",{"$nulls":8}," "," "]
[null,3007,7,3007,null,null,"bit",{"$nulls":8}," "," "]
[null,3008," ",6016,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3009," ",6018,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3010," ",6020,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3011," ",6022,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3012," ",6024,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3013," ",6026,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3014," ",6028,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3015," ",6030,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3016," ",6032,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3017," ",6034,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3018," ",6036,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3019," ",6038,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3020," ",6040,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,3021," ",6042,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,3022," ",6044,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,3023," ",6046,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 9",null,null," ",{"$nulls":11}," "," "]
[null,3100,0,3100,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,3101,1,3101,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3102,2,3102,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3103,3,3103,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3104,4,3104,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3105,5,3105,"sensor manual operation active",null,"bit",{"$nulls":8}," "," ","not accessible"]
[null,3106,6,3106,null,null,"bit",{"$nulls":8}," "," "]
[null,3107,7,3107,null,null,"bit",{"$nulls":8}," "," "]
[null,3108," ",6216,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3109," ",6218,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3110," ",6220,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3111," ",6222,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3112," ",6224,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3113," ",6226,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3114," ",6228,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3115," ",6230,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3116," ",6232,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3117," ",6234,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3118," ",6236,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3119," ",6238,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3120," ",6240,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,3121," ",6242,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,3122," ",6244,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,3123," ",6246,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 10",null,null," ",{"$nulls":11}," "," "]
[null,3200,0,3200,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,3201,1,3201,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3202,2,3202,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3203,3,3203,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3204,4,3204,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3205,5,3205,"sensor manual operation active",null,"bit",{"$nulls":8}," "," ","not accessible"]
[null,3206,6,3206,null,null,"bit",{"$nulls":8}," "," "]
[null,3207,7,3207,null,null,"bit",{"$nulls":8}," "," "]
[null,3208," ",6416,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3209," ",6418,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3210," ",6420,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3211," ",6422,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3212," ",6424,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3213," ",6426,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3214," ",6428,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3215," ",6430,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3216," ",6432,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3217," ",6434,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3218," ",6436,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3219," ",6438,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3220," ",6440,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,3221," ",6442,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,3222," ",6444,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,3223," ",6446,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 11",null,null," ",{"$nulls":11}," "," "]
[null,3300,0,3300,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,3301,1,3301,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3302,2,3302,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3303,3,3303,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3304,4,3304,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3305,5,3305,"sensor manual operation active",null,"bit",{"$nulls":8}," "," ","not accessible"]
[null,3306,6,3306,null,null,"bit",{"$nulls":8}," "," "]
[null,3307,7,3307,null,null,"bit",{"$nulls":8}," "," "]
[null,3308," ",6616,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3309," ",6618,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3310," ",6620,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3311," ",6622,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3312," ",6624,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3313," ",6626,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3314," ",6628,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3315," ",6630,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3316," ",6632,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3317," ",6634,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3318," ",6636,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3319," ",6638,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3320," ",6640,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,3321," ",6642,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,3322," ",6644,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,3323," ",6646,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 12",null,null," ",{"$nulls":11}," "," "]
[null,3400,0,3400,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,3401,1,3401,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3402,2,3402,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3403,3,3403,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3404,4,3404,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3405,5,3405,"sensor manual operation active",null,"bit",{"$nulls":8}," "," ","not accessible"]
[null,3406,6,3406,null,null,"bit",{"$nulls":8}," "," "]
[null,3407,7,3407,null,null,"bit",{"$nulls":8}," "," "]
[null,3408," ",6816,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3409," ",6818,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3410," ",6820,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3411," ",6822,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3412," ",6824,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3413," ",6826,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3414," ",6828,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3415," ",6830,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3416," ",6832,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3417," ",6834,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3418," ",6836,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3419," ",6838,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3420," ",6840,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,3421," ",6842,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,3422," ",6844,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,3423," ",6846,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 13",null,null," ",{"$nulls":11}," "," "]
[null,3500,0,3500,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,3501,1,3501,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3502,2,3502,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3503,3,3503,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3504,4,3504,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3505,5,3505,"sensor manual operation active",null,"bit",{"$nulls":8}," "," "]
[null,3506,6,3506,null,null,"bit",{"$nulls":8}," "," "]
[null,3507,7,3507,null,null,"bit",{"$nulls":8}," "," "]
[null,3508," ",7016,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3509," ",7018,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3510," ",7020,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3511," ",7022,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3512," ",7024,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3513," ",7026,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3514," ",7028,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3515," ",7030,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3516," ",7032,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3517," ",7034,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3518," ",7036,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3519," ",7038,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3520," ",7040,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,3521," ",7042,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,3522," ",7044,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,3523," ",7046,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 14",null,null," ",{"$nulls":11}," "," "]
[null,3600,0,3600,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,3601,1,3601,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3602,2,3602,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3603,3,3603,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3604,4,3604,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3605,5,3605,"sensor manual operation active",null,"bit",{"$nulls":8}," "," ","not accessible"]
[null,3606,6,3606,null,null,"bit",{"$nulls":8}," "," "]
[null,3607,7,3607,null,null,"bit",{"$nulls":8}," "," "]
[null,3608," ",7216,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3609," ",7218,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3610," ",7220,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3611," ",7222,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3612," ",7224,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3613," ",7226,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3614," ",7228,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3615," ",7230,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3616," ",7232,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3617," ",7234,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3618," ",7236,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3619," ",7238,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3620," ",7240,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,3621," ",7242,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,3622," ",7244,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,3623," ",7246,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 15",null,null," ",{"$nulls":11}," "," "]
[null,3700,0,3700,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,3701,1,3701,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3702,2,3702,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3703,3,3703,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3704,4,3704,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3705,5,3705,"sensor manual operation active",null,"bit",{"$nulls":8}," "," ","not accessible"]
[null,3706,6,3706,null,null,"bit",{"$nulls":8}," "," "]
[null,3707,7,3707,null,null,"bit",{"$nulls":8}," "," "]
[null,3708," ",7416,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3709," ",7418,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3710," ",7420,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3711," ",7422,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3712," ",7424,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3713," ",7426,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3714," ",7428,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3715," ",7430,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3716," ",7432,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3717," ",7434,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3718," ",7436,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3719," ",7438,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3720," ",7440,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,3721," ",7442,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,3722," ",7444,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,3723," ",7446,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 16",null,null," ",{"$nulls":11}," "," "]
[null,3800,0,3800,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,3801,1,3801,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3802,2,3802,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3803,3,3803,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3804,4,3804,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3805,5,3805,"sensor manual operation active",null,"bit",{"$nulls":8}," "," ","not accessible"]
[null,3806,6,3806,null,null,"bit",{"$nulls":8}," "," "]
[null,3807,7,3807,null,null,"bit",{"$nulls":8}," "," "]
[null,3808," ",7616,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3809," ",7618,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3810," ",7620,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3811," ",7622,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3812," ",7624,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3813," ",7626,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3814," ",7628,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3815," ",7630,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3816," ",7632,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3817," ",7634,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3818," ",7636,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3819," ",7638,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3820," ",7640,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,3821," ",7642,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,3822," ",7644,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,3823," ",7646,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 17",null,null," ",{"$nulls":11}," "," "]
[null,3900,0,3900,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,3901,1,3901,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3902,2,3902,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,3903,3,3903,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3904,4,3904,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,3905,5,3905,"sensor manual operation active",null,"bit",{"$nulls":8}," "," ","not accessible"]
[null,3906,6,3906,null,null,"bit",{"$nulls":8}," "," "]
[null,3907,7,3907,null,null,"bit",{"$nulls":8}," "," "]
[null,3908," ",7816,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3909," ",7818,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3910," ",7820,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3911," ",7822,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3912," ",7824,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,3913," ",7826,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3914," ",7828,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,3915," ",7830,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,3916," ",7832,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3917," ",7834,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3918," ",7836,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3919," ",7838,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,3920," ",7840,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,3921," ",7842,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,3922," ",7844,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,3923," ",7846,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 18",null,null," ",{"$nulls":11}," "," "]
[null,4000,0,4000,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,4001,1,4001,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,4002,2,4002,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,4003,3,4003,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,4004,4,4004,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,4005,5,4005,"sensor manual operation active",null,"bit",{"$nulls":8}," "," ","not accessible"]
[null,4006,6,4006,null,null,"bit",{"$nulls":8}," "," "]
[null,4007,7,4007,null,null,"bit",{"$nulls":8}," "," "]
[null,4008," ",8016,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,4009," ",8018,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,4010," ",8020,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,4011," ",8022,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,4012," ",8024,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,4013," ",8026,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,4014," ",8028,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,4015," ",8030,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,4016," ",8032,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,4017," ",8034,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,4018," ",8036,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,4019," ",8038,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,4020," ",8040,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,4021," ",8042,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,4022," ",8044,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,4023," ",8046,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 19",null,null," ",{"$nulls":11}," "," "]
[null,4100,0,4100,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,4101,1,4101,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,4102,2,4102,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,4103,3,4103,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,4104,4,4104,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,4105,5,4105,"sensor manual operation active",null,"bit",{"$nulls":8}," "," ","not accessible"]
[null,4106,6,4106,null,null,"bit",{"$nulls":8}," "," "]
[null,4107,7,4107,null,null,"bit",{"$nulls":8}," "," "]
[null,4108," ",8216,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,4109," ",8218,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,4110," ",8220,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,4111," ",8222,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,4112," ",8224,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,4113," ",8226,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,4114," ",8228,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,4115," ",8230,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,4116," ",8232,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,4117," ",8234,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,4118," ",8236,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,4119," ",8238,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,4120," ",8240,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,4121," ",8242,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,4122," ",8244,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,4123," ",8246,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 20",null,null," ",{"$nulls":11}," "," "]
[null,4200,0,4200,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,4201,1,4201,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,4202,2,4202,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,4203,3,4203,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,4204,4,4204,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,4205,5,4205,"sensor manual operation active",null,"bit",{"$nulls":8}," "," ","not accessible"]
[null,4206,6,4206,null,null,"bit",{"$nulls":8}," "," "]
[null,4207,7,4207,null,null,"bit",{"$nulls":8}," "," "]
[null,4208," ",8416,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,4209," ",8418,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,4210," ",8420,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,4211," ",8422,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,4212," ",8424,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,4213," ",8426,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,4214," ",8428,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,4215," ",8430,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,4216," ",8432,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,4217," ",8434,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,4218," ",8436,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,4219," ",8438,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,4220," ",8440,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,4221," ",8442,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,4222," ",8444,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,4223," ",8446,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," ",{"$nulls":11}," "," "]
["Sensor 21",null,null," ",{"$nulls":11}," "," "]
[null,4300,0,4300,"sensor config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->sensors","1, (2)"," "," "]
[null,4301,1,4301,"sensor limit alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,4302,2,4302,"sensor defect alarm","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window; Info->state->sensors","2, (1)"," "," "]
[null,4303,3,4303,"sensor common defect alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,4304,4,4304,"sensor commonlimit alarm","internal","bit",null,"0 / 1",null,"rw","r","active => common alarm influenced","Control->Components->sensors","1, (2)"," "," "]
[null,4305,5,4305,"sensor manual operation active",null,"bit",{"$nulls":8}," "," ","not accessible"]
[null,4306,6,4306,null,null,"bit",{"$nulls":8}," "," "]
[null,4307,7,4307,null,null,"bit",{"$nulls":8}," "," "]
[null,4308," ",8616,"sensor purpose","internal","byte",null,"1..16",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,4309," ",8618,"sensor type","internal","byte",null,"1..5",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,4310," ",8620,"sensor analog input","internal","byte",null,"0..21",null,"rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,4311," ",8622,"sensor min value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,4312," ",8624,"sensor max value","internal","word",null,"0..200","0,0..20,0mA/V","rw","r","phys. Unit depends on type","Service->equipment->sensors","3, (4)"," "," "]
[null,4313," ",8626,"sensor min phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,4314," ",8628,"sensor max phys. value","internal","word",null,"-500..1000","-50,0..100,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Service->equipment->sensors","3, (4)"," "," "]
[null,4315," ",8630,"sensor tolerance","internal","byte",null,"0..100","percent","rw","r",null,"Service->equipment->sensors","3, (4)"," "," "]
[null,4316," ",8632,"sensor alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,4317," ",8634,"sensor alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,4318," ",8636,"sensor failure alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,4319," ",8638,"sensor failure alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->Components->sensors","3, (4)"," "," "]
[null,4320," ",8640,"sensor adjust offset","internal","word",null,"-100..100","-10,0..10,0°C/%rF/bar","rw","r","phys. Unit depends on purpose","Control->Components->sensors","3, (4)"," "," "]
[null,4321," ",8642,"sensor current phys. value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," "]
[null,4322," ",8644,"sensor current value","internal","word",null,"0..200","0,0..20,0mA/V","r","r","phys. Unit depends on type","Info->state->sensors","4, (3)"," "," "]
[null,4323," ",8646,"sensor manual operation value","internal","word",null,"-1000..1000","-100,0..100,0°C/%rF/bar","r","r","phys. Unit depends on purpose","Info->state->sensors","4, (3)"," "," ","not accessible"]
[{"$nulls":3}," "]
["Compressor 1",null,null," "]
[null,4400,0,4400,"compressor1 config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->cooling->compressors","1, (2)","rw","rw"]
[null,4401,1,4401,"compr.1 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","chaged","Control->components->cooling->compressors","1, (2), 5","rw"]
[null,4402,2,4402,"compr.1 manual operation state","internal","bit",null,"0 / 1",null,"rw","rw","added","Control->components->cooling->compressors","1, (2), 5","rw"]
[null,4403,3,4403,"compr.1 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->cooling->compressors","2, (1)","r","r"]
[null,4404,4,4404,"compr. 1 alarm","internal","bit",null,"0 / 1","ok/alarm","r","r","highpressure alarm is integrated","Info->state->cooling->compressors","2, (1)","r","r"]
[null,4405,5,4405,"compr.1 low press. Alarm","internal","bit",null,"0 / 1","ok/alarm","r","r",null,"Info->state->cooling->compressors","2, (1)","r","r"]
[null,4406,6,4406,null,"internal","bit",{"$nulls":3},"rw",null,null,"Service->equipment->cooling->compressors"]
[null,4407,7,4407,"compr. 1 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->cooling->compressors","1, (2)"]
[null,4408,0,4408,"compr. 1 common alarm low press.","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->cooling->compressors","1, (2)"]
[null,4409,1,4409,null,null,"bit"]
[null,4410,2,4410,null,null,"bit"]
[null,4411,3,4411,null,null,"bit"]
[null,4412,4,4412,null,null,"bit"]
[null,4413,5,4413,null,null,"bit"]
[null,4414,6,4414,null,null,"bit"]
[null,4415,7,4415,null,null,"bit"]
[null,4416," ",8832,"compressor1 start temp. Summer","internal","word",null,"0..99","0,0..9,9K","rw","r",4409,"Control->components->cooling->compressors","3, (4)","rw"]
[null,4417," ",8834,"compressor1 hysteresis Summer","internal","word",null,"0..99","0,0..9,9K","rw","r",4410,"Control->components->cooling->compressors","3, (4)","rw"]
[null,4418," ",8836,"compressor1 start temp. Winter","internal","word",null,"0..99","0,0..9,9K","rw","r",4411,"Control->components->cooling->compressors","3, (4)","rw"]
[null,4419," ",8838,"compressor1 hysteresis winter","internal","word",null,"0..99","0,0..9,9K","rw","r",4412,"Control->components->cooling->compressors","3, (4)","rw"]
[null,4420," ",8840,"compr.1 digital out","internal","byte",null,"0..31",null,"rw","r",4413,"Service->equipment->cooling->compressors","3, (4)"]
[null,4421," ",8842,"compr.1 alarm digital in","internal","byte",null,"0..42",null,"rw","r",4414,"Service->equipment->cooling->compressors","3, (4)"]
[null,4422," ",8844,"compr.1 alarm priorities","internal","byte",null,"0..31",null,"rw","r",4415,"Control->components->cooling->compressors","3, (4)"]
[null,4423," ",8846,"compr.1 alarm delay","internal","byte",null,"0..100","seconds","rw","r",4416,"Control->components->cooling->compressors","3, (4)","rw"]
[null,4424," ",8848,"compr.1 low press. Digital in","internal","byte",null,"0..42",null,"rw","r",4417,"Service->equipment->cooling->compressors","3, (4)"]
[null,4425," ",8850,"compr.1 low press. Alarm priorities","internal","byte",null,"0..31",null,"rw","r",4418,"Control->components->cooling->compressors","3, (4)"]
[null,4426," ",8852,"compr.1 low press. Alarm delay","internal","byte",null,"0..100","seconds","rw","r",4419,"Control->components->cooling->compressors","3, (4)","rw"]
[null,4427," ",8854,"compr.1 break","internal","word",null,"10..1000","seconds","rw","r",4420,"Control->components->cooling->compressors","3, (4)"]
[null,4428," ",8856,"compr.1 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r",4421,"Info->state->cooling->compressors; Service->equipment->cooling->compressors","3, (4)","rw"]
[null,4429,null,8858,"compr.1 low press manag. time","internal","byte",null,"0..100","hours","rw","r"]
[null,4430,null,8860,"compr.1 low press manag. press.","internal","word",null,"0..100","0,0..10,0bar","rw","r"]
[null,4431,null,8862,"compr.1 low press manag. restarts","internal","byte",null,"0..10",null,"rw","r"]
[null,4432,null,8864,"compr.1 high press manag. time","internal","byte",null,"0..100","hours","rw","r"]
[null,4433,null,8866,"compr.1 high press manag. press.","internal","word",null,"0..100","0,0..10,0bar","rw","r"]
[null,4434,null,8868,"compr.1 high press manag. restarts","internal","byte",null,"0..10",null,"rw","r"]
[null,4435,null,8870,"compr.1 high press manag. mode","internal","byte",null,"0..1",null,"rw","r"]
[{"$nulls":3}," "]
["Compressor 2",null,null," "]
[null,4500,0,4500,"compressor 2 config. active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->cooling->compressors","1, (2)","rw","rw"]
[null,4501,1,4501,"compr. 2 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->cooling->compressors","1, (2), 5","rw"]
[null,4502,2,4502,"compr. 2 manual operation state","internal","bit",null,"0 / 1",null,"rw","rw","added","Control->components->cooling->compressors","1, (2), 5","rw"]
[null,4503,3,4503,"compr. 2 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->cooling->compressors","2, (1)","r","r"]
[null,4504,4,4504,"compr. 2 alarm","internal","bit",null,"0 / 1",null,"r","r","highpressure alarm is integrated","Info->state->cooling->compressors","2, (1)","r","r"]
[null,4505,5,4505,"compr. 2 low press. Alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->cooling->compressors","2, (1)","r","r"]
[null,4506,6,4506,null,"internal","bit",{"$nulls":3},"rw",null,null,"Service->equipment->cooling->compressors"]
[null,4507,7,4507,"compr. 2 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->cooling->compressors","1, (2)"]
[null,4508,0,4508,"compr. 2 common alarm low press.","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->cooling->compressors","1, (2)"]
[null,4508,1,9016,{"$nulls":6},"rw",null,null,"Control->components->cooling->compressors"]
[null,4510,2,4510,null,null,"bit"]
[null,4511,3,4511,null,null,"bit"]
[null,4512,4,4512,null,null,"bit"]
[null,4513,5,4513,null,null,"bit"]
[null,4514,6,4514,null,null,"bit"]
[null,4515,7,4515,null,null,"bit"]
[null,4516," ",9032,"compressor 2 start temp. Summer","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"rw","3, (4)","rw"]
[null,4517," ",9034,"compressor 2 hysteresis Summer","internal","word",null,"0..99","0,0..9,9K","rw","r",4410,"Control->components->cooling->compressors","3, (4)","rw"]
[null,4518," ",9036,"compressor 2 start temp. Winter","internal","word",null,"0..99","0,0..9,9K","rw","r",4411,"Control->components->cooling->compressors","3, (4)","rw"]
[null,4519," ",9038,"compressor 2 hysteresis winter","internal","word",null,"0..99","0,0..9,9K","rw","r",4412,"Control->components->cooling->compressors","3, (4)","rw"]
[null,4520," ",9040,"compr. 2 digital out","internal","byte",null,"0..31",null,"rw","r",4413,"Service->equipment->cooling->compressors","3, (4)"]
[null,4521," ",9042,"compr. 2 alarm digital in","internal","byte",null,"0..42",null,"rw","r",4414,"Service->equipment->cooling->compressors","3, (4)"]
[null,4522," ",9044,"compr. 2 alarm priorities","internal","byte",null,"0..31",null,"rw","r",4415,"Control->components->cooling->compressors","3, (4)"]
[null,4523," ",9046,"compr. 2 alarm delay","internal","byte",null,"0..100","seconds","rw","r",4416,"Control->components->cooling->compressors","3, (4)","rw"]
[null,4524," ",9048,"compr. 2 low press. Digital in","internal","byte",null,"0..42",null,"rw","r",4417,"Service->equipment->cooling->compressors","3, (4)"]
[null,4525," ",9050,"compr. 2 low press. Alarm priorities","internal","byte",null,"0..31",null,"rw","r",4418,"Control->components->cooling->compressors","3, (4)"]
[null,4526," ",9052,"compr. 2 low press. Alarm delay","internal","byte",null,"0..100","seconds","rw","r",4419,"Control->components->cooling->compressors","3, (4)","rw"]
[null,4527," ",9054,"compr. 2 break","internal","word",null,"10..1000","seconds","rw","r",4420,"Control->components->cooling->compressors","3, (4)"]
[null,4528," ",9056,"compr. 2 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r",4421,"Info->state->cooling->compressors; Service->equipment->cooling->compressors","3, (4)","rw"]
[null,4529,null,9058,"compr.1 low press manag. time","internal","byte",null,"0..100","hours","rw","r"]
[null,4530,null,9060,"compr.1 low press manag. press.","internal","word",null,"0..100","0,0..10,0bar","rw","r"]
[null,4531,null,9062,"compr.1 low press manag. restarts","internal","byte",null,"0..10",null,"rw","r"]
[null,4532,null,9064,"compr.1 high press manag. time","internal","byte",null,"0..100","hours","rw","r"]
[null,4533,null,9066,"compr.1 high press manag. press.","internal","word",null,"0..100","0,0..10,0bar","rw","r"]
[null,4534,null,9068,"compr.1 high press manag. restarts","internal","byte",null,"0..10",null,"rw","r"]
[null,4535,null,9070,"compr.1 high press manag. mode","internal","byte",null,"0..1",null,"rw","r"]
[{"$nulls":3}," "]
["Suction valve 1",null,null," "]
[null,4600,0,4600,"suctionvalve1 config. Active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->cooling->suctionvalves","1, (2)","rw","rw"]
[null,4601,1,4601,"suctionvalve1 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw",null,"Control->components->cooling->suctionvalves","1, (2), 5","rw"]
[null,4602,2,4602,null,"internal","bit"]
[null,4603,3,4603,null,"internal","bit"]
[null,4604,4,4604,null,"internal","bit"]
[null,4605,5,4605,null,"internal","bit"]
[null,4606,6,4606,null,"internal","bit"]
[null,4607,7,4607,null,"internal","bit"]
[null,4608," ",9216,"suctionvalve1 start temperature","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->cooling->suctionvalves","3, (4)","rw","rw"]
[null,4609," ",9218,"suctionvalve1 linear range","internal","word",null,"5..99","0,5..9,9K","rw","r",null,"Control->components->cooling->suctionvalves","3, (4)","rw","rw"]
[null,4610," ",9220,"suctionvalve1 analog out","internal","byte",null,"0..20",null,"rw","r",null,"Service->equipment->cooling->suctionvalves","3, (4)"]
[null,4611," ",9222,"suctionvalve1 current value","internal","byte",null,"0..100","percent","r","r",null,"Info->state->cooling->suctionvalves","4, (3)","r","r"]
[null,4612," ",9224,"suctionvalve1 manual operation value","internal","byte",null,"0..100","percent","rw","rw","added","Control->components->cooling->suctionvalves","3, (4), 16","rw"]
[{"$nulls":3}," "]
["Suction valve 2",null,null," "]
[null,4700,0,4700,"suctionvalve2 config. Active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->cooling->suctionvalves","1, (2)","rw",null,"not accessible"]
[null,4701,1,4701,"suctionvalve2 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw",null,"Control->components->cooling->suctionvalves","1, (2), 5","rw",null,"not accessible"]
[null,4702,2,4702,null,"internal","bit"]
[null,4703,3,4703,null,"internal","bit"]
[null,4704,4,4704,null,"internal","bit"]
[null,4705,5,4705,null,"internal","bit"]
[null,4706,6,4706,null,"internal","bit"]
[null,4707,7,4707,null,"internal","bit"]
[null,4708," ",9416,"suctionvalve2 start temperature","internal","word",null,"0..99","0,0..9,9K","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,4709," ",9418,"suctionvalve2 linear range","internal","word",null,"5..99","0,5..9,9K","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,4710," ",9420,"suctionvalve2 analog out","internal","byte",null,"0..20",null,"rw","r",null,"Service->equipment->cooling->suctionvalves","3, (4)",null,null,"not accessible"]
[null,4711," ",9422,"suctionvalve2 current value","internal","byte",null,"0..100","percent","r","r",null,"Info->state->cooling->suctionvalves","4, (3)","r",null,"not accessible"]
[null,4712," ",9424,"suctionvalve2 manual operation value","internal","byte",null,"0..100","percent","rw","rw","added","Control->components->cooling->suctionvalves","3, (4), 16","rw",null,"not accessible"]
[{"$nulls":3}," "]
["Electrical heating 1",null,null," "]
[null,4800,0,4800,"elec.-heating1 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->heating","1, (2)","rw","rw"]
[null,4801,1,4801,"elec.-heating1 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","chaged","Control->components->heating","1, (2), 5","rw"]
[null,4802,2,4802,"elec.-heating1 alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->heating","2, (1)","r","r"]
[null,4803,3,4803,"elec.-heating1 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->heating","2, (1)","r","r"]
[null,4804,4,4804,"elec.-heating1 manual operation running","internal","bit",null,"0 / 1",null,"rw","rw",null,"Control->components->heating","1, (2), 5","rw"]
[null,4805,5,4805,"elec.-heating1 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->heating","1, (2)"]
[null,4806,6,4806,null,"internal","bit"]
[null,4807,7,4807,null,"internal","bit"]
[null,4808," ",9616,"elec.-heating1 type","internal","byte",null,"1..2",null,"rw","r",null,"Service->equipment->heating","3, (4)","rw","rw"]
[null,4809," ",9618,"elec.-heating1 start temperature","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,4810," ",9620,"elec.-heating1 hysteresis","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,4811," ",9622,"elec.-heating1 linear range","internal","word",null,"5..99","0,5..9,9K","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,4812," ",9624,"elec.-heating1 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->heating","3, (4)"]
[null,4813," ",9626,"elec.-heating1 alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->heating","3, (4)"]
[null,4814," ",9628,"elec.-heating1 alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->heating","3, (4)"]
[null,4815," ",9630,"elec.-heating1 alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,4816," ",9632,"elec.-heating1 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r",null,"Info->state->heating; Service->equipment->heating","3, (4)","rw"]
[null,4817," ",9634,"elec.-heating1 PWM-grade","internal","byte",null,"0..100","percent","r","r",null,"Info->state->heating","4, (3)","r"]
[null,4818," ",9636,"elec.-heating1 manual operation PWM-grade","internal","byte",null,"0..100","percent","rw","rw","added","Control->components->heating","3, (4), 16","rw"]
[{"$nulls":3}," "]
["Electrical heating 2",null,null," "]
[null,4900,0,4900,"elec.-heating2 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->heating","1, (2)","rw","rw"]
[null,4901,1,4901,"elec.-heating2 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","chaged","Control->components->heating","1, (2), 5","rw"]
[null,4902,2,4902,"elec.-heating2 alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->heating","2, (1)","r","r"]
[null,4903,3,4903,"elec.-heating2 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->heating","2, (1)","r","r"]
[null,4904,4,4904,"elec.-heating2 manual operation running","internal","bit",null,"0 / 1",null,"rw","rw",null,"Control->components->heating","1, (2), 5"]
[null,4905,5,4905,"elec.-heating2 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->heating","1, (2)"]
[null,4906,6,4906,null,"internal","bit"]
[null,4907,7,4907,null,"internal","bit"]
[null,4908," ",9816,"elec.-heating2 type","internal","byte",null,"1..2",null,"rw","r",null,"Service->equipment->heating","3, (4)","rw","rw"]
[null,4909," ",9818,"elec.-heating2 start temperature","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,4910," ",9820,"elec.-heating2 hysteresis","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,4911," ",9822,"elec.-heating2 linear range","internal","word",null,"5..99","0,5..9,9K","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,4912," ",9824,"elec.-heating2 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->heating","3, (4)"]
[null,4913," ",9826,"elec.-heating2 alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->heating","3, (4)"]
[null,4914," ",9828,"elec.-heating2 alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->heating","3, (4)"]
[null,4915," ",9830,"elec.-heating2 alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,4916," ",9832,"elec.-heating2 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r",null,"Info->state->heating; Service->equipment->heating","3, (4)","rw"]
[{"$nulls":3}," "]
["Electrical heating 3",null,null," "]
[null,5000," ",5000,"elec.-heating3 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->heating","1, (2)","rw","rw"]
[null,5001," ",5001,"elec.-heating3 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","chaged","Control->components->heating","1, (2), 5","rw"]
[null,5002," ",5002,"elec.-heating3 alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->heating","2, (1)","r","r"]
[null,5003," ",5003,"elec.-heating3 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->heating","2, (1)","r","r"]
[null,5004," ",5004,"elec.-heating3 manual operation running","internal","bit",null,"0 / 1",null,"rw","rw",null,"Control->components->heating","1, (2), 5","rw"]
[null,5005," ",5005,"elec.-heating3 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->heating","1, (2)"]
[null,5006," ",5006,null,"internal","bit"]
[null,5007," ",5007,null,"internal","bit"]
[null,5008," ",10016,"elec.-heating3 type","internal","byte",null,"1..2",null,"rw","r",null,"Service->equipment->heating","3, (4)","rw","rw"]
[null,5009," ",10018,"elec.-heating3 start temperature","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,5010," ",10020,"elec.-heating3 hysteresis","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,5011," ",10022,"elec.-heating3 linear range","internal","word",null,"5..99","0,5..9,9K","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,5012," ",10024,"elec.-heating3 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->heating","3, (4)"]
[null,5013," ",10026,"elec.-heating3 alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->heating","3, (4)"]
[null,5014," ",10028,"elec.-heating3 alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->heating","3, (4)"]
[null,5015," ",10030,"elec.-heating3 alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,5016," ",10032,"elec.-heating3 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r",null,"Info->state->heating; Service->equipment->heating","3, (4)","rw"]
[{"$nulls":3}," "]
["Electrical heating 4",null,null," "]
[null,5100,0,5100,"elec.-heating4 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->heating","1, (2)","rw"]
[null,5101,1,5101,"elec.-heating4 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","chaged","Control->components->heating","1, (2), 5","rw"]
[null,5102,2,5102,"elec.-heating4 alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->heating","2, (1)","r"]
[null,5103,3,5103,"elec.-heating4 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->heating","2, (1)","r"]
[null,5104,4,5104,"elec.-heating4 manual operation running","internal","bit",null,"0 / 1",null,"rw","rw",null,"Control->components->heating","1, (2), 5"]
[null,5105,5,5105,"elec.-heating4 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->heating","1, (2)"]
[null,5106,6,5106,null,"internal","bit"]
[null,5107,7,5107,null,"internal","bit"]
[null,5108," ",10216,"elec.-heating4 type","internal","byte",null,"1..2",null,"rw","r",null,"Service->equipment->heating","3, (4)","rw"]
[null,5109," ",10218,"elec.-heating4 start temperature","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,5110," ",10220,"elec.-heating4 hysteresis","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,5111," ",10222,"elec.-heating4 linear range","internal","word",null,"5..99","0,5..9,9K","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,5112," ",10224,"elec.-heating4 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->heating","3, (4)"]
[null,5113," ",10226,"elec.-heating4 alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->heating","3, (4)"]
[null,5114," ",10228,"elec.-heating4 alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->heating","3, (4)"]
[null,5115," ",10230,"elec.-heating4 alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,5116," ",10232,"elec.-heating4 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r",null,"Info->state->heating; Service->equipment->heating","3, (4)","rw"]
[{"$nulls":3}," "]
["GE/CW-valve",null,null," "]
[null,5200,0,5200,"GE/CW-valve config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->cooling->gecwvalves","1, (2)","rw","rw"]
[null,5201,1,5201,"GE/CW-valve manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->cooling->gecwvalves","1, (2), 5","rw"]
[null,5202,2,5202,"GE/CW-valve close with compr.-start","internal","bit",null,"0 / 1",null,"rw","r",null,"Control->components->cooling->gecwvalves","1, (2)","rw"]
[null,5203,3,5203,null,"internal","bit"]
[null,5204,4,5204,null,"internal","bit"]
[null,5205,5,5205,null,"internal","bit"]
[null,5206,6,5206,null,"internal","bit"]
[null,5207,7,5207,null,"internal","bit"]
[null,5208," ",10416,"GE/CW-valve start temperature","internal","SI16",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->cooling->gecwvalves","3, (4)","rw"]
[null,5209," ",10418,"GE/CW-valve linear range","internal","SI16",null,"5..99","0,5..9,9K","rw","r",null,"Control->components->cooling->gecwvalves","3, (4)","rw"]
[null,5210," ",10420,"GE/CW-valve analog out","internal","byte",null,"0..20",null,"rw","r",null,"Service->equipment->cooling->gecwvalves","3, (4)","rw"]
[null,5211," ",10422,"GE/CW-valve GE-off-temp","internal","SI16",null,"0..500","0,0..50,0°C","rw","r",null,"Control->components->cooling->gecwvalves","3, (4)","rw"]
[null,5212," ",10424,"GE/CW-valve GE-dehum. Min.-temp.","internal","SI16",null,"0..500","0,0..50,0°C","rw","r","delete","Control->components->cooling->gecwvalves","3, (4)","rw"]
[null,5213," ",10426,"GE/CW-valve GE-dehum. Max.-temp.","internal","SI16",null,"0..500","0,0..50,0°C","rw","r","delete","Control->components->cooling->gecwvalves","3, (4)","rw"]
[null,5214," ",10428,"GE/CW-valve opening grade","internal","byte",null,"0..100","percent","r","r",null,"Info->state->cooling","4, (3)","r","r"]
[null,5215," ",10430,"GE/CW-valve manual operation opening grade","internal","byte",null,"0..100","percent","rw","rw","added","Control->components->cooling->gecwvalves","3, (4), 16","rw"]
[null,5216," ",10432,"GE/CW-valve analog out 2","internal","byte",null,"0..20",null,"rw","r",null,"Service->equipment->cooling->gecwvalves","3, (4)"]
[null,5217," ",10434,"GE/CW-valve din for switch","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->cooling->gecwvalves","3, (4)"]
[{"$nulls":3}," "]
["G-valve",null,null," "]
[null,5300," ",5300,"G-valve config active","internal","bit",null,"0 / 1",null,"rw","r","changed","Control->components->cooling->gvalves","1, (2)","rw","rw"]
[null,5301,1,5301,"G-valve manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed",null,"1, (2), 5","rw"]
[null,5302,2,5302,null,"internal","bit"]
[null,5303,3,5303,null,"internal","bit"]
[null,5304,4,5304,null,"internal","bit"]
[null,5305,5,5305,null,"internal","bit"]
[null,5306,6,5306,null,"internal","bit"]
[null,5307,7,5307,null,"internal","bit"]
[null,5308," ",10616,"G-valve pressure setpoint","internal","word",null,"50..250","5,0..25,0bar","rw","r",null,"Control->components->cooling->gvalves","3, (4)","rw","rw"]
[null,5309," ",10618,"G-valve analog out","internal","byte",null,"0..20",null,"rw","r",null,"Service->equipment->cooling->gvalves","3, (4)"]
[null,5310," ",10620,"G-valve pre opening time","internal","byte",null,"0..30","seconds","rw","rw",null,"Control->components->cooling->gvalves","3, (4), 16","rw"]
[null,5311," ",10622,"G-valve pre opening grade","internal","byte",null,"0..100","percent","rw","rw","added","Control->components->cooling->gvalves","3, (4), 16","rw"]
[null,5312," ",10624,"G-valve opening grade","internal","byte",null,"0..100","percent","r","r","added","Info->state->cooling","4, (3)","r"]
[null,5313," ",10626,"G-valve manual operation opening grade","internal","byte",null,"0..100","percent","rw","rw","added","Control->components->cooling->gvalves","3, (4), 16","rw"]
[null,5314," ",10628,"G-valve I factor","internal","byte",null,"0..100","percent","rw","rw","added","Control->components->cooling->gvalves","3, (4), 16","rw"]
[null,5315," ",10630,"G-valve D factor","internal","byte",null,"0..100","percent","rw","rw","added","Control->components->cooling->gvalves","3, (4), 16","rw"]
[{"$nulls":3}," "]
["Drycooler 1",null,null," "]
[null,5400,0,5400,"drycooler1 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->cooling->drycooler","1, (2)","rw","rw"]
[null,5401,1,5401,"drycooler1 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->cooling->drycooler","1, (2), 5","rw"]
[null,5402,2,5402,"drycooler1 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->cooling","2, (1)","r","r"]
[null,5403,3,5403,"drycooler1 alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->cooling","2, (1)","r","r"]
[null,5404,4,5404,"drycooler1 manual operation running","internal","bit",null,"0 / 1",null,"rw","rw","added","Control->components->cooling->drycooler","1, (2), 5","rw"]
[null,5405,5,5405,"drycooler1 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->cooling->drycooler","1, (2)"]
[null,5406,6,5406,null,"internal","bit"]
[null,5407,7,5407,null,"internal","bit"]
[null,5408," ",10816,"drycooler1 start-temperature winter","internal","word",null,"50..350","5,0..35,0°C","rw","r","changed","Control->components->cooling->drycooler","3, (4)","rw"]
[null,5409," ",10818,"drycooler1 start-temperature summer","internal","word",null,"100..500","10,0..50,0°C","rw","r","changed","Control->components->cooling->drycooler","3, (4)","rw"]
[null,5410," ",10820,"drycooler1 hysteresis","internal","word",null,"10..99","1,0..9,9K","rw","r",null,"Control->components->cooling->drycooler","3, (4)","rw"]
[null,5411," ",10822,"drycooler1 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->cooling->drycooler","3, (4)"]
[null,5412," ",10824,"drycooler1 alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->cooling->drycooler","3, (4)"]
[null,5413," ",10826,"drycooler1 alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->cooling->drycooler","3, (4)"]
[null,5414," ",10828,"drycooler1 alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->cooling->drycooler","3, (4)","rw"]
[null,5415," ",10830,"drycooler1 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r","added","Info->state->cooling; Service->equipment->cooling->drycooler","3, (4)","rw"]
[{"$nulls":3}," "]
["Drycooler 2",null,null," "]
[null,5500,0,5500,"drycooler2 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->cooling->drycooler","1, (2)","rw","rw"]
[null,5501,1,5501,"drycooler2 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->cooling->drycooler","1, (2), 5","rw"]
[null,5502,2,5502,"drycooler2 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->cooling","2, (1)","r","r"]
[null,5503,3,5503,"drycooler2 alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->cooling","2, (1)","r","r"]
[null,5504,4,5504,"drycooler2 manual operation running","internal","bit",null,"0 / 1",null,"rw","rw","added","Control->components->cooling->drycooler","1, (2), 5","rw"]
[null,5505,5,5505,"drycooler2 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->cooling->drycooler","1, (2)"]
[null,5506,6,5506,null,"internal","bit"]
[null,5507,7,5507,null,"internal","bit"]
[null,5508," ",11016,"drycooler2 start-temperature winter","internal","word",null,"50..350","5,0..35,0°C","rw","r","changed","Control->components->cooling->drycooler","3, (4)","rw"]
[null,5509," ",11018,"drycooler2 start-temperature summer","internal","word",null,"100..500","10,0..50,0°C","rw","r","changed","Control->components->cooling->drycooler","3, (4)","rw"]
[null,5510," ",11020,"drycooler2 hysteresis","internal","word",null,"10..99","1,0..9,9K","rw","r",null,"Control->components->cooling->drycooler","3, (4)","rw"]
[null,5511," ",11022,"drycooler2 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->cooling->drycooler","3, (4)"]
[null,5512," ",11024,"drycooler2 alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->cooling->drycooler","3, (4)"]
[null,5513," ",11026,"drycooler2 alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->cooling->drycooler","3, (4)"]
[null,5514," ",11028,"drycooler2 alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->cooling->drycooler","3, (4)","rw"]
[null,5515," ",11030,"drycooler2 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r","added","Info->state->cooling; Service->equipment->cooling->drycooler","3, (4)","rw"]
[{"$nulls":3}," "]
["Drycooler 3",null,null," "]
[null,5600,0,5600,"drycooler3 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->cooling->drycooler","1, (2)","rw"]
[null,5601,1,5601,"drycooler3 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->cooling->drycooler","1, (2), 5","rw"]
[null,5602,2,5602,"drycooler3 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->cooling","2, (1)","r"]
[null,5603,3,5603,"drycooler3 alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->cooling","2, (1)","r"]
[null,5604,4,5604,"drycooler3 manual operation running","internal","bit",null,"0 / 1",null,"rw","rw","added","Control->components->cooling->drycooler","1, (2), 5","rw"]
[null,5605,35,5605,"drycooler3 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->cooling->drycooler","1, (2)"]
[null,5606,6,5606,null,"internal","bit"]
[null,5607,7,5607,null,"internal","bit"]
[null,5608,null,11216,"drycooler3 start-temperature winter","internal","word",null,"50..350","5,0..35,0°C","rw","r","changed","Control->components->cooling->drycooler","3, (4)","rw"]
[null,5609," ",11218,"drycooler3 start-temperature summer","internal","word",null,"100..500","10,0..50,0°C","rw","r","changed","Control->components->cooling->drycooler","3, (4)","rw"]
[null,5610," ",11220,"drycooler3 hysteresis","internal","word",null,"10..99","1,0..9,9K","rw","r",null,"Control->components->cooling->drycooler","3, (4)","rw"]
[null,5611," ",11222,"drycooler3 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->cooling->drycooler","3, (4)"]
[null,5612," ",11224,"drycooler3 alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->cooling->drycooler","3, (4)"]
[null,5613," ",11226,"drycooler3 alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->cooling->drycooler","3, (4)"]
[null,5614," ",11228,"drycooler3 alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->cooling->drycooler","3, (4)","rw"]
[null,5615," ",11230,"drycooler3 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r","added","Info->state->cooling; Service->equipment->cooling->drycooler","3, (4)","rw"]
[{"$nulls":3}," "]
["Drycooler 4",null,null," "]
[null,5700,0,5700,"drycooler4 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->cooling->drycooler","1, (2)","rw"]
[null,5701,1,5701,"drycooler4 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->cooling->drycooler","1, (2), 5","rw"]
[null,5702,2,5702,"drycooler4 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->cooling","2, (1)","r"]
[null,5703,3,5703,"drycooler4 alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->cooling","2, (1)","r"]
[null,5704,4,5704,"drycooler4 manual operation running","internal","bit",null,"0 / 1",null,"rw","rw","added","Control->components->cooling->drycooler","1, (2), 5","rw"]
[null,5705,5,5705,"drycooler4 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->cooling->drycooler","1, (2)"]
[null,5706,6,5706,null,"internal","bit"]
[null,5707,7,5707,null,"internal","bit"]
[null,5708," ",11416,"drycooler4 start-temperature winter","internal","word",null,"50..350","5,0..35,0°C","rw","r","changed","Control->components->cooling->drycooler","3, (4)","rw"]
[null,5709," ",11418,"drycooler4 start-temperature summer","internal","word",null,"100..500","10,0..50,0°C","rw","r","changed","Control->components->cooling->drycooler","3, (4)","rw"]
[null,5710," ",11420,"drycooler4 hysteresis","internal","word",null,"10..99","1,0..9,9K","rw","r",null,"Control->components->cooling->drycooler","3, (4)","rw"]
[null,5711," ",11422,"drycooler4 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->cooling->drycooler","3, (4)"]
[null,5712," ",11424,"drycooler4 alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->cooling->drycooler","3, (4)"]
[null,5713," ",11426,"drycooler4 alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->cooling->drycooler","3, (4)"]
[null,5714," ",11428,"drycooler4 alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->cooling->drycooler","3, (4)","rw"]
[null,5715," ",11430,"drycooler4 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r","added","Info->state->cooling; Service->equipment->cooling->drycooler","3, (4)","rw"]
[{"$nulls":3}," "]
["Pump 1",null,null," "]
[null,5800,0,5800,"pump1 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->cooling->pumps","1, (2)","rw","rw"]
[null,5801,1,5801,"pump1 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->cooling->pumps","1, (2), 5","rw"]
[null,5802,2,5802,"pump1 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->cooling","2, (1)","r","r"]
[null,5803,3,5803,"pump1 alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->cooling","2, (1)","r","r"]
[null,5804,4,5804,"pump1 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->cooling->pumps","1, (2)"]
[null,5805,5,5805,"pump1 manual operation running","internal","bit",null,"0 / 1",null,"rw","r",{"$nulls":3},"rw"]
[null,5806,6,5806,null,"internal","bit"]
[null,5807,7,5807,null,"internal","bit"]
[null,5808," ",11616,"pump1 type","internal","byte",null,"1..3",null,"rw","r","added","Service->equipment->cooling->pumps","3, (4)","rw","rw"]
[null,5809," ",11618,"pump1 start-temperature","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,5810," ",11620,"pump1 hysteresis","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,5811," ",11622,"pump1 linear range","internal","word",null,"5..200","0,5..20,0K","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,5812," ",11624,"pump1 pressure setpoint","internal","word",null,"0..300","0,0..30,0bar","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,5813," ",11626,"pump1 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->cooling->pumps","3, (4)"]
[null,5814," ",11628,"pump1 analog out","internal","byte",null,"0..20",null,"rw","r",null,"Service->equipment->cooling->pumps","3, (4)"]
[null,5815," ",11630,"pump1 alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->cooling->pumps","3, (4)"]
[null,5816," ",11632,"pump1 alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->cooling->pumps","3, (4)"]
[null,5817," ",11634,"pump1 alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,5818," ",11636,"pump1 pre runtime","internal","byte",null,"0..20","seconds","rw","r","added","Service->equipment->cooling->pumps","3, (4)"]
[null,5819," ",11638,"pump1 pre speed","internal","byte",null,"0..100","percent","rw","r","added","Service->equipment->cooling->pumps","3, (4)"]
[null,5820," ",11640,"pump1 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r",null,"Info->state->cooling; Service->equipment->cooling->pumps","3, (4)","rw"]
[null,5821," ",11642,"pump1 speed","internal","byte",null,"0..100","percent","r","r",null,"Info->state->cooling","4, (3)","r","r"]
[null,5822," ",11644,"pump1 manual operation speed","internal","byte",null,"0..100","percent","rw","rw","added","Control->components->cooling->pumps","3, (4), 16","rw"]
[null,5823," ",11646,"pump1 partner-unit","internal","byte",null,"0..31",null,"rw","r","added","Service->equipment->cooling->pumps","3, (4)"]
[null,5824," ",11648,"pump1 partner-pump","internal","byte",null,"0..4",null,"rw","r",null,"Service->equipment->cooling->pumps","3, (4)"]
[null,5825," ",11650,"pump1 I factor","internal","byte",null,"0..100","percent","rw","r",null,"Info->state->cooling","4, (3)","rw"]
[null,5826," ",11652,"pump1 D factor","internal","byte",null,"0..100","percent","rw","r",null,"Info->state->cooling","4, (3)","rw"]
[{"$nulls":3}," "]
["Pump 2",null,null," "]
[null,5900,0,5900,"pump2 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->cooling->pumps","1, (2)","rw","rw"]
[null,5901,1,5901,"pump2 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->cooling->pumps","1, (2), 5"]
[null,5902,2,5902,"pump2 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->cooling","2, (1)","r","r"]
[null,5903,3,5903,"pump2 alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->cooling","2, (1)","r","r"]
[null,5904,4,5904,"pump2 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->cooling->pumps","1, (2)"]
[null,5905,5,5905,"pump2 manual operation running","internal","bit",null,"0 / 1",null,"rw","r",{"$nulls":3},"rw"]
[null,5906,6,5906,null,"internal","bit"]
[null,5907,7,5907,null,"internal","bit"]
[null,5908," ",11816,"pump2 type","internal","byte",null,"1..3",null,"rw","r","added","Service->equipment->cooling->pumps","3, (4)","rw","rw"]
[null,5909," ",11818,"pump2 start-temperature","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,5910," ",11820,"pump2 hysteresis","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,5911," ",11822,"pump2 linear range","internal","word",null,"5..200","0,5..20,0","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,5912," ",11824,"pump2 pressure setpoint","internal","word",null,"0..300","0,0..30,0bar","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,5913," ",11826,"pump2 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->cooling->pumps","3, (4)"]
[null,5914," ",11828,"pump2 analog out","internal","byte",null,"0..20",null,"rw","r",null,"Service->equipment->cooling->pumps","3, (4)"]
[null,5915," ",11830,"pump2 alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->cooling->pumps","3, (4)"]
[null,5916," ",11832,"pump2 alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->cooling->pumps","3, (4)"]
[null,5917," ",11834,"pump2 alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,5918," ",11836,"pump2 pre runtime","internal","byte",null,"0..20","seconds","rw","r","added","Service->equipment->cooling->pumps","3, (4)"]
[null,5919," ",11838,"pump2 pre speed","internal","byte",null,"0..100","percent","rw","r","added","Service->equipment->cooling->pumps","3, (4)"]
[null,5920," ",11840,"pump2 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r",null,"Info->state->cooling; Service->equipment->cooling->pumps","3, (4)","rw"]
[null,5921," ",11842,"pump2 speed","internal","byte",null,"0..100","percent","r","r",null,"Info->state->cooling","4, (3)","r","r"]
[null,5922," ",11844,"pump2 manual operation speed","internal","byte",null,"0..100","percent","rw","rw","added","Control->components->cooling->pumps","3, (4), 16","rw"]
[null,5923," ",11846,"pump2 partner-unit","internal","byte",null,"0..31",null,"rw","r","added","Service->equipment->cooling->pumps","3, (4)"]
[null,5924," ",11848,"pump2 partner-pump","internal","byte",null,"0..4",null,"rw","r",null,"Service->equipment->cooling->pumps","3, (4)"]
[null,5925," ",11850,"pump2 I factor","internal","byte",null,"0..100","percent","rw","r",null,"Info->state->cooling","4, (3)","rw"]
[null,5926," ",11852,"pump2 D factor","internal","byte",null,"0..100","percent","rw","r",null,"Info->state->cooling","4, (3)","rw"]
[{"$nulls":3}," "]
["Pump 3",null,null," "]
[null,6000,0,6000,"pump3 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->cooling->pumps","1, (2)","rw"]
[null,6001,1,6001,"pump3 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->cooling->pumps","1, (2), 5"]
[null,6002,2,6002,"pump3 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->cooling","2, (1)","r"]
[null,6003,3,6003,"pump3 alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->cooling","2, (1)","r"]
[null,6004,4,6004,"pump3 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->cooling->pumps","1, (2)"]
[null,6005,5,6005,"pump3 manual operation running","internal","bit",null,"0 / 1",null,"rw","r",{"$nulls":3},"rw"]
[null,6006,6,6006,null,"internal","bit"]
[null,6007,7,6007,null,"internal","bit"]
[null,6008," ",12016,"pump3 type","internal","byte",null,"1..3",null,"rw","r","added","Service->equipment->cooling->pumps","3, (4)","rw"]
[null,6009," ",12018,"pump3 start-temperature","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,6010," ",12020,"pump3 hysteresis","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,6011," ",12022,"pump3 linear range","internal","word",null,"5..200","0,5..20,0","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,6012," ",12024,"pump3 pressure setpoint","internal","word",null,"0..300","0,0..30,0bar","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,6013," ",12026,"pump3 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->cooling->pumps","3, (4)"]
[null,6014," ",12028,"pump3 analog out","internal","byte",null,"0..20",null,"rw","r",null,"Service->equipment->cooling->pumps","3, (4)"]
[null,6015," ",12030,"pump3 alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->cooling->pumps","3, (4)"]
[null,6016," ",12032,"pump3 alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->cooling->pumps","3, (4)"]
[null,6017," ",12034,"pump3 alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,6018," ",12036,"pump3 pre runtime","internal","byte",null,"0..20","seconds","rw","r","added","Service->equipment->cooling->pumps","3, (4)"]
[null,6019," ",12038,"pump3 pre speed","internal","byte",null,"0..100","percent","rw","r","added","Service->equipment->cooling->pumps","3, (4)"]
[null,6020," ",12040,"pump3 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r",null,"Info->state->cooling; Service->equipment->cooling->pumps","3, (4)","rw"]
[null,6021," ",12042,"pump3 speed","internal","byte",null,"0..100","percent","r","r",null,"Info->state->cooling","4, (3)","r"]
[null,6022," ",12044,"pump3 manual operation speed","internal","byte",null,"0..100","percent","rw","rw","added","Control->components->cooling->pumps","3, (4), 16","rw"]
[null,6023," ",12046,"pump3 partner-unit","internal","byte",null,"0..31",null,"rw","r","added","Service->equipment->cooling->pumps","3, (4)"]
[null,6024," ",12048,"pump3 partner-pump","internal","byte",null,"0..4",null,"rw","r",null,"Service->equipment->cooling->pumps","3, (4)"]
[null,6025," ",12050,"pump3 I factor","internal","byte",null,"0..100","percent","rw","r",null,"Info->state->cooling","4, (3)","rw"]
[null,6026," ",12052,"pump3 D factor","internal","byte",null,"0..100","percent","rw","r",null,"Info->state->cooling","4, (3)","rw"]
[{"$nulls":3}," "]
["Pump 4",null,null," "]
[null,6100,0,6100,"pump4 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->cooling->pumps","1, (2)","rw"]
[null,6101,1,6101,"pump4 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->cooling->pumps","1, (2), 5"]
[null,6102,2,6102,"pump4 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->cooling","2, (1)","r"]
[null,6103,3,6103,"pump4 alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->cooling","2, (1)","r"]
[null,6104,4,6104,"pump4 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->cooling->pumps","1, (2)"]
[null,6105,5,6105,"pump4 manual operation running","internal","bit",null,"0 / 1",null,"rw","r",{"$nulls":3},"rw"]
[null,6106,6,6106,null,"internal","bit"]
[null,6107,7,6107,null,"internal","bit"]
[null,6108," ",12216,"pump4 type","internal","byte",null,"1..3",null,"rw","r","added","Service->equipment->cooling->pumps","3, (4)","rw"]
[null,6109," ",12218,"pump4 start-temperature","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,6110," ",12220,"pump4 hysteresis","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,6111," ",12222,"pump4 linear range","internal","word",null,"5..200","0,5..20,0","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,6112," ",12224,"pump4 pressure setpoint","internal","word",null,"0..300","0,0..30,0bar","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,6113," ",12226,"pump4 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->cooling->pumps","3, (4)"]
[null,6114," ",12228,"pump4 analog out","internal","byte",null,"0..20",null,"rw","r",null,"Service->equipment->cooling->pumps","3, (4)"]
[null,6115," ",12230,"pump4 alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->cooling->pumps","3, (4)"]
[null,6116," ",12232,"pump4 alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->cooling->pumps","3, (4)"]
[null,6117," ",12234,"pump4 alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->cooling->pumps","3, (4)","rw"]
[null,6118," ",12236,"pump4 pre runtime","internal","byte",null,"0..20","seconds","rw","r","added","Service->equipment->cooling->pumps","3, (4)"]
[null,6119," ",12238,"pump4 pre speed","internal","byte",null,"0..100","percent","rw","r","added","Service->equipment->cooling->pumps","3, (4)","rw"]
[null,6120," ",12240,"pump4 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r",null,"Info->state->cooling; Service->equipment->cooling->pumps","3, (4)","rw"]
[null,6121," ",12242,"pump4 speed","internal","byte",null,"0..100","percent","r","r",null,"Info->state->cooling","4, (3)","r"]
[null,6122," ",12244,"pump4 manual operation speed","internal","byte",null,"0..100","percent","rw","rw","added","Control->components->cooling->pumps","3, (4), 16","rw"]
[null,6123," ",12246,"pump4 partner-unit","internal","byte",null,"0..31",null,"rw","r","added","Service->equipment->cooling->pumps","3, (4)"]
[null,6124," ",12248,"pump4 partner-pump","internal","byte",null,"0..4",null,"rw","r",null,"Service->equipment->cooling->pumps","3, (4)"]
[null,6125," ",12250,"pump4 I factor","internal","byte",null,"0..100","percent","rw","r",null,"Info->state->cooling","4, (3)","r"]
[null,6126," ",12252,"pump4 D factor","internal","byte",null,"0..100","percent","rw","r",null,"Info->state->cooling","4, (3)","r"]
[{"$nulls":3}," "]
["Hotgas-heating",null,null," "]
[null,6200,0,6200,"hotgas-heating config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->heating","1, (2)","rw","rw"]
[null,6201,1,6201,"hotgas-heating manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->heating","1, (2), 5","rw"]
[null,6202,2,6202,"hotgas-heating running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->heating","2, (1)","r","r"]
[null,6203,3,6203,"hotgas-heating manual operation running","internal","bit",null,"0 / 1",null,"rw","rw","added","Control->components->heating","1, (2), 5","rw"]
[null,6204,4,6204,null,"internal","bit"]
[null,6205,5,6205,null,"internal","bit"]
[null,6206,6,6206,null,"internal","bit"]
[null,6207,7,6207,null,"internal","bit"]
[null,6208," ",12416,"hotgas-heating start temperature","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,6209," ",12418,"hotgas-heating hysteresis","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,6210," ",12420,"hotgas-heating digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->heating","3, (4)"]
[{"$nulls":3}," "]
["PWW-heating",null,null," "]
[null,6300,0,6300,"PWW-heating config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->heating","1, (2)","rw","rw"]
[null,6301,1,6301,"PWW-heating manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->heating","1, (2), 5","rw"]
[null,6302,2,6302,"PWW-heating running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->heating","2, (1)","r","r"]
[null,6303,3,6303,"PWW-heating manual operation running","internal","bit",null,"0 / 1",null,"rw","rw","added","Control->components->heating","1, (2), 5","rw"]
[null,6304,4,6304,null,"internal","bit"]
[null,6305,5,6305,null,"internal","bit"]
[null,6306,6,6306,null,"internal","bit"]
[null,6307,7,6307,null,"internal","bit"]
[null,6308," ",12616,"PWW-heating type","internal","byte",null,"1..2",null,"rw","r",null,"Service->equipment->heating","3, (4)","rw","rw"]
[null,6309," ",12618,"PWW-heating start-temperature ","internal","word",null,"0..99","0,0..9,9K","rw","r","changed","Control->components->heating","3, (4)","rw"]
[null,6310," ",12620,"PWW-heating start-temperature 2","internal","word",{"$nulls":3},"rw","r","so far not used","Control->components->heating","3, (4)","rw",null,"not accessible, TMO"]
[null,6311," ",12622,"PWW-heating hysteresis","internal","word",null,"0..99","0,0..9,9K","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,6312," ",12624,"PWW-heating linear range","internal","word",null,"5..99","0,5..9,9K","rw","r",null,"Control->components->heating","3, (4)","rw"]
[null,6313," ",12626,"PWW-heating digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->heating","3, (4)"]
[null,6314," ",12628,"PWW-heating analog out","internal","byte",null,"0..20",null,"rw","r",null,"Service->equipment->heating","3, (4)"]
[null,6315," ",12630,"PWW-heating current value","internal","byte",null,"0..100","percent","r","r",null,"Info->state->heating","3, (4)","r","r"]
[null,6316," ",12632,"PWW-heating manual operation value","internal","byte",null,"0..100","percent","rw","rw",null,"Control->components->heating","3, (4), 16","rw"]
[{"$nulls":3}," "]
["Humidifier 1",null,null," "]
[null,6400,0,6400,"humidifier1 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->humidifier","1, (2)","r","r"]
[null,6401,1,6401,"humidifier1 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->humidifier","1, (2), 5","rw"]
[null,6402,2,6402,"humidifier1 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->humidity","2, (1)","r","r"]
[null,6403,3,6403,"humidifier1 alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->humidity","2, (1)","r","r"]
[null,6404,4,6404,"humidifier1 manual operation running","internal","bit",null,"0 / 1",null,"rw","rw","added","Control->components->humidifier","1, (2), 5","rw"]
[null,6405,5,6405,"humidifier1 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->humidifier","1, (2)","r"]
[null,6406,6,6406,"humidifier1 conductivity config","internal","bit",null,"0 / 1",null,"rw","r",{"$nulls":3},"r"]
[null,6407,7,6407,"humidifier1 common alarm 5µS","internal","bit",null,"0 / 1",null,"rw","r",{"$nulls":3},"r"]
[null,6408,0,6408,"humidifier1 common alarm 20µS","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->humidifier","1, (2)","r"]
[null,6409,1,6409,"humidifier1 alarm 5µS","internal","bit",null,"0 / 1",null,"r","r",null,"Control->components->humidifier","1, (2), 5","r"]
[null,6410,2,6410,"humidifier1 alarm 20µS","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->humidity","2, (1)","r"]
[null,6411,3,6411,null,"internal","bit",{"$nulls":3},"r",null,null,"Info->state->humidity"]
[null,6412,4,6412,null,"internal","bit",{"$nulls":3},"rw",null,null,"Control->components->humidifier"]
[null,6413,5,6413,null,"internal","bit",{"$nulls":3},"rw",null,null,"Control->components->humidifier"]
[null,6414,6,6414,null,"internal","bit",{"$nulls":3},"rw"]
[null,6415,7,6415,null,"internal","bit"]
[null,6416," ",12832,"humidifier1 type","internal","byte",null,"1..2",null,"rw","r",null,"Service->equipment->humidifier","3, (4)","rw","rw"]
[null,6417," ",12834,"humidifier1 start-humidity","internal","word",null,"0..200","0,0..20,0%rF","rw","r","changed","Control->components->humidifier","3, (4)","rw"]
[null,6418," ",12836,"humidifier1 start-humidity 2","internal","word",{"$nulls":3},"rw","r","so far not used","Control->components->humidifier","3, (4)","rw",null,"not accessible, TMO"]
[null,6419," ",12838,"humidifier1 hysteresis","internal","word",null,"0..200","0,0..20,0%rF","rw","r",null,"Control->components->humidifier","3, (4)","rw"]
[null,6420," ",12840,"humidifier1 linear range","internal","word",null,"5..200","0,5..20,0","rw","r",null,"Control->components->humidifier","3, (4)","rw"]
[null,6421," ",12842,"humidifier1 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->humidifier","3, (4)"]
[null,6422," ",12844,"humidifier1 analog out","internal","byte",null,"0..20",null,"rw","r",null,"Service->equipment->humidifier","3, (4)"]
[null,6423," ",12846,"humidifier1 alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->humidifier","3, (4)"]
[null,6424," ",12848,"humidifier1 alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->humidifier","3, (4)"]
[null,6425," ",12850,"humidifier1 alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->humidifier","3, (4)","rw"]
[null,6426," ",12852,"humidifier1 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r",null,"Info->state->humidity; Service->equipment->humidifier","3, (4)","rw"]
[null,6427," ",12854,"humidifier1 current value","internal","byte",null,"0..100","percent","r","r",null,"Info->state->humidity","3, (4)","r","r"]
[null,6428," ",12856,"humidifier1 manual operation value","internal","byte",null,"0..100","percent","rw","rw",null,"Control->components->humidifier","3, (4), 16","rw"]
[null,6429," ",12858,"humidifier1 alarm digital in 5µS","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->humidifier","3, (4)"]
[null,6430," ",12860,"humidifier1 alarm digital in 20µS","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->humidifier","3, (4)"]
[null,6431," ",12862,"humidifier1 alarm delay 5µS","internal","UI16",null,"0..1000","seconds","rw","r",null,"Control->components->humidifier","3, (4)"]
[null,6432," ",12864,"humidifier1 alarm delay 20µS","internal","UI16",null,"0..1000","seconds","rw","r",null,"Control->components->humidifier","3, (4)"]
[null,6433," ",12866,"humidifier1 alarm priorities 5µS","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->humidifier","3, (4)"]
[null,6434," ",12868,"humidifier1 alarm priorities 20µS","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->humidifier","3, (4)"]
[]
["Humidifier 2",null,null," "]
[null,6500,0,6500,"humidifier2 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->humidifier","1, (2)"]
[null,6501,1,6501,"humidifier2 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->humidifier","1, (2), 5"]
[null,6502,2,6502,"humidifier2 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->humidity","2, (1)"]
[null,6503,3,6503,"humidifier2 alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->humidity","2, (1)"]
[null,6504,4,6504,"humidifier2 manual operation running","internal","bit",null,"0 / 1",null,"rw","rw","added","Control->components->humidifier","1, (2), 5"]
[null,6505,5,6505,"humidifier2 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->humidifier","1, (2)"]
[null,6506,6,6506,"humidifier2 conductivity config","internal","bit",null,"0 / 1",null,"rw","r"]
[null,6507,7,6507,"humidifier2 common alarm 5µS","internal","bit",null,"0 / 1",null,"rw","r"]
[null,6508,0,6508,"humidifier2 common alarm 20µS","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->humidifier","1, (2)"]
[null,6509,1,6509,"humidifier1 alarm 5µS","internal","bit",null,"0 / 1",null,"r","r","changed","Control->components->humidifier","1, (2), 5"]
[null,6510,2,6510,"humidifier1 alarm 20µS","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->humidity","2, (1)"]
[null,6511,3,6511,null,"internal","bit",{"$nulls":3},"r",null,null,"Info->state->humidity"]
[null,6512,4,6512,null,"internal","bit",{"$nulls":3},"rw",null,null,"Control->components->humidifier"]
[null,6513,5,6513,null,"internal","bit",{"$nulls":3},"rw",null,null,"Control->components->humidifier"]
[null,6514,6,6514,null,"internal","bit",{"$nulls":3},"rw"]
[null,6515,7,6515,null,"internal","bit"]
[null,6516," ",13032,"humidifier2 type","internal","byte",null,"1..2",null,"rw","r",null,"Service->equipment->humidifier","3, (4)"]
[null,6517," ",13034,"humidifier2 start-humidity","internal","word",null,"0..200","0,0..20,0%rF","rw","r","changed","Control->components->humidifier","3, (4)"]
[null,6518," ",13036,"humidifier2 start-humidity 2","internal","word",{"$nulls":3},"rw","r","delete","Control->components->humidifier","3, (4)",null,null,"not accessible, TMO"]
[null,6519," ",13038,"humidifier2 hysteresis","internal","word",null,"0..200","0,0..20,0%rF","rw","r",null,"Control->components->humidifier","3, (4)"]
[null,6520," ",13040,"humidifier2 linear range","internal","word",null,"5..200","0,5..20,0","rw","r",null,"Control->components->humidifier","3, (4)"]
[null,6521," ",13042,"humidifier2 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->humidifier","3, (4)"]
[null,6522," ",13044,"humidifier2 analog out","internal","byte",null,"0..20",null,"rw","r",null,"Service->equipment->humidifier","3, (4)"]
[null,6523," ",13046,"humidifier2 alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->humidifier","3, (4)"]
[null,6524," ",13048,"humidifier2 alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->humidifier","3, (4)"]
[null,6525," ",13050,"humidifier2 alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->humidifier","3, (4)"]
[null,6526," ",13052,"humidifier2 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r",null,"Info->state->humidity; Service->equipment->humidifier","3, (4)"]
[null,6527," ",13054,"humidifier2 current value","internal","byte",null,"0..100","percent","r","r",null,"Info->state->humidity","3, (4)"]
[null,6528," ",13056,"humidifier2 manual operation value","internal","byte",null,"0..100","percent","rw","rw",null,"Control->components->humidifier","3, (4), 16"]
[null,6529," ",13058,"humidifier2 alarm digital in 5µS","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->humidifier","3, (4)"]
[null,6530," ",13060,"humidifier2 alarm digital in 20µS","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->humidifier","3, (4)"]
[null,6531," ",13062,"humidifier2 alarm delay 5µS","internal","UI16",null,"0..1000","seconds","rw","r",null,"Control->components->humidifier","3, (4)"]
[null,6532," ",13064,"humidifier2 alarm delay 20µS","internal","UI16",null,"0..1000","seconds","rw","r",null,"Control->components->humidifier","3, (4)"]
[null,6533," ",13066,"humidifier2 alarm priorities 5µS","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->humidifier","3, (4)"]
[null,6534," ",13068,"humidifier2 alarm priorities 20µS","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->humidifier","3, (4)"]
[{"$nulls":3}," "]
["Humidifier 3",null,null," "]
[null,6600,0,6600,"humidifier3 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->humidifier","1, (2)"]
[null,6601,1,6601,"humidifier3 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->humidifier","1, (2), 5"]
[null,6602,2,6602,"humidifier3 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->humidity","2, (1)"]
[null,6603,3,6603,"humidifier3 alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->humidity","2, (1)"]
[null,6604,4,6604,"humidifier3 manual operation running","internal","bit",null,"0 / 1",null,"rw","rw","added","Control->components->humidifier","1, (2), 5"]
[null,6605,5,6605,"humidifier3 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->humidifier","1, (2)"]
[null,6606,6,6606,"humidifier3 conductivity config","internal","bit",null,"0 / 1",null,"rw","r"]
[null,6607,7,6607,"humidifier3 common alarm 5µS","internal","bit",null,"0 / 1",null,"rw","r"]
[null,6608,0,6608,"humidifier3 common alarm 20µS","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->humidifier","1, (2)"]
[null,6609,1,6609,"humidifier1 alarm 5µS","internal","bit",null,"0 / 1",null,"r","r","changed","Control->components->humidifier","1, (2), 5"]
[null,6610,2,6610,"humidifier1 alarm 20µS","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->humidity","2, (1)"]
[null,6611,3,6611,null,"internal","bit",{"$nulls":3},"r",null,null,"Info->state->humidity"]
[null,6612,4,6612,null,"internal","bit",{"$nulls":3},"rw",null,null,"Control->components->humidifier"]
[null,6613,5,6613,null,"internal","bit",{"$nulls":3},"rw",null,null,"Control->components->humidifier"]
[null,6614,6,6614,null,"internal","bit",{"$nulls":3},"rw"]
[null,6615,7,6615,null,"internal","bit"]
[null,6616," ",13232,"humidifier3 type","internal","byte",null,"1..2",null,"rw","r",null,"Service->equipment->humidifier","3, (4)"]
[null,6617," ",13234,"humidifier3 start-humidity","internal","word",null,"0..200","0,0..20,0%rF","rw","r","changed","Control->components->humidifier","3, (4)"]
[null,6618," ",13236,"humidifier3 start-humidity 2","internal","word",{"$nulls":3},"rw","r","delete","Control->components->humidifier","3, (4)",null,null,"not accessible, TMO"]
[null,6619," ",13238,"humidifier3 hysteresis","internal","word",null,"0..200","0,0..20,0%rF","rw","r",null,"Control->components->humidifier","3, (4)"]
[null,6620," ",13240,"humidifier3 linear range","internal","word",null,"5..200","0,5..20,0","rw","r",null,"Control->components->humidifier","3, (4)"]
[null,6621," ",13242,"humidifier3 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->humidifier","3, (4)"]
[null,6622," ",13244,"humidifier3 analog out","internal","byte",null,"0..20",null,"rw","r",null,"Service->equipment->humidifier","3, (4)"]
[null,6623," ",13246,"humidifier3 alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->humidifier","3, (4)"]
[null,6624," ",13248,"humidifier3 alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->humidifier","3, (4)"]
[null,6625," ",13250,"humidifier3 alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->humidifier","3, (4)"]
[null,6626," ",13252,"humidifier3 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r",null,"Info->state->humidity; Service->equipment->humidifier","3, (4)"]
[null,6627," ",13254,"humidifier3 current value","internal","byte",null,"0..100","percent","r","r",null,"Info->state->humidity","3, (4)"]
[null,6628," ",13256,"humidifier3 manual operation value","internal","byte",null,"0..100","percent","rw","rw",null,"Control->components->humidifier","3, (4), 16"]
[null,6629," ",13258,"humidifier3 alarm digital in 5µS","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->humidifier","3, (4)"]
[null,6630," ",13260,"humidifier3 alarm digital in 20µS","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->humidifier","3, (4)"]
[null,6631," ",13262,"humidifier3 alarm delay 5µS","internal","UI16",null,"0..1000","seconds","rw","r",null,"Control->components->humidifier","3, (4)"]
[null,6632," ",13264,"humidifier3 alarm delay 20µS","internal","UI16",null,"0..1000","seconds","rw","r",null,"Control->components->humidifier","3, (4)"]
[null,6633," ",13266,"humidifier3 alarm priorities 5µS","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->humidifier","3, (4)"]
[null,6634," ",13268,"humidifier3 alarm priorities 20µS","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->humidifier","3, (4)"]
[{"$nulls":3}," "]
["Humidifier 4",null,null," "]
[null,6700,0,6700,"humidifier4 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->humidifier","1, (2)",null,null,"not accessible, TMO"]
[null,6701,1,6701,"humidifier4 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->humidifier","1, (2), 5",null,null,"not accessible, TMO"]
[null,6702,2,6702,"humidifier4 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->humidity","2, (1)",null,null,"not accessible, TMO"]
[null,6703,3,6703,"humidifier4 alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->humidity","2, (1)",null,null,"not accessible, TMO"]
[null,6704,4,6704,"humidifier4 manual operation running","internal","bit",null,"0 / 1",null,"rw","rw","added","Control->components->humidifier","1, (2), 5",null,null,"not accessible, TMO"]
[null,6705,5,6705,"humidifier4 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->humidifier","1, (2)",null,null,"not accessible, TMO"]
[null,6706,6,6706,"humidifier4 conductivity config","internal","bit",null,"0 / 1",null,"rw","r",{"$nulls":5},"not accessible, TMO"]
[null,6707,7,6707,"humidifier4 common alarm 5µS","internal","bit",null,"0 / 1",null,"rw","r",{"$nulls":5},"not accessible, TMO"]
[null,6708,0,6708,"humidifier4 common alarm 20µS","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->humidifier","1, (2)",null,null,"not accessible, TMO"]
[null,6709,1,6709,"humidifier1 alarm 5µS","internal","bit",null,"0 / 1",null,"r","r","changed","Control->components->humidifier","1, (2), 5",null,null,"not accessible, TMO"]
[null,6710,2,6710,"humidifier1 alarm 20µS","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->humidity","2, (1)",null,null,"not accessible, TMO"]
[null,6711,3,6711,null,"internal","bit",{"$nulls":3},"r",null,null,"Info->state->humidity"]
[null,6712,4,6712,null,"internal","bit",{"$nulls":3},"rw",null,null,"Control->components->humidifier"]
[null,6713,5,6713,null,"internal","bit",{"$nulls":3},"rw",null,null,"Control->components->humidifier"]
[null,6714,6,6714,null,"internal","bit",{"$nulls":3},"rw"]
[null,6715,7,6715,null,"internal","bit"]
[null,6716," ",13432,"humidifier4 type","internal","byte",null,"1..2",null,"rw","r",null,"Service->equipment->humidifier","3, (4)",null,null,"not accessible, TMO"]
[null,6717," ",13434,"humidifier4 start-humidity","internal","word",null,"0..200","0,0..20,0%rF","rw","r","changed","Control->components->humidifier","3, (4)",null,null,"not accessible, TMO"]
[null,6718," ",13436,"humidifier4 start-humidity 2","internal","word",{"$nulls":3},"rw","r","delete","Control->components->humidifier","3, (4)",null,null,"not accessible, TMO"]
[null,6719," ",13438,"humidifier4 hysteresis","internal","word",null,"0..200","0,0..20,0%rF","rw","r",null,"Control->components->humidifier","3, (4)",null,null,"not accessible, TMO"]
[null,6720," ",13440,"humidifier4 linear range","internal","word",null,"5..200","0,5..20,0","rw","r",null,"Control->components->humidifier","3, (4)",null,null,"not accessible, TMO"]
[null,6721," ",13442,"humidifier4 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->humidifier","3, (4)",null,null,"not accessible, TMO"]
[null,6722," ",13444,"humidifier4 analog out","internal","byte",null,"0..20",null,"rw","r",null,"Service->equipment->humidifier","3, (4)",null,null,"not accessible, TMO"]
[null,6723," ",13446,"humidifier4 alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->humidifier","3, (4)",null,null,"not accessible, TMO"]
[null,6724," ",13448,"humidifier4 alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->humidifier","3, (4)",null,null,"not accessible, TMO"]
[null,6725," ",13450,"humidifier4 alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->humidifier","3, (4)",null,null,"not accessible, TMO"]
[null,6726," ",13452,"humidifier4 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r",null,"Info->state->humidity; Service->equipment->humidifier","3, (4)",null,null,"not accessible, TMO"]
[null,6727," ",13454,"humidifier4 current value","internal","byte",null,"0..100","percent","r","r",null,"Info->state->humidity","3, (4)",null,null,"not accessible, TMO"]
[null,6728," ",13456,"humidifier4 manual operation value","internal","byte",null,"0..100","percent","rw","rw",null,"Control->components->humidifier","3, (4), 16",null,null,"not accessible, TMO"]
[null,6729," ",13458,"humidifier4 alarm digital in 5µS","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->humidifier","3, (4)",null,null,"not accessible, TMO"]
[null,6730," ",13460,"humidifier4 alarm digital in 20µS","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->humidifier","3, (4)",null,null,"not accessible"]
[null,6731," ",13462,"humidifier4 alarm delay 5µS","internal","UI16",null,"0..1000","seconds","rw","r",null,"Control->components->humidifier","3, (4)",null,null,"not accessible"]
[null,6732," ",13464,"humidifier4 alarm delay 20µS","internal","UI16",null,"0..1000","seconds","rw","r",null,"Control->components->humidifier","3, (4)",null,null,"not accessible"]
[null,6733," ",13466,"humidifier4 alarm priorities 5µS","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->humidifier","3, (4)",null,null,"not accessible"]
[null,6734," ",13468,"humidifier4 alarm priorities 20µS","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->humidifier","3, (4)",null,null,"not accessible"]
[{"$nulls":3}," "]
["Dehumidification",null,null," "]
[null,6800,0,6800,"dehumidification valve config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->dehumidification","1, (2)","rw","rw"]
[null,6801,1,6801,"dehumidification manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->dehumidification","1, (2), 5","rw"]
[null,6802,2,6802,"dehumidification running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->humidity","2, (1)","r","r"]
[null,6803,3,6803,"dehumidifier alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->humidity","2, (1)","r","r","not accessible, TMO"]
[null,6804,4,6804,"dehumidification manual operation running","internal","bit",null,"0 / 1",null,"rw","rw","added","Control->components->dehumidification","1, (2), 5","rw"]
[null,6805,5,6805,"dehumidification hotgas bypass config active","internal","bit",null,"0 / 1",null,"rw","r"]
[null,6806,6,6806,null,"internal","bit"]
[null,6807,7,6807,null,"internal","bit"]
[null,6808," ",13616,"dehumidifier type","internal","byte",{"$nulls":3},"rw","r","delete","not available","3, (4)","rw","rw","not accessible, TMO"]
[null,6809," ",13618,"dehumidifier start-humidity","internal","word",null,"0..1000","0,0..100,0%rF","rw","r","changed","Control->components->dehumidification","3, (4)","rw"]
[null,6810," ",13620,"dehumidifier start-humidity 2","internal","word",{"$nulls":3},"rw","r","delete","not available","3, (4)","rw",null,"not accessible, TMO"]
[null,6811," ",13622,"dehumidification hysteresis","internal","word",null,"0..300","0,0..30,0%rF","rw","r",null,"Control->components->dehumidification","3, (4)","rw"]
[null,6812," ",13624,"dehumidifier linear range","internal","word",{"$nulls":3},"rw","r","delete","not available","3, (4)","rw",null,"not accessible, TMO"]
[null,6813," ",13626,"dehumidification digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->dehumidification","3, (4)"]
[null,6814," ",13628,"dehumidifier analog out","internal","byte",{"$nulls":3},"rw","r","delete","not available","3, (4)",null,null,"not accessible, TMO"]
[null,6815," ",13630,"dehumidifier alarm digital in","internal","byte",{"$nulls":3},"rw","r","delete","not available","3, (4)",null,null,"not accessible, TMO"]
[null,6816," ",13632,"dehumidifier alarm priorities","internal","byte",{"$nulls":3},"rw","r","delete","not available","3, (4)",null,null,"not accessible, TMO"]
[null,6817," ",13634,"dehumidifier min water temp","internal","word",null,"0..500","0,0..50,0°C","rw","r","added","Control->components->dehumidification","3, (4)","rw"]
[null,6818," ",13636,"dehumidifier max water temp","internal","word",null,"0..500","0,0..50,0°C","rw","r","added","Control->components->dehumidification","3, (4)","rw"]
[null,6819," ",13638,"dehumidifier alarm delay","internal","byte",{"$nulls":3},"rw","r","delete","not available","3, (4)","rw",null,"not accessible, TMO"]
[null,6820," ",13640,"dehumidifier runtime","internal","word",{"$nulls":3},"r(w0)","r",null,"Info->state->humidity; Service->equipment->dehumidification",null,"rw",null,"not accessible, TMO"]
[null,6821,null,13642,"dehumidification stop on room temp","internal","word",null,"0..100","0,0..10,0K","rw","r",{"$nulls":3},"rw"]
[null,6822,null,13644,"min fan speed when precision dehumidification","internal","byte",null,"0..100","percent","rw","r",{"$nulls":3},"rw"]
[{"$nulls":3}," "]
["Fan 1",null,null," "]
[null,6900,0,6900,"fan1 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->air->fan","1, (2)","rw","rw"]
[null,6901,1,6901,"fan1 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->air->fan","1, (2), 5","rw"]
[null,6902,2,6902,"fan1 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->air","2, (1)","r","r"]
[null,6903,3,6903,"fan1 alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->air","2, (1)","r","r"]
[null,6904,4,6904,"fan1 filter alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->air","2, (1)","r","r"]
[null,6905,5,6905,"fan1 manual operation running","internal","bit",null,"0 / 1",null,"rw","rw",null,"Control->components->air->fan","1, (2), 5"]
[null,6906,6,6906,"fan1 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->air->fan","1, (2)"]
[null,6907,7,6907,"fan1 common alarm filter","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->air->fan","1, (2)"]
[null,6908," ",13816,"fan1 type","internal","byte",null,"1..2",null,"rw","r",null,"Service->equipment->air->fan","3, (4)","rw","rw"]
[null,6909," ",13818,"fan1 speed nmax.","internal","byte",null,"40..100","percent","rw","r",null,"Control->components->air->fan","3, (4)","rw","r"]
[null,6910," ",13820,"fan1 CW-mode nmax","internal","byte",null,"40..100","percent","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[null,6911," ",13822,"fan1 pre runtime","internal","byte",null,"0..100","seconds","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,6912," ",13824,"fan1 run after time","internal","byte",null,"0..100","seconds","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,6913," ",13826,"fan1 start temp","internal","word",null,"0..99","0,0..9,9K","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,6914," ",13828,"fan1 start speed","internal","byte",null,"0..10","percent","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,6915," ",13830,"fan1 speed start","internal","word",{"$nulls":3},"rw","r","added","Control->components->air->fan","3, (4)","rw",null,"not accessible"]
[null,6916," ",13832,"fan1 start 100% time","internal","byte",null,"0..100","seconds","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,6917," ",13834,"fan1 reduce time","internal","byte",null,"30..120","minutes","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,6918," ",13836,"fan1 reduce speed","internal","byte",null,"0..100","percent","rw","r","added","Control->components->air->fan","3, (4)","rw","rw"]
[null,6919," ",13838,"fan1 offset","internal","byte",null,"-10..10","percent","rw","r",null,"Control->components->air->fan","3, (4)","rw","rw"]
[null,6920," ",13840,"fan1 dehumidification speed","internal","byte",null,"0..20","percent","rw","r",null,"Control->components->air->fan","3, (4)","rw","rw"]
[null,6921," ",13842,"fan1 ups speed","internal","byte",null,"0..20","percent","rw","r","added","Control->components->air->fan","3, (4)","rw","rw"]
[null,6922," ",13844,"fan1 offset filter clogged","internal","byte",null,"0..10","percent","rw","r",null,"Control->components->air->fan","3, (4)","rw","rw"]
[null,6923," ",13846,"fan1 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->air->fan","3, (4)"]
[null,6924," ",13848,"fan1 analog out","internal","byte",null,"0..20",null,"rw","r",null,"Service->equipment->air->fan","3, (4)"]
[null,6925," ",13850,"fan1 alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->air->fan","3, (4)"]
[null,6926," ",13852,"fan1 alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->air->fan","3, (4)"]
[null,6927," ",13854,"fan1 alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[null,6928," ",13856,"fan1 filter alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->air->fan","3, (4)"]
[null,6929," ",13858,"fan1 filter alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->air->fan","3, (4)"]
[null,6930," ",13860,"fan1 filter alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->air->fan","3, (4)"]
[null,6931," ",13862,"fan1 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r",null,"Info->state->air; Service->equipment->air->fan","3, (4)","rw"]
[null,6932," ",13864,"fan1 speed","internal","byte",null,"0..100","percent","r","r",null,"Info->state->air","3, (4)","r","r"]
[null,6933," ",13866,"fan1 manual operation speed","internal","byte",null,"0..100","percent","rw","rw","added","Control->components->air->fan","3, (4), 16","rw"]
[null,6934," ",13868,"fan1 min speed","internal","byte",null,"0..100","percent","rw","r",null,"Control->components->air->fan","3, (4)","r","r"]
[{"$nulls":3}," "]
["Fan 2",null,null," "]
[null,7000,0,7000,"fan2 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->air->fan","1, (2)","rw"]
[null,7001,1,7001,"fan2 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->air->fan","1, (2), 5","rw"]
[null,7002,2,7002,"fan2 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->air","2, (1)","r"]
[null,7003,3,7003,"fan2 alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->air","2, (1)","r"]
[null,7004,4,7004,"fan2 filter alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->air","2, (1)","r"]
[null,7005,5,7005,"fan2 manual operation running","internal","bit",null,"0 / 1",null,"rw","rw",null,"Control->components->air->fan","1, (2), 5","rw"]
[null,7006,6,7006,"fan2 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->air->fan","1, (2)"]
[null,7007,7,7007,"fan2 common alarm filter","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->air->fan","1, (2)"]
[null,7008," ",14016,"fan2 type","internal","byte",null,"1..2",null,"rw","r",null,"Service->equipment->air->fan","3, (4)","rw"]
[null,7009," ",14018,"fan2 speed nmax.","internal","byte",null,"40..100","percent","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[null,7010," ",14020,"fan2 CW-mode nmax","internal","byte",null,"40..100","percent","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[null,7011," ",14022,"fan2 pre runtime","internal","byte",null,"0..100","seconds","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,7012," ",14024,"fan2 run after time","internal","byte",null,"0..100","seconds","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,7013," ",14026,"fan2 start temp","internal","word",null,"0..99","0,0..9,9K","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,7014," ",14028,"fan2 start speed","internal","byte",null,"0..10","percent","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,7015," ",14030,"fan2 speed start","internal","word",{"$nulls":3},"rw","r","added","Control->components->air->fan","3, (4)","rw",null,"not accessible"]
[null,7016," ",14032,"fan2 start 100% time","internal","byte",null,"0..100","seconds","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,7017," ",14034,"fan2 reduce time","internal","byte",null,"30..120","minutes","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,7018," ",14036,"fan2 reduce speed","internal","byte",null,"0..100","percent","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,7019," ",14038,"fan2 offset","internal","byte",null,"-10..10","percent","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[null,7020," ",14040,"fan2 dehumidification speed","internal","byte",null,"0..20","percent","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[null,7021," ",14042,"fan2 ups speed","internal","byte",null,"0..20","percent","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,7022," ",14044,"fan2 offset filter clogged","internal","byte",null,"0..10","percent","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[null,7023," ",14046,"fan2 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->air->fan","3, (4)"]
[null,7024," ",14048,"fan2 analog out","internal","byte",null,"0..20",null,"rw","r",null,"Service->equipment->air->fan","3, (4)"]
[null,7025," ",14050,"fan2 alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->air->fan","3, (4)"]
[null,7026," ",14052,"fan2 alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->air->fan","3, (4)"]
[null,7027," ",14054,"fan2 alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[null,7028," ",14056,"fan2 filter alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->air->fan","3, (4)"]
[null,7029," ",14058,"fan2 filter alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->air->fan","3, (4)"]
[null,7030," ",14060,"fan2 filter alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[null,7031," ",14062,"fan2 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r",null,"Info->state->air; Service->equipment->air->fan","3, (4)","rw"]
[null,7032," ",14064,"fan2 speed","internal","byte",null,"0..100","percent","r","r",null,"Info->state->air","3, (4)","r"]
[null,7033," ",14066,"fan2 manual operation speed","internal","byte",null,"0..100","percent","rw","rw","added","Control->components->air->fan","3, (4), 16","rw"]
[null,7034," ",14068,"fan2 min speed","internal","byte",null,"0..100","percent","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[{"$nulls":3}," "]
["Fan 3",null,null," "]
[null,7100,0,7100,"fan3 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->air->fan","1, (2)","rw"]
[null,7101,1,7101,"fan3 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->air->fan","1, (2), 5","rw"]
[null,7102,2,7102,"fan3 running","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->air","2, (1)","r"]
[null,7103,3,7103,"fan3 alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->air","2, (1)","r"]
[null,7104,4,7104,"fan3 filter alarm","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->air","2, (1)","r"]
[null,7105,5,7105,"fan3 manual operation running","internal","bit",null,"0 / 1",null,"rw","rw",null,"Control->components->air->fan","1, (2), 5","rw"]
[null,7106,6,7106,"fan3 common alarm","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->air->fan","1, (2)"]
[null,7107,7,7107,"fan3 common alarm filter","internal","bit",null,"0 / 1",null,"rw","r","added","Control->components->air->fan","1, (2)"]
[null,7108," ",14216,"fan3 type","internal","byte",null,"1..2",null,"rw","r",null,"Service->equipment->air->fan","3, (4)","rw"]
[null,7109," ",14218,"fan3 speed nmax.","internal","byte",null,"40..100","percent","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[null,7110," ",14220,"fan3 CW-mode nmax","internal","byte",null,"40..100","percent","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[null,7111," ",14222,"fan3 pre runtime","internal","byte",null,"0..100","seconds","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,7112," ",14224,"fan3 run after time","internal","byte",null,"0..100","seconds","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,7113," ",14226,"fan3 start temp","internal","word",null,"0..99","0,0..9,9K","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,7114," ",14228,"fan3 start speed","internal","byte",null,"0..10","percent","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,7115," ",14230,"fan3 speed start","internal","word",{"$nulls":3},"rw","r","added","Control->components->air->fan","3, (4)","rw",null,"not accessible"]
[null,7116," ",14232,"fan3 start 100% time","internal","byte",null,"0..100","seconds","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,7117," ",14234,"fan3 reduce time","internal","byte",null,"30..120","minutes","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,7118," ",14236,"fan3 reduce speed","internal","byte",null,"0..100","percent","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,7119," ",14238,"fan3 offset","internal","byte",null,"-10..10","percent","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[null,7120," ",14240,"fan3 dehumidification speed","internal","byte",null,"0..20","percent","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[null,7121," ",14242,"fan3 ups speed","internal","byte",null,"0..20","percent","rw","r","added","Control->components->air->fan","3, (4)","rw"]
[null,7122," ",14244,"fan3 offset filter clogged","internal","byte",null,"0..10","percent","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[null,7123," ",14246,"fan3 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->air->fan","3, (4)"]
[null,7124," ",14248,"fan3 analog out","internal","byte",null,"0..20",null,"rw","r",null,"Service->equipment->air->fan","3, (4)"]
[null,7125," ",14250,"fan3 alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->air->fan","3, (4)"]
[null,7126," ",14252,"fan3 alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->air->fan","3, (4)"]
[null,7127," ",14254,"fan3 alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[null,7128," ",14256,"fan3 filter alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->air->fan","3, (4)"]
[null,7129," ",14258,"fan3 filter alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Control->components->air->fan","3, (4)"]
[null,7130," ",14260,"fan3 filter alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[null,7131," ",14262,"fan3 runtime","internal","UI32",null,"0..0xFFFFFFFF","hours","rw","r",null,"Info->state->air; Service->equipment->air->fan","3, (4)","rw"]
[null,7132," ",14264,"fan3 speed","internal","byte",null,"0..100","percent","r","r",null,"Info->state->air","3, (4)","r"]
[null,7133," ",14266,"fan3 manual operation speed","internal","byte",null,"0..100","percent","rw","rw","added","Control->components->air->fan","3, (4), 16","rw"]
[null,7134," ",14268,"fan3 min speed","internal","byte",null,"0..100","percent","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[{"$nulls":3}," "]
["Louver 1",null,null," "]
[null,7200,0,7200,"louver1 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->air->fan","1, (2)","rw","rw"]
[null,7201,1,7201,"louver1 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->air->fan","1, (2), 5","rw"]
[null,7202,2,7202,"louver1 open","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->air","2, (1)","r","r"]
[null,7203,3,7203,"louver1 manual operation open","internal","bit",null,"0 / 1",null,"rw","rw","added","Control->components->air->fan","1, (2), 5","rw"]
[null,7204,4,7204,null,"internal","bit"]
[null,7205,5,7205,null,"internal","bit"]
[null,7206,6,7206,null,"internal","bit"]
[null,7207,7,7207,null,"internal","bit"]
[null,7208," ",14416,"louver1 delay","internal","byte",null,"0..180","seconds","rw","r",null,"Control->components->air->fan","3, (4)","r"]
[null,7209," ",14418,"louver1 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->air->fan","3, (4)"]
[{"$nulls":3}," "]
["Louver 2",null,null," "]
[null,7300,0,7300,"louver2 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->air->fan","1, (2)","rw","rw"]
[null,7301,1,7301,"louver2 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->air->fan","1, (2), 5","rw"]
[null,7302,2,7302,"louver2 open","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->air","2, (1)","r","r"]
[null,7303,3,7303,"louver2 manual operation open","internal","bit",null,"0 / 1",null,"rw","rw","added","Control->components->air->fan","1, (2), 5","rw"]
[null,7304,4,7304,null,"internal","bit"]
[null,7305,5,7305,null,"internal","bit"]
[null,7306,6,7306,null,"internal","bit"]
[null,7307,7,7307,null,"internal","bit"]
[null,7308," ",14616,"louver2 delay","internal","byte",null,"0..180","seconds","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[null,7309," ",14618,"louver2 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->air->fan","3, (4)"]
[{"$nulls":3}," "]
["Louver 3",null,null," "]
[null,7400,0,7400,"louver3 config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->air->fan","1, (2)","rw"]
[null,7401,1,7401,"louver3 manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","changed","Control->components->air->fan","1, (2), 5","rw"]
[null,7402,2,7402,"louver3 open","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->air","2, (1)","r"]
[null,7403,3,7403,"louver3 manual operation open","internal","bit",null,"0 / 1",null,"rw","rw","added","Control->components->air->fan","1, (2), 5","rw"]
[null,7404,4,7404,null,"internal","bit"]
[null,7405,5,7405,null,"internal","bit"]
[null,7406,6,7406,null,"internal","bit"]
[null,7407,7,7407,null,"internal","bit"]
[null,7408," ",14816,"louver3 delay","internal","byte",null,"0..180","seconds","rw","r",null,"Control->components->air->fan","3, (4)","rw"]
[null,7409," ",14818,"louver3 digital out","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->air->fan","3, (4)"]
[{"$nulls":3}," "]
["External alarm 1",null,null," "]
[null,7500,0,7500,"ext. alarm config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->extalarms","1, (2)","rw","rw"]
[null,7501,1,7501,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","r","simulates alarm to check resulting output","Service->equipment->extalarms","1, (2)","rw"]
[null,7502,2,7502,"ext. alarm active","internal","bit",null,"0 / 1",null,"r","r",null,"alarm/event-window","2, (1)","r","r"]
[null,7503,3,7503,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","r","simulates alarm to check resulting output","Service->equipment->extalarms","1, (2)","rw"]
[null,7504,4,7504,"ext. alarm common alarm","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->extalarms","1, (2)"]
[null,7505,5,7505,null,"internal","bit"]
[null,7506,6,7506,null,"internal","bit"]
[null,7507,7,7507,null,"internal","bit"]
[null,7508," ",15016,"ext. alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,7509," ",15018,"ext. alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,7510," ",15020,"ext. alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Service->equipment->extalarms","3, (4)","rw"]
[null,7511," ",15022,"ext. alarm text 0","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,7512," ",15024,"ext. alarm text 1","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7513," ",15026,"ext. alarm text 2","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7514," ",15028,"ext. alarm text 3","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7515," ",15030,"ext. alarm text 4","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7516," ",15032,"ext. alarm text 5","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7517," ",15034,"ext. alarm text 6","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7518," ",15036,"ext. alarm text 7","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7519," ",15038,"ext. alarm text 8","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7520," ",15040,"ext. alarm text 9","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7521," ",15042,"ext. alarm text 10","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7522," ",15044,"ext. alarm text 11","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7523," ",15046,"ext. alarm text 12","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7524," ",15048,"ext. alarm text 13","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7525," ",15050,"ext. alarm text 14","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7526," ",15052,"ext. alarm text 15","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7527," ",15054,"ext. alarm text 16","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7528," ",15056,"ext. alarm text 17","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7529," ",15058,"ext. alarm text 18","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7530," ",15060,"ext. alarm text 19","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[{"$nulls":3}," "]
["External alarm 2",null,null," "]
[null,7600,0,7600,"ext. alarm config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->extalarms","1, (2)","rw","rw"]
[null,7601,1,7601,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","r","simulates alarm to check resulting output","Service->equipment->extalarms","1, (2)","rw"]
[null,7602,2,7602,"ext. alarm active","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->misc","2, (1)","r","r"]
[null,7603,3,7603,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","r","simulates alarm to check resulting output","Service->equipment->extalarms","1, (2)","rw"]
[null,7604,4,7604,"ext. alarm common alarm","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->extalarms","1, (2)"]
[null,7605,5,7605,null,"internal","bit"]
[null,7606,6,7606,null,"internal","bit"]
[null,7607,7,7607,null,"internal","bit"]
[null,7608," ",15216,"ext. alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,7609," ",15218,"ext. alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,7610," ",15220,"ext. alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Service->equipment->extalarms","3, (4)","rw"]
[null,7611," ",15222,"ext. alarm text 0","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,7612," ",15224,"ext. alarm text 1","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7613," ",15226,"ext. alarm text 2","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7614," ",15228,"ext. alarm text 3","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7615," ",15230,"ext. alarm text 4","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7616," ",15232,"ext. alarm text 5","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7617," ",15234,"ext. alarm text 6","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7618," ",15236,"ext. alarm text 7","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7619," ",15238,"ext. alarm text 8","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7620," ",15240,"ext. alarm text 9","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7621," ",15242,"ext. alarm text 10","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7622," ",15244,"ext. alarm text 11","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7623," ",15246,"ext. alarm text 12","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7624," ",15248,"ext. alarm text 13","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7625," ",15250,"ext. alarm text 14","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7626," ",15252,"ext. alarm text 15","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7627," ",15254,"ext. alarm text 16","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7628," ",15256,"ext. alarm text 17","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7629," ",15258,"ext. alarm text 18","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7630," ",15260,"ext. alarm text 19","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[{"$nulls":3}," "]
["External alarm 3",null,null," "]
[null,7700,0,7700,"ext. alarm config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->extalarms","1, (2)","rw"]
[null,7701,1,7701,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","r","simulates alarm to check resulting output","Service->equipment->extalarms","1, (2)","rw"]
[null,7702,2,7702,"ext. alarm active","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->misc","2, (1)","r"]
[null,7703,3,7703,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","r","simulates alarm to check resulting output","Service->equipment->extalarms","1, (2)","rw"]
[null,7704,4,7704,"ext. alarm common alarm","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->extalarms","1, (2)"]
[null,7705,5,7705,null,"internal","bit"]
[null,7706,6,7706,null,"internal","bit"]
[null,7707,7,7707,null,"internal","bit"]
[null,7708," ",15416,"ext. alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,7709," ",15418,"ext. alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,7710," ",15420,"ext. alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Service->equipment->extalarms","3, (4)","rw"]
[null,7711," ",15422,"ext. alarm text 0","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,7712," ",15424,"ext. alarm text 1","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7713," ",15426,"ext. alarm text 2","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7714," ",15428,"ext. alarm text 3","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7715," ",15430,"ext. alarm text 4","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7716," ",15432,"ext. alarm text 5","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7717," ",15434,"ext. alarm text 6","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7718," ",15436,"ext. alarm text 7","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7719," ",15438,"ext. alarm text 8","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7720," ",15440,"ext. alarm text 9","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7721," ",15442,"ext. alarm text 10","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7722," ",15444,"ext. alarm text 11","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7723," ",15446,"ext. alarm text 12","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7724," ",15448,"ext. alarm text 13","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7725," ",15450,"ext. alarm text 14","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7726," ",15452,"ext. alarm text 15","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7727," ",15454,"ext. alarm text 16","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7728," ",15456,"ext. alarm text 17","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7729," ",15458,"ext. alarm text 18","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7730," ",15460,"ext. alarm text 19","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[{"$nulls":3}," "]
["External alarm 4",null,null," "]
[null,7800,0,7800,"ext. alarm config active","internal","bit",null,"0 / 1",null,"rw","rw","rw","rw","rw","rw"]
[null,7801,1,7801,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","rw","rw","rw","rw","rw"]
[null,7802,2,7802,"ext. alarm active","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->misc","2, (1)","r"]
[null,7803,3,7803,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","r","simulates alarm to check resulting output","Service->equipment->extalarms","1, (2)","rw"]
[null,7804,4,7804,"ext. alarm common alarm","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->extalarms","1, (2)"]
[null,7805,5,7805,null,"internal","bit"]
[null,7806,6,7806,null,"internal","bit"]
[null,7807,7,7807,null,"internal","bit"]
[null,7808," ",15616,"ext. alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,7809," ",15618,"ext. alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,7810," ",15620,"ext. alarm delay","internal","byte",null,"0..100","seconds","rw","rw","rw","rw","rw","rw"]
[null,7811," ",15622,"ext. alarm text 0","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw"]
[null,7812," ",15624,"ext. alarm text 1","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,7813," ",15626,"ext. alarm text 2","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,7814," ",15628,"ext. alarm text 3","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,7815," ",15630,"ext. alarm text 4","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,7816," ",15632,"ext. alarm text 5","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,7817," ",15634,"ext. alarm text 6","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,7818," ",15636,"ext. alarm text 7","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,7819," ",15638,"ext. alarm text 8","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,7820," ",15640,"ext. alarm text 9","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,7821," ",15642,"ext. alarm text 10","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,7822," ",15644,"ext. alarm text 11","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,7823," ",15646,"ext. alarm text 12","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,7824," ",15648,"ext. alarm text 13","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,7825," ",15650,"ext. alarm text 14","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,7826," ",15652,"ext. alarm text 15","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,7827," ",15654,"ext. alarm text 16","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,7828," ",15656,"ext. alarm text 17","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,7829," ",15658,"ext. alarm text 18","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[null,7830," ",15660,"ext. alarm text 19","internal","byte",null,"32..125","ASCII","rw","rw","rw","rw","rw","rw",null,"not accessible"]
[{"$nulls":3}," "]
["External alarm 5",null,null," "]
[null,7900,0,7900,"ext. alarm config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->extalarms","1, (2)","rw"]
[null,7901,1,7901,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","r","simulates alarm to check resulting output","Service->equipment->extalarms","1, (2)","rw"]
[null,7902,2,7902,"ext. alarm active","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->misc","2, (1)","r"]
[null,7903,3,7903,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","r","simulates alarm to check resulting output","Service->equipment->extalarms","1, (2)","rw"]
[null,7904,4,7904,"ext. alarm common alarm","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->extalarms","1, (2)"]
[null,7905,5,7905,null,"internal","bit"]
[null,7906,6,7906,null,"internal","bit"]
[null,7907,7,7907,null,"internal","bit"]
[null,7908," ",15816,"ext. alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,7909," ",15818,"ext. alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,7910," ",15820,"ext. alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Service->equipment->extalarms","3, (4)","rw"]
[null,7911," ",15822,"ext. alarm text 0","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,7912," ",15824,"ext. alarm text 1","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7913," ",15826,"ext. alarm text 2","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7914," ",15828,"ext. alarm text 3","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7915," ",15830,"ext. alarm text 4","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7916," ",15832,"ext. alarm text 5","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7917," ",15834,"ext. alarm text 6","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7918," ",15836,"ext. alarm text 7","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7919," ",15838,"ext. alarm text 8","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7920," ",15840,"ext. alarm text 9","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7921," ",15842,"ext. alarm text 10","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7922," ",15844,"ext. alarm text 11","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7923," ",15846,"ext. alarm text 12","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7924," ",15848,"ext. alarm text 13","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7925," ",15850,"ext. alarm text 14","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7926," ",15852,"ext. alarm text 15","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7927," ",15854,"ext. alarm text 16","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7928," ",15856,"ext. alarm text 17","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7929," ",15858,"ext. alarm text 18","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[null,7930," ",15860,"ext. alarm text 19","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw",null,"not accessible"]
[{"$nulls":3}," "]
["External alarm 6",null,null," "]
[null,8000,0,8000,"ext. alarm config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->extalarms","1, (2)"]
[null,8001,1,8001,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","r","simulates alarm to check resulting output","Service->equipment->extalarms","1, (2)"]
[null,8002,2,8002,"ext. alarm active","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->misc","2, (1)"]
[null,8003,3,8003,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","r","simulates alarm to check resulting output","Service->equipment->extalarms","1, (2)"]
[null,8004,4,8004,"ext. alarm common alarm","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->extalarms","1, (2)"]
[null,8005,5,8005,null,"internal","bit"]
[null,8006,6,8006,null,"internal","bit"]
[null,8007,7,8007,null,"internal","bit"]
[null,8008," ",16016,"ext. alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,8009," ",16018,"ext. alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,8010," ",16020,"ext. alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,8011," ",16022,"ext. alarm text 0","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[null,8012," ",16024,"ext. alarm text 1","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8013," ",16026,"ext. alarm text 2","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8014," ",16028,"ext. alarm text 3","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8015," ",16030,"ext. alarm text 4","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8016," ",16032,"ext. alarm text 5","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8017," ",16034,"ext. alarm text 6","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8018," ",16036,"ext. alarm text 7","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8019," ",16038,"ext. alarm text 8","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8020," ",16040,"ext. alarm text 9","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8021," ",16042,"ext. alarm text 10","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8022," ",16044,"ext. alarm text 11","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8023," ",16046,"ext. alarm text 12","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8024," ",16048,"ext. alarm text 13","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8025," ",16050,"ext. alarm text 14","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8026," ",16052,"ext. alarm text 15","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8027," ",16054,"ext. alarm text 16","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8028," ",16056,"ext. alarm text 17","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8029," ",16058,"ext. alarm text 18","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8030," ",16060,"ext. alarm text 19","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[{"$nulls":3}," "]
["External alarm 7",null,null," "]
[null,8100,0,8100,"ext. alarm config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->extalarms","1, (2)"]
[null,8101,1,8101,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","r","simulates alarm to check resulting output","Service->equipment->extalarms","1, (2)"]
[null,8102,2,8102,"ext. alarm active","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->misc","2, (1)"]
[null,8103,3,8103,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","r","simulates alarm to check resulting output","Service->equipment->extalarms","1, (2)"]
[null,8104,4,8104,"ext. alarm common alarm","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->extalarms","1, (2)"]
[null,8105,5,8105,null,"internal","bit"]
[null,8106,6,8106,null,"internal","bit"]
[null,8107,7,8107,null,"internal","bit"]
[null,8108," ",16216,"ext. alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,8109," ",16218,"ext. alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,8110," ",16220,"ext. alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,8111," ",16222,"ext. alarm text 0","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[null,8112," ",16224,"ext. alarm text 1","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8113," ",16226,"ext. alarm text 2","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8114," ",16228,"ext. alarm text 3","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8115," ",16230,"ext. alarm text 4","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8116," ",16232,"ext. alarm text 5","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8117," ",16234,"ext. alarm text 6","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8118," ",16236,"ext. alarm text 7","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8119," ",16238,"ext. alarm text 8","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8120," ",16240,"ext. alarm text 9","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8121," ",16242,"ext. alarm text 10","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8122," ",16244,"ext. alarm text 11","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8123," ",16246,"ext. alarm text 12","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8124," ",16248,"ext. alarm text 13","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8125," ",16250,"ext. alarm text 14","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8126," ",16252,"ext. alarm text 15","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8127," ",16254,"ext. alarm text 16","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8128," ",16256,"ext. alarm text 17","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8129," ",16258,"ext. alarm text 18","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8130," ",16260,"ext. alarm text 19","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[{"$nulls":3}," "]
["External alarm 8",null,null," "]
[null,8200,0,8200,"ext. alarm config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->extalarms","1, (2)"]
[null,8201,1,8201,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","r","simulates alarm to check resulting output","Service->equipment->extalarms","1, (2)"]
[null,8202,2,8202,"ext. alarm active","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->misc","2, (1)"]
[null,8203,3,8203,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","r","simulates alarm to check resulting output","Service->equipment->extalarms","1, (2)"]
[null,8204,4,8204,"ext. alarm common alarm","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->extalarms","1, (2)"]
[null,8205,5,8205,null,"internal","bit"]
[null,8206,6,8206,null,"internal","bit"]
[null,8207,7,8207,null,"internal","bit"]
[null,8208," ",16416,"ext. alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,8209," ",16418,"ext. alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,8210," ",16420,"ext. alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,8211," ",16422,"ext. alarm text 0","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[null,8212," ",16424,"ext. alarm text 1","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8213," ",16426,"ext. alarm text 2","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8214," ",16428,"ext. alarm text 3","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8215," ",16430,"ext. alarm text 4","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8216," ",16432,"ext. alarm text 5","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8217," ",16434,"ext. alarm text 6","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8218," ",16436,"ext. alarm text 7","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8219," ",16438,"ext. alarm text 8","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8220," ",16440,"ext. alarm text 9","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8221," ",16442,"ext. alarm text 10","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8222," ",16444,"ext. alarm text 11","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8223," ",16446,"ext. alarm text 12","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8224," ",16448,"ext. alarm text 13","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8225," ",16450,"ext. alarm text 14","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8226," ",16452,"ext. alarm text 15","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8227," ",16454,"ext. alarm text 16","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8228," ",16456,"ext. alarm text 17","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8229," ",16458,"ext. alarm text 18","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8230," ",16460,"ext. alarm text 19","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[{"$nulls":3}," "]
["External alarm 9",null,null," "]
[null,8300,0,8300,"ext. alarm config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->extalarms","1, (2)"]
[null,8301,1,8301,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","r","simulates alarm to check resulting output","Service->equipment->extalarms","1, (2)"]
[null,8302,2,8302,"ext. alarm active","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->misc","2, (1)"]
[null,8303,3,8303,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","r","simulates alarm to check resulting output","Service->equipment->extalarms","1, (2)"]
[null,8304,4,8304,"ext. alarm common alarm","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->extalarms","1, (2)"]
[null,8305,5,8305,null,"internal","bit"]
[null,8306,6,8306,null,"internal","bit"]
[null,8307,7,8307,null,"internal","bit"]
[null,8308," ",16616,"ext. alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,8309," ",16618,"ext. alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,8310," ",16620,"ext. alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,8311," ",16622,"ext. alarm text 0","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[null,8312," ",16624,"ext. alarm text 1","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8313," ",16626,"ext. alarm text 2","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8314," ",16628,"ext. alarm text 3","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8315," ",16630,"ext. alarm text 4","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8316," ",16632,"ext. alarm text 5","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8317," ",16634,"ext. alarm text 6","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8318," ",16636,"ext. alarm text 7","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8319," ",16638,"ext. alarm text 8","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8320," ",16640,"ext. alarm text 9","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8321," ",16642,"ext. alarm text 10","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8322," ",16644,"ext. alarm text 11","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8323," ",16646,"ext. alarm text 12","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8324," ",16648,"ext. alarm text 13","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8325," ",16650,"ext. alarm text 14","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8326," ",16652,"ext. alarm text 15","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8327," ",16654,"ext. alarm text 16","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8328," ",16656,"ext. alarm text 17","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8329," ",16658,"ext. alarm text 18","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8330," ",16660,"ext. alarm text 19","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[{"$nulls":3}," "]
["External alarm 10",null,null," "]
[null,8400,0,8400,"ext. alarm config active","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->extalarms","1, (2)"]
[null,8401,1,8401,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","r","simulates alarm to check resulting output","Service->equipment->extalarms","1, (2)"]
[null,8402,2,8402,"ext. alarm active","internal","bit",null,"0 / 1",null,"r","r",null,"Info->state->misc","2, (1)"]
[null,8403,3,8403,"ext. alarm manual operation active","internal","bit",null,"0 / 1",null,"rw","r","simulates alarm to check resulting output","Service->equipment->extalarms","1, (2)"]
[null,8404,4,8404,"ext. alarm common alarm","internal","bit",null,"0 / 1",null,"rw","r",null,"Service->equipment->extalarms","1, (2)"]
[null,8405,5,8405,null,"internal","bit"]
[null,8406,6,8406,null,"internal","bit"]
[null,8407,7,8407,null,"internal","bit"]
[null,8408," ",16816,"ext. alarm digital in","internal","byte",null,"0..42",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,8409," ",16818,"ext. alarm priorities","internal","byte",null,"0..31",null,"rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,8410," ",16820,"ext. alarm delay","internal","byte",null,"0..100","seconds","rw","r",null,"Service->equipment->extalarms","3, (4)"]
[null,8411," ",16822,"ext. alarm text 0","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[null,8412," ",16824,"ext. alarm text 1","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8413," ",16826,"ext. alarm text 2","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8414," ",16828,"ext. alarm text 3","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8415," ",16830,"ext. alarm text 4","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8416," ",16832,"ext. alarm text 5","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8417," ",16834,"ext. alarm text 6","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8418," ",16836,"ext. alarm text 7","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8419," ",16838,"ext. alarm text 8","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8420," ",16840,"ext. alarm text 9","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8421," ",16842,"ext. alarm text 10","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8422," ",16844,"ext. alarm text 11","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8423," ",16846,"ext. alarm text 12","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8424," ",16848,"ext. alarm text 13","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8425," ",16850,"ext. alarm text 14","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8426," ",16852,"ext. alarm text 15","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8427," ",16854,"ext. alarm text 16","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8428," ",16856,"ext. alarm text 17","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8429," ",16858,"ext. alarm text 18","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[null,8430," ",16860,"ext. alarm text 19","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)",null,null,"not accessible"]
[]
["DP8500..DP11699 formerly defined for sequencing data, but never implemented => reusable",null,null," "]
[]
["Alarmbitmap for easy consecutive alarmrequest"]
[null,8500,null,8500,"airflow 1",null,"bit",null,"0 / 1","ok/alarm",null,null,"usually unused and substituted by fan-failure",null,"1, 2"]
[null,8501,null,8501,"airflow 2",null,"bit",null,"0 / 1","ok/alarm",null,null,"usually unused and substituted by fan-failure",null,"1, 2"]
[null,8502,null,8502,"airflow 3",null,"bit",null,"0 / 1","ok/alarm",null,null,"usually unused and substituted by fan-failure",null,"1, 2"]
[null,8503,null,8503,"highpressure 1",null,"bit",null,"0 / 1","ok/alarm",null,null,"unused, combined with compressor failure",null,"1, 2"]
[null,8504,null,8504,"highpressure 2",null,"bit",null,"0 / 1","ok/alarm",null,null,"unused, combined with compressor failure",null,"1, 2"]
[null,8505,null,8505,"water detector",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8506,null,8506,"Phasecheck",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8507,null,8507,"fire/smoke",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2",null,null,"then: local stop, no reset over bms possible"]
[null,8508,null,8508,"return air temp. too high alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8509,null,8509,"return air humid. too high alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8510,null,8510,"supply air temp. too high alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8511,null,8511,"supply air humid. too high alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8512,null,8512,"water temp. too high alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8513,null,8513,"return air temp. too low alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8514,null,8514,"return air humid. too low alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8515,null,8515,"supply air temp. too low alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8516,null,8516,"supply air humid. too low alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8517,null,8517,"water temp. too low alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8518,null,8518,"sensor 1 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8519,null,8519,"sensor 2 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8520,null,8520,"sensor 3 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8521,null,8521,"sensor 4 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8522,null,8522,"sensor 5 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8523,null,8523,"sensor 6 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8524,null,8524,"sensor 7 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8525,null,8525,"sensor 8 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8526,null,8526,"sensor 9 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8527,null,8527,"sensor 10 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8528,null,8528,"sensor 11 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8529,null,8529,"sensor 12 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8530,null,8530,"sensor 13 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8531,null,8531,"sensor 14 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8532,null,8532,"sensor 15 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8533,null,8533,"sensor 16 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8534,null,8534,"sensor 17 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8535,null,8535,"sensor 18 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8536,null,8536,"sensor 19 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8537,null,8537,"sensor 20 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8538,null,8538,"sensor 21 limit alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8539,null,8539,"sensor 1 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8540,null,8540,"sensor 2 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8541,null,8541,"sensor 3 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8542,null,8542,"sensor 4 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8543,null,8543,"sensor 5 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8544,null,8544,"sensor 6 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8545,null,8545,"sensor 7 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8546,null,8546,"sensor 8 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8547,null,8547,"sensor 9 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8548,null,8548,"sensor 10 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8549,null,8549,"sensor 11 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8550,null,8550,"sensor 12 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8551,null,8551,"sensor 13 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8552,null,8552,"sensor 14 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8553,null,8553,"sensor 15 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8554,null,8554,"sensor 16 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8555,null,8555,"sensor 17 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8556,null,8556,"sensor 18 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8557,null,8557,"sensor 19 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8558,null,8558,"sensor 20 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8559,null,8559,"sensor 21 defect alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8560,null,8560,"compr. 1 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8561,null,8561,"compr. 2 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8562,null,8562,"compr.1 low press. Alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8563,null,8563,"compr.2 low press. Alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8564,null,8564,"elec.-heating1 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8565,null,8565,"elec.-heating2 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8566,null,8566,"elec.-heating3 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8567,null,8567,"elec.-heating4 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8568,null,8568,"drycooler1 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8569,null,8569,"drycooler2 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8570,null,8570,"drycooler3 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8571,null,8571,"drycooler4 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8572,null,8572,"pump1 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8573,null,8573,"pump2 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8574,null,8574,"pump3 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8575,null,8575,"pump4 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8576,null,8576,"humidifier1 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8577,null,8577,"humidifier2 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8578,null,8578,"humidifier3 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8579,null,8579,"humidifier1 alarm 5µS",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8580,null,8580,"humidifier2 alarm 5µS",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8581,null,8581,"humidifier3 alarm 5µS",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8582,null,8582,"humidifier1 alarm 20µS",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8583,null,8583,"humidifier2 alarm 20µS",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8584,null,8584,"humidifier3 alarm 20µS",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8585,null,8585,"fan1 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8586,null,8586,"fan2 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8587,null,8587,"fan3 alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8588,null,8588,"fan1 filter alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8589,null,8589,"fan2 filter alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8590,null,8590,"fan3 filter alarm",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8591,null,8591,"ext. Alarm 1 active",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8592,null,8592,"ext. Alarm 2 active",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8593,null,8593,"ext. Alarm 3 active",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8594,null,8594,"ext. Alarm 4 active",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8595,null,8595,"ext. Alarm 5 active",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8596,null,8596,"ext. Alarm 6 active",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8597,null,8597,"ext. Alarm 7 active",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8598,null,8598,"ext. Alarm 8 active",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8599,null,8599,"ext. Alarm 9 active",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[null,8600,null,8600,"ext. Alarm 10 active",null,"bit",null,"0 / 1","ok/alarm","r","r",null,null,"1, 2"]
[{"$nulls":3}," "]
["My zone",null,null," "]
[null,11700,null,23400,"my zone","internal","byte",null,"0..32",null,"r","r",null,"sequencing-view; Service->sequencing",null,"r"]
[null,11701,null,23402,"my zone room temperature","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r",null,"sequencing-view; Info->state->actual/setpoints",null,"r"]
[null,11702," ",23404,"my zone room humidity","internal","word",null,"0..1000","0,0..100,0%rF","r","r",null,"sequencing-view; Info->state->actual/setpoints",null,"r"]
[null,11703," ",23406,"my zone supply temperature","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r",null,"sequencing-view; Info->state->actual/setpoints",null,"r"]
[null,11704," ",23408,"my zone supply humidity","internal","word",null,"0..1000","0,0..100,0%rF","r","r",null,"sequencing-view; Info->state->actual/setpoints",null,"r"]
[null,11705," ",23410,"my zone sequencing time","internal","word",null,"0..0xFFFF","minutes","r","r",null,"sequencing-view; Service->sequencing",null,"r"]
[null,11706," ",23418,"my zone number of error units","internal","byte",null,"0..32",null,"r","r",null,"sequencing-view; Service->sequencing",null,"r"]
[null,11707," ",23420,"my zone emergency temperature","internal","word",null,"0..400","0,0..40,0°C","r","r",null,"sequencing-view; Service->sequencing",null,"r"]
[null,11708,0,11708,"my zone CW energy save mode activ","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing",null,"r"]
[null,11709,1,11709,"my zone testsequencing","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing",null,"r"]
[null,11710,2,{"$nulls":3},"bit",{"$nulls":3},"r"]
[null,11711,3,{"$nulls":3},"bit",{"$nulls":3},"r"]
[null,11712,4,{"$nulls":3},"bit",{"$nulls":3},"r"]
[null,11713,5,{"$nulls":3},"bit",{"$nulls":3},"r"]
[null,11714,6,{"$nulls":3},"bit",{"$nulls":3},"r"]
[null,11715,7,{"$nulls":3},"bit",{"$nulls":3},"r"]
[null,11716,0,11716,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11717,1,11717,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11718,2,11718,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11719,3,11719,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11720,4,11720,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11721,5,11721,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11722,6,11722,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11723,7,11723,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11724,0,11724,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11725,1,11725,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11726,2,11726,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11727,3,11727,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11728,4,11728,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11729,5,11729,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11730,6,11730,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11731,7,11731,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11732,0,11732,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11733,1,11733,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11734,2,11734,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11735,3,11735,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11736,4,11736,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11737,5,11737,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11738,6,11738,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11739,7,11739,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11740,0,11740,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11741,1,11741,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11742,2,11742,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11743,3,11743,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11744,4,11744,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11745,5,11745,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11746,6,11746,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11747,7,11747,"XYZ alarm valid","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11748,0,11748,"unit 0 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11749,1,11749,"unit 1 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11750,2,11750,"unit 2 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11751,3,11751,"unit 3 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11752,4,11752,"unit 4 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11753,5,11753,"unit 5 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11754,6,11754,"unit 6 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11755,7,11755,"unit 7 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11756,0,11756,"unit 8 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11757,1,11757,"unit 9 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11758,2,11758,"unit 10 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11759,3,11759,"unit 11 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11760,4,11760,"unit 12 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11761,5,11761,"unit 13 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11762,6,11762,"unit 14 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11763,7,11763,"unit 15 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11764,0,11764,"unit 16 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11765,1,11765,"unit 17 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11766,2,11766,"unit 18 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11767,3,11767,"unit 19 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11768,4,11768,"unit 20 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11769,5,11769,"unit 21 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11770,6,11770,"unit 22 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11771,7,11771,"unit 23 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11772,0,11772,"unit 24 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11773,1,11773,"unit 25 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11774,2,11774,"unit 26 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11775,3,11775,"unit 27 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11776,4,11776,"unit 28 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11777,5,11777,"unit 29 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11778,6,11778,"unit 30 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[null,11779,7,11779,"unit 31 member of zone","internal","bit",null,"0 / 1",null,"r","r",null,"sequencing-view; Service->sequencing"]
[{"$nulls":3}," "]
[{"$nulls":3}," "]
["Global zone data",null,null," "]
[null,11800,0,11800,"emergency operation active","internal","bit",null,"0 / 1",null,"r","r",null,"statusline?","2, (1)","r"]
[null,11801,1,11801,null,"internal","bit"]
[null,11802,2,11802,null,"internal","bit"]
[null,11803,3,11803,null,"internal","bit"]
[null,11804,4,11804,null,"internal","bit"]
[null,11805,5,11805,null,"internal","bit"]
[null,11806,6,11806,null,"internal","bit"]
[null,11807,7,11807,null,"internal","bit"]
[null,11808," ",23616,"zone of unit0","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11809," ",23618,"zone of unit1","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11810," ",23620,"zone of unit2","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11811," ",23622,"zone of unit3","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11812," ",23624,"zone of unit4","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11813," ",23626,"zone of unit5","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11814," ",23628,"zone of unit6","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11815," ",23630,"zone of unit7","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11816," ",23632,"zone of unit8","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11817," ",23634,"zone of unit9","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11818," ",23636,"zone of unit10","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11819," ",23638,"zone of unit11","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11820," ",23640,"zone of unit12","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11821," ",23642,"zone of unit13","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11822," ",23644,"zone of unit14","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11823," ",23646,"zone of unit15","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11824," ",23648,"zone of unit16","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11825," ",23650,"zone of unit17","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11826," ",23652,"zone of unit18","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11827," ",23654,"zone of unit19","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11828," ",23656,"zone of unit20","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11829," ",23658,"zone of unit21","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11830," ",23660,"zone of unit22","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11831," ",23662,"zone of unit23","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11832," ",23664,"zone of unit24","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11833," ",23666,"zone of unit25","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11834," ",23668,"zone of unit26","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11835," ",23670,"zone of unit27","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11836," ",23672,"zone of unit28","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11837," ",23674,"zone of unit29","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11838," ",23676,"zone of unit30","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[null,11839," ",23678,"zone of unit31","internal","byte",null,"1..32",null,"r","r",null,"sequencing-view","3, (4)"]
[{"$nulls":3}," "]
[{"$nulls":3}," "]
[{"$nulls":3}," "]
[{"$nulls":3}," "]
["eventlog:",null,null," "]
[null,12000," ",24000,"unit event1 year","internal","byte",null,"0..99","2000..2099","r","r",null,"Info->events",null,"r"]
[null,12001," ",24002,"unit event1 month","internal","byte",null,"1..12",null,"r","r",null,"Info->events",null,"r"]
[null,12002," ",24004,"unit event1 day","internal","byte",null,"1..31",null,"r","r",null,"Info->events",null,"r"]
[null,12003," ",24006,"unit event1 hour","internal","byte",null,"0..23",null,"r","r",null,"Info->events",null,"r"]
[null,12004," ",24008,"unit event1 minute","internal","byte",null,"0..59",null,"r","r",null,"Info->events",null,"r"]
[null,12005," ",24010,"unit event1 second","internal","byte",null,"0..59",null,"r","r",null,"Info->events",null,"r"]
[null,12006," ",24012,"unit event1 text-ID","internal","word",null,"0..0xFFFF",null,"r","r",null,"Info->events",null,"r"]
[{"$nulls":3}," "]
[null,12007," ",24014,"unit event2 year","internal","byte",null,"0..99","2000..2099","r","r",null,"Info->events",null,"r"]
[null,12008," ",24016,"unit event2 month","internal","byte",null,"1..12",null,"r","r",null,"Info->events",null,"r"]
[null,12009," ",24018,"unit event2 day","internal","byte",null,"1..31",null,"r","r",null,"Info->events",null,"r"]
[null,12010," ",24020,"unit event2 hour","internal","byte",null,"0..23",null,"r","r",null,"Info->events",null,"r"]
[null,12011," ",24022,"unit event2 minute","internal","byte",null,"0..59",null,"r","r",null,"Info->events",null,"r"]
[null,12012," ",24024,"unit event2 second","internal","byte",null,"0..59",null,"r","r",null,"Info->events",null,"r"]
[null,12013," ",24026,"unit event2 text-ID","internal","word",null,"0..0xFFFF",null,"r","r",null,"Info->events",null,"r"]
[{"$nulls":3}," "]
[null,12014," ",24028,"unit event3 year","internal","byte",null,"0..99","2000..2099","r","r",null,"Info->events",null,"r"]
[null,12015," ",24030,"unit event3 month","internal","byte",null,"1..12",null,"r","r",null,"Info->events",null,"r"]
[null,12016," ",24032,"unit event3 day","internal","byte",null,"1..31",null,"r","r",null,"Info->events",null,"r"]
[null,12017," ",24034,"unit event3 hour","internal","byte",null,"0..23",null,"r","r",null,"Info->events",null,"r"]
[null,12018," ",24036,"unit event3 minute","internal","byte",null,"0..59",null,"r","r",null,"Info->events",null,"r"]
[null,12019," ",24038,"unit event3 second","internal","byte",null,"0..59",null,"r","r",null,"Info->events",null,"r"]
[null,12020," ",24040,"unit event3 text-ID","internal","word",null,"0..0xFFFF",null,"r","r",null,"Info->events",null,"r"]
[null,"\""," ",2,"\"","\"","\"",null,"\"","\"","\"","\"",null,"Info->events",null,"\""]
[null,13393," ",26786,"unit event200 year","internal","byte",null,"0..99","2000..2099","r","r",null,"Info->events",null,"r"]
[null,13394," ",26788,"unit event200 month","internal","byte",null,"1..12",null,"r","r",null,"Info->events",null,"r"]
[null,13395," ",26790,"unit event200 day","internal","byte",null,"1..31",null,"r","r",null,"Info->events",null,"r"]
[null,13396," ",26792,"unit event200 hour","internal","byte",null,"0..23",null,"r","r",null,"Info->events",null,"r"]
[null,13397," ",26794,"unit event200 minute","internal","byte",null,"0..59",null,"r","r",null,"Info->events",null,"r"]
[null,13398," ",26796,"unit event200 second","internal","byte",null,"0..59",null,"r","r",null,"Info->events",null,"r"]
[null,13399," ",26798,"unit event200 text-ID","internal","word",null,"0..0xFFFF",null,"r","r",null,"Info->events",null,"r"]
[{"$nulls":3}," "]
[null,14000," ",28000,"system name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[null,14001," ",28002,"system name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[null,14002," ",28004,"system name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[null,14003," ",28006,"system name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,14004," ",28008,"system name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[null,14005," ",28010,"system name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[null,14006," ",28012,"system name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[null,14007," ",28014,"system name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[null,14008," ",28016,"system name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[null,14009," ",28018,"system name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[null,14010," ",28020,"system name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[null,14011," ",28022,"system name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[null,14012," ",28024,"system name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[null,14013," ",28026,"system name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[null,14014," ",28028,"system name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[null,14015," ",28030,"system name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)"]
[{"$nulls":3}," "]
[null,14100," ",28200,"unit name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,14101," ",28202,"unit name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,14102," ",28204,"unit name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,14103," ",28206,"unit name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,14104," ",28208,"unit name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,14105," ",28210,"unit name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,14106," ",28212,"unit name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,14107," ",28214,"unit name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,14108," ",28216,"unit name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,14109," ",28218,"unit name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,14110," ",28220,"unit name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,14111," ",28222,"unit name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,14112," ",28224,"unit name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,14113," ",28226,"unit name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,14114," ",28228,"unit name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[null,14115," ",28230,"unit name","internal","byte",null,"32..125","ASCII","rw","r","one character of string","Service->equipment->extalarms","3, (4)","rw"]
[{"$nulls":3}," "]
["Data log 1",null," "," "]
[null,15000," ",30000,"unit valuelog1 type","internal","byte",null,"0..15",null,"rw","r",null,"Info->graphic; Control->graphic",null,"r"]
[null,15001," ",30002,"unit valuelog1 period","internal","word",null,"0..60000","minutes","rw","r",null,"Info->graphic; Control->graphic",null,"r"]
[null,15002," ",30004,"unit valuelog1 number","internal","word",null,"0..1440",null,"r","r",null,"Info->graphic",null,"r"]
[null,15003," ",30006,"unit valuelog1 value1 year","internal","byte",null,"0..99","2000..2099","r","r",null,"Info->graphic",null,"r"]
[null,15004," ",30008,"unit valuelog1 value1 month","internal","byte",null,"1..12",null,"r","r",null,"Info->graphic",null,"r"]
[null,15005," ",30010,"unit valuelog1 value1 day","internal","byte",null,"1..31",null,"r","r",null,"Info->graphic",null,"r"]
[null,15006," ",30012,"unit valuelog1 value1 hour","internal","byte",null,"0..23",null,"r","r",null,"Info->graphic",null,"r"]
[null,15007," ",30014,"unit valuelog1 value1 minute","internal","byte",null,"0..59",null,"r","r",null,"Info->graphic",null,"r"]
[null,15008," ",30016,"unit valuelog1 value1 second","internal","byte",null,"0..59",null,"r","r",null,"Info->graphic",null,"r"]
[null,15009," ",30018,"unit valuelog1 value1 value","internal","word",null,"0..0xFFFF",null,"r","r","phys. Unit depends on type","Info->graphic",null,"r"]
[{"$nulls":3}," "]
[null,15010," ",30020,"unit valuelog1 value2 year","internal","byte",null,"0..99","2000..2099","r","r",null,"Info->graphic",null,"r"]
[null,15011," ",30022,"unit valuelog1 value2 month","internal","byte",null,"1..12",null,"r","r",null,"Info->graphic",null,"r"]
[null,15012," ",30024,"unit valuelog1 value2 day","internal","byte",null,"1..31",null,"r","r",null,"Info->graphic",null,"r"]
[null,15013," ",30026,"unit valuelog1 value2 hour","internal","byte",null,"0..23",null,"r","r",null,"Info->graphic",null,"r"]
[null,15014," ",30028,"unit valuelog1 value2 minute","internal","byte",null,"0..59",null,"r","r",null,"Info->graphic",null,"r"]
[null,15015," ",30030,"unit valuelog1 value2 second","internal","byte",null,"0..59",null,"r","r",null,"Info->graphic",null,"r"]
[null,15016," ",30032,"unit valuelog1 value2 value","internal","word",null,"0..0xFFFF",null,"r","r","phys. Unit depends on type","Info->graphic",null,"r"]
[{"$nulls":3}," "]
[null,15017," ",30034,"unit valuelog1 value3 year","internal","byte",null,"0..99","2000..2099","r","r",null,"Info->graphic",null,"r"]
[null,15018," ",30036,"unit valuelog1 value3 month","internal","byte",null,"1..12",null,"r","r",null,"Info->graphic",null,"r"]
[null,15019," ",30038,"unit valuelog1 value3 day","internal","byte",null,"1..31",null,"r","r",null,"Info->graphic",null,"r"]
[null,15020," ",30040,"unit valuelog1 value3 hour","internal","byte",null,"0..23",null,"r","r",null,"Info->graphic",null,"r"]
[null,15021," ",30042,"unit valuelog1 value3 minute","internal","byte",null,"0..59",null,"r","r",null,"Info->graphic",null,"r"]
[null,15022," ",30044,"unit valuelog1 value3 second","internal","byte",null,"0..59",null,"r","r",null,"Info->graphic",null,"r"]
[null,15023," ",30046,"unit valuelog1 value3 value","internal","word",null,"0..0xFFFF",null,"r","r","phys. Unit depends on type","Info->graphic",null,"r"]
[null,"\""," ",2,"\"","\"","\"",null,"\"","\"","\"","\"",null,"Info->graphic",null,"\""]
[null,25076," ",50152,"unit valuelog1 value1440 year","internal","byte",null,"0..99","2000..2099","r","r",null,"Info->graphic",null,"r"]
[null,25077," ",50154,"unit valuelog1 value1440 month","internal","byte",null,"1..12",null,"r","r",null,"Info->graphic",null,"r"]
[null,25078," ",50156,"unit valuelog1 value1440 day","internal","byte",null,"1..31",null,"r","r",null,"Info->graphic",null,"r"]
[null,25079," ",50158,"unit valuelog1 value1440 hour","internal","byte",null,"0..23",null,"r","r",null,"Info->graphic",null,"r"]
[null,25080," ",50160,"unit valuelog1 value1440 minute","internal","byte",null,"0..59",null,"r","r",null,"Info->graphic",null,"r"]
[null,25081," ",50162,"unit valuelog1 value1440 second","internal","byte",null,"0..59",null,"r","r",null,"Info->graphic",null,"r"]
[null,25082," ",50164,"unit valuelog1 value1440 value","internal","word",null,"0..0xFFFF",null,"r","r","phys. Unit depends on type","Info->graphic",null,"r"]
[{"$nulls":3}," "]
["Data log 2",null," "," "]
[null,25100," ",50200,"unit valuelog2 type","internal","byte",null,"0..15",null,"rw","r",null,"Info->graphic; Control->graphic",null,"r"]
[null,25101," ",50202,"unit valuelog2 period","internal","word",null,"0..60000","minutes","rw","r",null,"Info->graphic; Control->graphic",null,"r"]
[null,25102," ",50204,"unit valuelog2 number","internal","word",null,"0..1440",null,"r","r",null,"Info->graphic",null,"r"]
[null,25103," ",50206,"unit valuelog2 value1 year","internal","byte",null,"0..99","2000..2099","r","r",null,"Info->graphic",null,"r"]
[null,25104," ",50208,"unit valuelog2 value1 month","internal","byte",null,"1..12",null,"r","r",null,"Info->graphic",null,"r"]
[null,25105," ",50210,"unit valuelog2 value1 day","internal","byte",null,"1..31",null,"r","r",null,"Info->graphic",null,"r"]
[null,25106," ",50212,"unit valuelog2 value1 hour","internal","byte",null,"0..23",null,"r","r",null,"Info->graphic",null,"r"]
[null,25107," ",50214,"unit valuelog2 value1 minute","internal","byte",null,"0..59",null,"r","r",null,"Info->graphic",null,"r"]
[null,25108," ",50216,"unit valuelog2 value1 second","internal","byte",null,"0..59",null,"r","r",null,"Info->graphic",null,"r"]
[null,25109," ",50218,"unit valuelog2 value1 value","internal","word",null,"0..0xFFFF",null,"r","r","phys. Unit depends on type","Info->graphic",null,"r"]
[{"$nulls":3}," ",{"$nulls":11},"r"]
[null,25110," ",50220,"unit valuelog2 value2 year","internal","byte",null,"0..99","2000..2099","r","r",null,"Info->graphic",null,"r"]
[null,25111," ",50222,"unit valuelog2 value2 month","internal","byte",null,"1..12",null,"r","r",null,"Info->graphic",null,"r"]
[null,25112," ",50224,"unit valuelog2 value2 day","internal","byte",null,"1..31",null,"r","r",null,"Info->graphic",null,"r"]
[null,25113," ",50226,"unit valuelog2 value2 hour","internal","byte",null,"0..23",null,"r","r",null,"Info->graphic",null,"r"]
[null,25114," ",50228,"unit valuelog2 value2 minute","internal","byte",null,"0..59",null,"r","r",null,"Info->graphic",null,"r"]
[null,25115," ",50230,"unit valuelog2 value2 second","internal","byte",null,"0..59",null,"r","r",null,"Info->graphic",null,"r"]
[null,25116," ",50232,"unit valuelog2 value2 value","internal","word",null,"0..0xFFFF",null,"r","r","phys. Unit depends on type","Info->graphic",null,"r"]
[{"$nulls":3}," ",{"$nulls":11},"r"]
[null,25117," ",50234,"unit valuelog2 value3 year","internal","byte",null,"0..99","2000..2099","r","r",null,"Info->graphic",null,"r"]
[null,25118," ",50236,"unit valuelog2 value3 month","internal","byte",null,"1..12",null,"r","r",null,"Info->graphic",null,"r"]
[null,25119," ",50238,"unit valuelog2 value3 day","internal","byte",null,"1..31",null,"r","r",null,"Info->graphic",null,"r"]
[null,25120," ",50240,"unit valuelog2 value3 hour","internal","byte",null,"0..23",null,"r","r",null,"Info->graphic",null,"r"]
[null,25121," ",50242,"unit valuelog2 value3 minute","internal","byte",null,"0..59",null,"r","r",null,"Info->graphic",null,"r"]
[null,25122," ",50244,"unit valuelog2 value3 second","internal","byte",null,"0..59",null,"r","r",null,"Info->graphic",null,"r"]
[null,25123," ",50246,"unit valuelog2 value3 value","internal","word",null,"0..0xFFFF",null,"r","r","phys. Unit depends on type","Info->graphic",null,"r"]
[null,"\""," ",2,"\"","\"","\"",null,"\"","\"","\"","\"",null,"Info->graphic",null,"r"]
[null,35176," ",70352,"unit valuelog2 value1440 year","internal","byte",null,"0..99","2000..2099","r","r",null,"Info->graphic",null,"r"]
[null,35177," ",70354,"unit valuelog2 value1440 month","internal","byte",null,"1..12",null,"r","r",null,"Info->graphic",null,"r"]
[null,35178," ",70356,"unit valuelog2 value1440 day","internal","byte",null,"1..31",null,"r","r",null,"Info->graphic",null,"r"]
[null,35179," ",70358,"unit valuelog2 value1440 hour","internal","byte",null,"0..23",null,"r","r",null,"Info->graphic",null,"r"]
[null,35180," ",70360,"unit valuelog2 value1440 minute","internal","byte",null,"0..59",null,"r","r",null,"Info->graphic",null,"r"]
[null,35181," ",70362,"unit valuelog2 value1440 second","internal","byte",null,"0..59",null,"r","r",null,"Info->graphic",null,"r"]
[null,35182," ",70364,"unit valuelog2 value1440 value","internal","word",null,"0..0xFFFF",null,"r","r","phys. Unit depends on type","Info->graphic",null,"r"]
[{"$nulls":3}," "]
[{"$nulls":3}," "]
["Global Zone Data:",null,null," "]
[{"$nulls":3}," "]
[null,35200,null,70400,"Bitmap of zone 1 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35201,null,70402,"Bitmap of zone 2 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35202,null,70404,"Bitmap of zone 3 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35203,null,70406,"Bitmap of zone 4 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35204,null,70408,"Bitmap of zone 5 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35205,null,70410,"Bitmap of zone 6 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35206,null,70412,"Bitmap of zone 7 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35207,null,70414,"Bitmap of zone 8 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35208,null,70416,"Bitmap of zone 9 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35209,null,70418,"Bitmap of zone 10 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35210,null,70420,"Bitmap of zone 11 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35211,null,70422,"Bitmap of zone 12 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35212,null,70424,"Bitmap of zone 13 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35213,null,70426,"Bitmap of zone 14 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35214,null,70428,"Bitmap of zone 15 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35215,null,70430,"Bitmap of zone 16 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35216,null,70432,"Bitmap of zone 17 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35217,null,70434,"Bitmap of zone 18 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35218,null,70436,"Bitmap of zone 19 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35219,null,70438,"Bitmap of zone 20 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35220,null,70440,"Bitmap of zone 21 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35221,null,70442,"Bitmap of zone 22 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35222,null,70444,"Bitmap of zone 23 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35223,null,70446,"Bitmap of zone 24 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35224,null,70448,"Bitmap of zone 25 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35225,null,70450,"Bitmap of zone 26 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35226,null,70452,"Bitmap of zone 27 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35227,null,70454,"Bitmap of zone 28 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35228,null,70456,"Bitmap of zone 29 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35229,null,70458,"Bitmap of zone 30 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35230,null,70460,"Bitmap of zone 31 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35231,null,70462,"Bitmap of zone 32 members","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[{"$nulls":3}," "]
[null,35232,null,70464,"Sequencing time of zone 1","internal","UI16",null,"0..0xFFFF","hours","rw","r","Time in hours"]
[null,35233,null,70466,"Sequencing time of zone 2","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35234,null,70468,"Sequencing time of zone 3","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35235,null,70470,"Sequencing time of zone 4","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35236,null,70472,"Sequencing time of zone 5","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35237,null,70474,"Sequencing time of zone 6","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35238,null,70476,"Sequencing time of zone 7","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35239,null,70478,"Sequencing time of zone 8","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35240,null,70480,"Sequencing time of zone 9","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35241,null,70482,"Sequencing time of zone 10","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35242,null,70484,"Sequencing time of zone 11","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35243,null,70486,"Sequencing time of zone 12","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35244,null,70488,"Sequencing time of zone 13","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35245,null,70490,"Sequencing time of zone 14","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35246,null,70492,"Sequencing time of zone 15","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35247,null,70494,"Sequencing time of zone 16","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35248,null,70496,"Sequencing time of zone 17","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35249,null,70498,"Sequencing time of zone 18","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35250,null,70500,"Sequencing time of zone 19","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35251,null,70502,"Sequencing time of zone 20","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35252,null,70504,"Sequencing time of zone 21","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35253,null,70506,"Sequencing time of zone 22","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35254,null,70508,"Sequencing time of zone 23","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35255,null,70510,"Sequencing time of zone 24","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35256,null,70512,"Sequencing time of zone 25","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35257,null,70514,"Sequencing time of zone 26","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35258,null,70516,"Sequencing time of zone 27","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35259,null,70518,"Sequencing time of zone 28","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35260,null,70520,"Sequencing time of zone 29","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35261,null,70522,"Sequencing time of zone 30","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35262,null,70524,"Sequencing time of zone 31","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[null,35263,null,70526,"Sequencing time of zone 32","internal","UI16",null,"0..0xFFFF","hours","rw","r"]
[{"$nulls":3}," "]
[null,35264,null,70528,"Valid alarms 1 of zone 1","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35265,null,70530,"Valid alarms 1 of zone 2","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35266,null,70532,"Valid alarms 1 of zone 3","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35267,null,70534,"Valid alarms 1 of zone 4","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35268,null,70536,"Valid alarms 1 of zone 5","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35269,null,70538,"Valid alarms 1 of zone 6","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35270,null,70540,"Valid alarms 1 of zone 7","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35271,null,70542,"Valid alarms 1 of zone 8","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35272,null,70544,"Valid alarms 1 of zone 9","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35273,null,70546,"Valid alarms 1 of zone 10","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35274,null,70548,"Valid alarms 1 of zone 11","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35275,null,70550,"Valid alarms 1 of zone 12","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35276,null,70552,"Valid alarms 1 of zone 13","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35277,null,70554,"Valid alarms 1 of zone 14","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35278,null,70556,"Valid alarms 1 of zone 15","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35279,null,70558,"Valid alarms 1 of zone 16","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35280,null,70560,"Valid alarms 1 of zone 17","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35281,null,70562,"Valid alarms 1 of zone 18","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35282,null,70564,"Valid alarms 1 of zone 19","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35283,null,70566,"Valid alarms 1 of zone 20","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35284,null,70568,"Valid alarms 1 of zone 21","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35285,null,70570,"Valid alarms 1 of zone 22","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35286,null,70572,"Valid alarms 1 of zone 23","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35287,null,70574,"Valid alarms 1 of zone 24","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35288,null,70576,"Valid alarms 1 of zone 25","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35289,null,70578,"Valid alarms 1 of zone 26","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35290,null,70580,"Valid alarms 1 of zone 27","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35291,null,70582,"Valid alarms 1 of zone 28","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35292,null,70584,"Valid alarms 1 of zone 29","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35293,null,70586,"Valid alarms 1 of zone 30","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35294,null,70588,"Valid alarms 1 of zone 31","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35295,null,70590,"Valid alarms 1 of zone 32","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[{"$nulls":3}," "]
[null,35296,null,70592,"Valid alarms 2 of zone 1","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35297,null,70594,"Valid alarms 2 of zone 2","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35298,null,70596,"Valid alarms 2 of zone 3","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35299,null,70598,"Valid alarms 2 of zone 4","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35300,null,70600,"Valid alarms 2 of zone 5","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35301,null,70602,"Valid alarms 2 of zone 6","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35302,null,70604,"Valid alarms 2 of zone 7","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35303,null,70606,"Valid alarms 2 of zone 8","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35304,null,70608,"Valid alarms 2 of zone 9","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35305,null,70610,"Valid alarms 2 of zone 10","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35306,null,70612,"Valid alarms 2 of zone 11","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35307,null,70614,"Valid alarms 2 of zone 12","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35308,null,70616,"Valid alarms 2 of zone 13","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35309,null,70618,"Valid alarms 2 of zone 14","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35310,null,70620,"Valid alarms 2 of zone 15","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35311,null,70622,"Valid alarms 2 of zone 16","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35312,null,70624,"Valid alarms 2 of zone 17","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35313,null,70626,"Valid alarms 2 of zone 18","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35314,null,70628,"Valid alarms 2 of zone 19","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35315,null,70630,"Valid alarms 2 of zone 20","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35316,null,70632,"Valid alarms 2 of zone 21","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35317,null,70634,"Valid alarms 2 of zone 22","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35318,null,70636,"Valid alarms 2 of zone 23","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35319,null,70638,"Valid alarms 2 of zone 24","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35320,null,70640,"Valid alarms 2 of zone 25","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35321,null,70642,"Valid alarms 2 of zone 26","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35322,null,70644,"Valid alarms 2 of zone 27","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35323,null,70646,"Valid alarms 2 of zone 28","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35324,null,70648,"Valid alarms 2 of zone 29","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35325,null,70650,"Valid alarms 2 of zone 30","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35326,null,70652,"Valid alarms 2 of zone 31","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35327,null,70654,"Valid alarms 2 of zone 32","internal","UI32",null,"0-0xFFFFFFFF","bit-coded","rw","r"]
[{"$nulls":3}," "]
[null,35328,null,70656,"5 min testsequencing active in zone 1","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35329,null,70658,"5 min testsequencing active in zone 2","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35330,null,70660,"5 min testsequencing active in zone 3","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35331,null,70662,"5 min testsequencing active in zone 4","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35332,null,70664,"5 min testsequencing active in zone 5","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35333,null,70666,"5 min testsequencing active in zone 6","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35334,null,70668,"5 min testsequencing active in zone 7","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35335,null,70670,"5 min testsequencing active in zone 8","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35336,null,70672,"5 min testsequencing active in zone 9","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35337,null,70674,"5 min testsequencing active in zone 10","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35338,null,70676,"5 min testsequencing active in zone 11","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35339,null,70678,"5 min testsequencing active in zone 12","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35340,null,70680,"5 min testsequencing active in zone 13","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35341,null,70682,"5 min testsequencing active in zone 14","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35342,null,70684,"5 min testsequencing active in zone 15","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35343,null,70686,"5 min testsequencing active in zone 16","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35344,null,70688,"5 min testsequencing active in zone 17","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35345,null,70690,"5 min testsequencing active in zone 18","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35346,null,70692,"5 min testsequencing active in zone 19","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35347,null,70694,"5 min testsequencing active in zone 20","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35348,null,70696,"5 min testsequencing active in zone 21","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35349,null,70698,"5 min testsequencing active in zone 22","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35350,null,70700,"5 min testsequencing active in zone 23","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35351,null,70702,"5 min testsequencing active in zone 24","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35352,null,70704,"5 min testsequencing active in zone 25","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35353,null,70706,"5 min testsequencing active in zone 26","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35354,null,70708,"5 min testsequencing active in zone 27","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35355,null,70710,"5 min testsequencing active in zone 28","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35356,null,70712,"5 min testsequencing active in zone 29","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35357,null,70714,"5 min testsequencing active in zone 30","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35358,null,70716,"5 min testsequencing active in zone 31","internal","BIT1",null,"0..1",null,"rw","r"]
[null,35359,null,70718,"5 min testsequencing active in zone 32","internal","BIT1",null,"0..1",null,"rw","r"]
[{"$nulls":3}," "]
[null,35360,null,70720,"Number of error units of zone 1","internal","UI8",null,"0-32",null,"rw","r"]
[null,35361,null,70722,"Number of error units of zone 2","internal","UI8",null,"0-32",null,"rw","r"]
[null,35362,null,70724,"Number of error units of zone 3","internal","UI8",null,"0-32",null,"rw","r"]
[null,35363,null,70726,"Number of error units of zone 4","internal","UI8",null,"0-32",null,"rw","r"]
[null,35364,null,70728,"Number of error units of zone 5","internal","UI8",null,"0-32",null,"rw","r"]
[null,35365,null,70730,"Number of error units of zone 6","internal","UI8",null,"0-32",null,"rw","r"]
[null,35366,null,70732,"Number of error units of zone 7","internal","UI8",null,"0-32",null,"rw","r"]
[null,35367,null,70734,"Number of error units of zone 8","internal","UI8",null,"0-32",null,"rw","r"]
[null,35368,null,70736,"Number of error units of zone 9","internal","UI8",null,"0-32",null,"rw","r"]
[null,35369,null,70738,"Number of error units of zone 10","internal","UI8",null,"0-32",null,"rw","r"]
[null,35370,null,70740,"Number of error units of zone 11","internal","UI8",null,"0-32",null,"rw","r"]
[null,35371,null,70742,"Number of error units of zone 12","internal","UI8",null,"0-32",null,"rw","r"]
[null,35372,null,70744,"Number of error units of zone 13","internal","UI8",null,"0-32",null,"rw","r"]
[null,35373,null,70746,"Number of error units of zone 14","internal","UI8",null,"0-32",null,"rw","r"]
[null,35374,null,70748,"Number of error units of zone 15","internal","UI8",null,"0-32",null,"rw","r"]
[null,35375,null,70750,"Number of error units of zone 16","internal","UI8",null,"0-32",null,"rw","r"]
[null,35376,null,70752,"Number of error units of zone 17","internal","UI8",null,"0-32",null,"rw","r"]
[null,35377,null,70754,"Number of error units of zone 18","internal","UI8",null,"0-32",null,"rw","r"]
[null,35378,null,70756,"Number of error units of zone 19","internal","UI8",null,"0-32",null,"rw","r"]
[null,35379,null,70758,"Number of error units of zone 20","internal","UI8",null,"0-32",null,"rw","r"]
[null,35380,null,70760,"Number of error units of zone 21","internal","UI8",null,"0-32",null,"rw","r"]
[null,35381,null,70762,"Number of error units of zone 22","internal","UI8",null,"0-32",null,"rw","r"]
[null,35382,null,70764,"Number of error units of zone 23","internal","UI8",null,"0-32",null,"rw","r"]
[null,35383,null,70766,"Number of error units of zone 24","internal","UI8",null,"0-32",null,"rw","r"]
[null,35384,null,70768,"Number of error units of zone 25","internal","UI8",null,"0-32",null,"rw","r"]
[null,35385,null,70770,"Number of error units of zone 26","internal","UI8",null,"0-32",null,"rw","r"]
[null,35386,null,70772,"Number of error units of zone 27","internal","UI8",null,"0-32",null,"rw","r"]
[null,35387,null,70774,"Number of error units of zone 28","internal","UI8",null,"0-32",null,"rw","r"]
[null,35388,null,70776,"Number of error units of zone 29","internal","UI8",null,"0-32",null,"rw","r"]
[null,35389,null,70778,"Number of error units of zone 30","internal","UI8",null,"0-32",null,"rw","r"]
[null,35390,null,70780,"Number of error units of zone 31","internal","UI8",null,"0-32",null,"rw","r"]
[null,35391,null,70782,"Number of error units of zone 32","internal","UI8",null,"0-32",null,"rw","r"]
[{"$nulls":3}," "]
[null,35392,null,70784,"Emergency temperature of zone 1","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35393,null,70786,"Emergency temperature of zone 2","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35394,null,70788,"Emergency temperature of zone 3","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35395,null,70790,"Emergency temperature of zone 4","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35396,null,70792,"Emergency temperature of zone 5","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35397,null,70794,"Emergency temperature of zone 6","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35398,null,70796,"Emergency temperature of zone 7","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35399,null,70798,"Emergency temperature of zone 8","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35400,null,70800,"Emergency temperature of zone 9","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35401,null,70802,"Emergency temperature of zone 10","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35402,null,70804,"Emergency temperature of zone 11","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35403,null,70806,"Emergency temperature of zone 12","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35404,null,70808,"Emergency temperature of zone 13","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35405,null,70810,"Emergency temperature of zone 14","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35406,null,70812,"Emergency temperature of zone 15","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35407,null,70814,"Emergency temperature of zone 16","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35408,null,70816,"Emergency temperature of zone 17","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35409,null,70818,"Emergency temperature of zone 18","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35410,null,70820,"Emergency temperature of zone 19","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35411,null,70822,"Emergency temperature of zone 20","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35412,null,70824,"Emergency temperature of zone 21","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35413,null,70826,"Emergency temperature of zone 22","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35414,null,70828,"Emergency temperature of zone 23","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35415,null,70830,"Emergency temperature of zone 24","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35416,null,70832,"Emergency temperature of zone 25","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35417,null,70834,"Emergency temperature of zone 26","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35418,null,70836,"Emergency temperature of zone 27","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35419,null,70838,"Emergency temperature of zone 28","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35420,null,70840,"Emergency temperature of zone 29","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35421,null,70842,"Emergency temperature of zone 30","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35422,null,70844,"Emergency temperature of zone 31","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[null,35423,null,70846,"Emergency temperature of zone 32","internal","SI16",null,"0..400","0,0..40,0°C","rw","r"]
[{"$nulls":3}," "]
[null,35424,null,70848,"Emergency operation of zone 1 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35425,null,70850,"Emergency operation of zone 2 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35426,null,70852,"Emergency operation of zone 3 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35427,null,70854,"Emergency operation of zone 4 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35428,null,70856,"Emergency operation of zone 5 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35429,null,70858,"Emergency operation of zone 6 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35430,null,70860,"Emergency operation of zone 7 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35431,null,70862,"Emergency operation of zone 8 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35432,null,70864,"Emergency operation of zone 9 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35433,null,70866,"Emergency operation of zone 10 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35434,null,70868,"Emergency operation of zone 11 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35435,null,70870,"Emergency operation of zone 12 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35436,null,70872,"Emergency operation of zone 13 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35437,null,70874,"Emergency operation of zone 14 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35438,null,70876,"Emergency operation of zone 15 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35439,null,70878,"Emergency operation of zone 16 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35440,null,70880,"Emergency operation of zone 17 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35441,null,70882,"Emergency operation of zone 18 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35442,null,70884,"Emergency operation of zone 19 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35443,null,70886,"Emergency operation of zone 20 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35444,null,70888,"Emergency operation of zone 21 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35445,null,70890,"Emergency operation of zone 22 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35446,null,70892,"Emergency operation of zone 23 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35447,null,70894,"Emergency operation of zone 24 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35448,null,70896,"Emergency operation of zone 25 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35449,null,70898,"Emergency operation of zone 26 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35450,null,70900,"Emergency operation of zone 27 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35451,null,70902,"Emergency operation of zone 28 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35452,null,70904,"Emergency operation of zone 29 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35453,null,70906,"Emergency operation of zone 30 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35454,null,70908,"Emergency operation of zone 31 active","internal","BIT1",null,"0, 1",null,"r","r"]
[null,35455,null,70910,"Emergency operation of zone 32 active","internal","BIT1",null,"0, 1",null,"r","r"]
[{"$nulls":3}," "]
[null,35456,null,70912,"nMax of zone 1","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35457,null,70914,"nMax of zone 2","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35458,null,70916,"nMax of zone 3","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35459,null,70918,"nMax of zone 4","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35460,null,70920,"nMax of zone 5","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35461,null,70922,"nMax of zone 6","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35462,null,70924,"nMax of zone 7","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35463,null,70926,"nMax of zone 8","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35464,null,70928,"nMax of zone 9","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35465,null,70930,"nMax of zone 10","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35466,null,70932,"nMax of zone 11","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35467,null,70934,"nMax of zone 12","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35468,null,70936,"nMax of zone 13","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35469,null,70938,"nMax of zone 14","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35470,null,70940,"nMax of zone 15","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35471,null,70942,"nMax of zone 16","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35472,null,70944,"nMax of zone 17","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35473,null,70946,"nMax of zone 18","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35474,null,70948,"nMax of zone 19","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35475,null,70950,"nMax of zone 20","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35476,null,70952,"nMax of zone 21","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35477,null,70954,"nMax of zone 22","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35478,null,70956,"nMax of zone 23","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35479,null,70958,"nMax of zone 24","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35480,null,70960,"nMax of zone 25","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35481,null,70962,"nMax of zone 26","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35482,null,70964,"nMax of zone 27","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35483,null,70966,"nMax of zone 28","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35484,null,70968,"nMax of zone 29","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35485,null,70970,"nMax of zone 30","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35486,null,70972,"nMax of zone 31","internal","UI8",null,"0-100%",null,"rw","r"]
[null,35487,null,70974,"nMax of zone 32","internal","UI8",null,"0-100%",null,"rw","r"]
[{"$nulls":3}," "]
[null,35488,null,70976,"CW energy save mode of zone 1","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35489,null,70978,"CW energy save mode of zone 2","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35490,null,70980,"CW energy save mode of zone 3","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35491,null,70982,"CW energy save mode of zone 4","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35492,null,70984,"CW energy save mode of zone 5","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35493,null,70986,"CW energy save mode of zone 6","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35494,null,70988,"CW energy save mode of zone 7","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35495,null,70990,"CW energy save mode of zone 8","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35496,null,70992,"CW energy save mode of zone 9","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35497,null,70994,"CW energy save mode of zone 10","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35498,null,70996,"CW energy save mode of zone 11","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35499,null,70998,"CW energy save mode of zone 12","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35500,null,71000,"CW energy save mode of zone 13","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35501,null,71002,"CW energy save mode of zone 14","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35502,null,71004,"CW energy save mode of zone 15","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35503,null,71006,"CW energy save mode of zone 16","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35504,null,71008,"CW energy save mode of zone 17","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35505,null,71010,"CW energy save mode of zone 18","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35506,null,71012,"CW energy save mode of zone 19","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35507,null,71014,"CW energy save mode of zone 20","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35508,null,71016,"CW energy save mode of zone 21","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35509,null,71018,"CW energy save mode of zone 22","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35510,null,71020,"CW energy save mode of zone 23","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35511,null,71022,"CW energy save mode of zone 24","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35512,null,71024,"CW energy save mode of zone 25","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35513,null,71026,"CW energy save mode of zone 26","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35514,null,71028,"CW energy save mode of zone 27","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35515,null,71030,"CW energy save mode of zone 28","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35516,null,71032,"CW energy save mode of zone 29","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35517,null,71034,"CW energy save mode of zone 30","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35518,null,71036,"CW energy save mode of zone 31","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35519,null,71038,"CW energy save mode of zone 32","internal","BIT1",null,"0, 1",null,"rw","r"]
[{"$nulls":3}," "]
[null,35520,null,71040,"Remaining time to switch of zone 1","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35521,null,71042,"Remaining time to switch of zone 2","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35522,null,71044,"Remaining time to switch of zone 3","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35523,null,71046,"Remaining time to switch of zone 4","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35524,null,71048,"Remaining time to switch of zone 5","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35525,null,71050,"Remaining time to switch of zone 6","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35526,null,71052,"Remaining time to switch of zone 7","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35527,null,71054,"Remaining time to switch of zone 8","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35528,null,71056,"Remaining time to switch of zone 9","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35529,null,71058,"Remaining time to switch of zone 10","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35530,null,71060,"Remaining time to switch of zone 11","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35531,null,71062,"Remaining time to switch of zone 12","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35532,null,71064,"Remaining time to switch of zone 13","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35533,null,71066,"Remaining time to switch of zone 14","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35534,null,71068,"Remaining time to switch of zone 15","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35535,null,71070,"Remaining time to switch of zone 16","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35536,null,71072,"Remaining time to switch of zone 17","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35537,null,71074,"Remaining time to switch of zone 18","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35538,null,71076,"Remaining time to switch of zone 19","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35539,null,71078,"Remaining time to switch of zone 20","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35540,null,71080,"Remaining time to switch of zone 21","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35541,null,71082,"Remaining time to switch of zone 22","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35542,null,71084,"Remaining time to switch of zone 23","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35543,null,71086,"Remaining time to switch of zone 24","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35544,null,71088,"Remaining time to switch of zone 25","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35545,null,71090,"Remaining time to switch of zone 26","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35546,null,71092,"Remaining time to switch of zone 27","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35547,null,71094,"Remaining time to switch of zone 28","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35548,null,71096,"Remaining time to switch of zone 29","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35549,null,71098,"Remaining time to switch of zone 30","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35550,null,71100,"Remaining time to switch of zone 31","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[null,35551,null,71102,"Remaining time to switch of zone 32","internal","UI32",null,"0-0xFFFFFFFF","minutes","rw","r"]
[{"$nulls":3}," "]
[null,35552,null,71104,"Sequencing switch of zone 1","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35553,null,71106,"Sequencing switch of zone 2","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35554,null,71108,"Sequencing switch of zone 3","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35555,null,71110,"Sequencing switch of zone 4","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35556,null,71112,"Sequencing switch of zone 5","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35557,null,71114,"Sequencing switch of zone 6","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35558,null,71116,"Sequencing switch of zone 7","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35559,null,71118,"Sequencing switch of zone 8","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35560,null,71120,"Sequencing switch of zone 9","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35561,null,71122,"Sequencing switch of zone 10","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35562,null,71124,"Sequencing switch of zone 11","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35563,null,71126,"Sequencing switch of zone 12","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35564,null,71128,"Sequencing switch of zone 13","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35565,null,71130,"Sequencing switch of zone 14","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35566,null,71132,"Sequencing switch of zone 15","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35567,null,71134,"Sequencing switch of zone 16","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35568,null,71136,"Sequencing switch of zone 17","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35569,null,71138,"Sequencing switch of zone 18","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35570,null,71140,"Sequencing switch of zone 19","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35571,null,71142,"Sequencing switch of zone 20","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35572,null,71144,"Sequencing switch of zone 21","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35573,null,71146,"Sequencing switch of zone 22","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35574,null,71148,"Sequencing switch of zone 23","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35575,null,71150,"Sequencing switch of zone 24","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35576,null,71152,"Sequencing switch of zone 25","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35577,null,71154,"Sequencing switch of zone 26","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35578,null,71156,"Sequencing switch of zone 27","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35579,null,71158,"Sequencing switch of zone 28","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35580,null,71160,"Sequencing switch of zone 29","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35581,null,71162,"Sequencing switch of zone 30","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35582,null,71164,"Sequencing switch of zone 31","internal","BIT1",null,"0, 1",null,"rw","r"]
[null,35583,null,71166,"Sequencing switch of zone 32","internal","BIT1",null,"0, 1",null,"rw","r"]
[{"$nulls":3}," "]
[null,35900,null,null,"Sequencing Stop Bitmap of all zone","internal","UI32",null,"0..0xFFFFFFFF","bit-coded","rw","r"]
[{"$nulls":3}," "]
["Global Unit Data:",null,null," "]
[{"$nulls":3}," "]
[null,36000,null,72000,"Room temperature of unit 0","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36001,null,72002,"Room temperature of unit 1","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36002,null,72004,"Room temperature of unit 2","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36003,null,72006,"Room temperature of unit 3","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36004,null,72008,"Room temperature of unit 4","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36005,null,72010,"Room temperature of unit 5","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36006,null,72012,"Room temperature of unit 6","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36007,null,72014,"Room temperature of unit 7","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36008,null,72016,"Room temperature of unit 8","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36009,null,72018,"Room temperature of unit 9","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36010,null,72020,"Room temperature of unit 10","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36011,null,72022,"Room temperature of unit 11","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36012,null,72024,"Room temperature of unit 12","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36013,null,72026,"Room temperature of unit 13","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36014,null,72028,"Room temperature of unit 14","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36015,null,72030,"Room temperature of unit 15","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36016,null,72032,"Room temperature of unit 16","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36017,null,72034,"Room temperature of unit 17","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36018,null,72036,"Room temperature of unit 18","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36019,null,72038,"Room temperature of unit 19","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36020,null,72040,"Room temperature of unit 20","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36021,null,72042,"Room temperature of unit 21","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36022,null,72044,"Room temperature of unit 22","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36023,null,72046,"Room temperature of unit 23","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36024,null,72048,"Room temperature of unit 24","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36025,null,72050,"Room temperature of unit 25","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36026,null,72052,"Room temperature of unit 26","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36027,null,72054,"Room temperature of unit 27","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36028,null,72056,"Room temperature of unit 28","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36029,null,72058,"Room temperature of unit 29","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36030,null,72060,"Room temperature of unit 30","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36031,null,72062,"Room temperature of unit 31","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[{"$nulls":3}," "]
[null,36032,null,72064,"Room humidity of unit 0","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36033,null,72066,"Room humidity of unit 1","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36034,null,72068,"Room humidity of unit 2","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36035,null,72070,"Room humidity of unit 3","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36036,null,72072,"Room humidity of unit 4","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36037,null,72074,"Room humidity of unit 5","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36038,null,72076,"Room humidity of unit 6","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36039,null,72078,"Room humidity of unit 7","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36040,null,72080,"Room humidity of unit 8","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36041,null,72082,"Room humidity of unit 9","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36042,null,72084,"Room humidity of unit 10","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36043,null,72086,"Room humidity of unit 11","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36044,null,72088,"Room humidity of unit 12","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36045,null,72090,"Room humidity of unit 13","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36046,null,72092,"Room humidity of unit 14","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36047,null,72094,"Room humidity of unit 15","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36048,null,72096,"Room humidity of unit 16","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36049,null,72098,"Room humidity of unit 17","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36050,null,72100,"Room humidity of unit 18","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36051,null,72102,"Room humidity of unit 19","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36052,null,72104,"Room humidity of unit 20","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36053,null,72106,"Room humidity of unit 21","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36054,null,72108,"Room humidity of unit 22","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36055,null,72110,"Room humidity of unit 23","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36056,null,72112,"Room humidity of unit 24","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36057,null,72114,"Room humidity of unit 25","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36058,null,72116,"Room humidity of unit 26","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36059,null,72118,"Room humidity of unit 27","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36060,null,72120,"Room humidity of unit 28","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36061,null,72122,"Room humidity of unit 29","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36062,null,72124,"Room humidity of unit 30","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36063,null,72126,"Room humidity of unit 31","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[{"$nulls":3}," "]
[null,36064,null,72128,"Supply temperature of unit 0","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36065,null,72130,"Supply temperature of unit 1","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36066,null,72132,"Supply temperature of unit 2","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36067,null,72134,"Supply temperature of unit 3","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36068,null,72136,"Supply temperature of unit 4","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36069,null,72138,"Supply temperature of unit 5","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36070,null,72140,"Supply temperature of unit 6","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36071,null,72142,"Supply temperature of unit 7","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36072,null,72144,"Supply temperature of unit 8","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36073,null,72146,"Supply temperature of unit 9","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36074,null,72148,"Supply temperature of unit 10","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36075,null,72150,"Supply temperature of unit 11","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36076,null,72152,"Supply temperature of unit 12","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36077,null,72154,"Supply temperature of unit 13","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36078,null,72156,"Supply temperature of unit 14","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36079,null,72158,"Supply temperature of unit 15","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36080,null,72160,"Supply temperature of unit 16","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36081,null,72162,"Supply temperature of unit 17","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36082,null,72164,"Supply temperature of unit 18","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36083,null,72166,"Supply temperature of unit 19","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36084,null,72168,"Supply temperature of unit 20","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36085,null,72170,"Supply temperature of unit 21","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36086,null,72172,"Supply temperature of unit 22","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36087,null,72174,"Supply temperature of unit 23","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36088,null,72176,"Supply temperature of unit 24","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36089,null,72178,"Supply temperature of unit 25","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36090,null,72180,"Supply temperature of unit 26","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36091,null,72182,"Supply temperature of unit 27","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36092,null,72184,"Supply temperature of unit 28","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36093,null,72186,"Supply temperature of unit 29","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36094,null,72188,"Supply temperature of unit 30","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[null,36095,null,72190,"Supply temperature of unit 31","internal","word",null,"-1000..1000","-100,0..100,0°C","r","r"]
[{"$nulls":3}," "]
[null,36096,null,72192,"Supply humidity of unit 0","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36097,null,72194,"Supply humidity of unit 1","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36098,null,72196,"Supply humidity of unit 2","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36099,null,72198,"Supply humidity of unit 3","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36100,null,72200,"Supply humidity of unit 4","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36101,null,72202,"Supply humidity of unit 5","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36102,null,72204,"Supply humidity of unit 6","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36103,null,72206,"Supply humidity of unit 7","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36104,null,72208,"Supply humidity of unit 8","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36105,null,72210,"Supply humidity of unit 9","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36106,null,72212,"Supply humidity of unit 10","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36107,null,72214,"Supply humidity of unit 11","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36108,null,72216,"Supply humidity of unit 12","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36109,null,72218,"Supply humidity of unit 13","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36110,null,72220,"Supply humidity of unit 14","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36111,null,72222,"Supply humidity of unit 15","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36112,null,72224,"Supply humidity of unit 16","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36113,null,72226,"Supply humidity of unit 17","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36114,null,72228,"Supply humidity of unit 18","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36115,null,72230,"Supply humidity of unit 19","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36116,null,72232,"Supply humidity of unit 20","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36117,null,72234,"Supply humidity of unit 21","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36118,null,72236,"Supply humidity of unit 22","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36119,null,72238,"Supply humidity of unit 23","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36120,null,72240,"Supply humidity of unit 24","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36121,null,72242,"Supply humidity of unit 25","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36122,null,72244,"Supply humidity of unit 26","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36123,null,72246,"Supply humidity of unit 27","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36124,null,72248,"Supply humidity of unit 28","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36125,null,72250,"Supply humidity of unit 29","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36126,null,72252,"Supply humidity of unit 30","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[null,36127,null,72254,"Supply humidity of unit 31","internal","word",null,"0..1000","0,0..100,0%rF","r","r"]
[{"$nulls":3}," "]
[null,36128,null,72256,"Overload switch of unit 0","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36129,null,72258,"Overload switch of unit 1","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36130,null,72260,"Overload switch of unit 2","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36131,null,72262,"Overload switch of unit 3","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36132,null,72264,"Overload switch of unit 4","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36133,null,72266,"Overload switch of unit 5","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36134,null,72268,"Overload switch of unit 6","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36135,null,72270,"Overload switch of unit 7","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36136,null,72272,"Overload switch of unit 8","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36137,null,72274,"Overload switch of unit 9","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36138,null,72276,"Overload switch of unit 10","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36139,null,72278,"Overload switch of unit 11","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36140,null,72280,"Overload switch of unit 12","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36141,null,72282,"Overload switch of unit 13","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36142,null,72284,"Overload switch of unit 14","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36143,null,72286,"Overload switch of unit 15","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36144,null,72288,"Overload switch of unit 16","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36145,null,72290,"Overload switch of unit 17","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36146,null,72292,"Overload switch of unit 18","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36147,null,72294,"Overload switch of unit 19","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36148,null,72296,"Overload switch of unit 20","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36149,null,72298,"Overload switch of unit 21","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36150,null,72300,"Overload switch of unit 22","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36151,null,72302,"Overload switch of unit 23","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36152,null,72304,"Overload switch of unit 24","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36153,null,72306,"Overload switch of unit 25","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36154,null,72308,"Overload switch of unit 26","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36155,null,72310,"Overload switch of unit 27","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36156,null,72312,"Overload switch of unit 28","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36157,null,72314,"Overload switch of unit 29","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36158,null,72316,"Overload switch of unit 30","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[null,36159,null,72318,"Overload switch of unit 31","internal","SI16",null,"0..99","0,0..9,9K","r","r"]
[{"$nulls":3}," "]
[null,36160,null,72320,"Zone state of unit 0","internal","UI8",null,"0-255",null,"r","r"]
[null,36161,null,72322,"Zone state of unit 1","internal","UI8",null,"0-255",null,"r","r"]
[null,36162,null,72324,"Zone state of unit 2","internal","UI8",null,"0-255",null,"r","r"]
[null,36163,null,72326,"Zone state of unit 3","internal","UI8",null,"0-255",null,"r","r"]
[null,36164,null,72328,"Zone state of unit 4","internal","UI8",null,"0-255",null,"r","r"]
[null,36165,null,72330,"Zone state of unit 5","internal","UI8",null,"0-255",null,"r","r"]
[null,36166,null,72332,"Zone state of unit 6","internal","UI8",null,"0-255",null,"r","r"]
[null,36167,null,72334,"Zone state of unit 7","internal","UI8",null,"0-255",null,"r","r"]
[null,36168,null,72336,"Zone state of unit 8","internal","UI8",null,"0-255",null,"r","r"]
[null,36169,null,72338,"Zone state of unit 9","internal","UI8",null,"0-255",null,"r","r"]
[null,36170,null,72340,"Zone state of unit 10","internal","UI8",null,"0-255",null,"r","r"]
[null,36171,null,72342,"Zone state of unit 11","internal","UI8",null,"0-255",null,"r","r"]
[null,36172,null,72344,"Zone state of unit 12","internal","UI8",null,"0-255",null,"r","r"]
[null,36173,null,72346,"Zone state of unit 13","internal","UI8",null,"0-255",null,"r","r"]
[null,36174,null,72348,"Zone state of unit 14","internal","UI8",null,"0-255",null,"r","r"]
[null,36175,null,72350,"Zone state of unit 15","internal","UI8",null,"0-255",null,"r","r"]
[null,36176,null,72352,"Zone state of unit 16","internal","UI8",null,"0-255",null,"r","r"]
[null,36177,null,72354,"Zone state of unit 17","internal","UI8",null,"0-255",null,"r","r"]
[null,36178,null,72356,"Zone state of unit 18","internal","UI8",null,"0-255",null,"r","r"]
[null,36179,null,72358,"Zone state of unit 19","internal","UI8",null,"0-255",null,"r","r"]
[null,36180,null,72360,"Zone state of unit 20","internal","UI8",null,"0-255",null,"r","r"]
[null,36181,null,72362,"Zone state of unit 21","internal","UI8",null,"0-255",null,"r","r"]
[null,36182,null,72364,"Zone state of unit 22","internal","UI8",null,"0-255",null,"r","r"]
[null,36183,null,72366,"Zone state of unit 23","internal","UI8",null,"0-255",null,"r","r"]
[null,36184,null,72368,"Zone state of unit 24","internal","UI8",null,"0-255",null,"r","r"]
[null,36185,null,72370,"Zone state of unit 25","internal","UI8",null,"0-255",null,"r","r"]
[null,36186,null,72372,"Zone state of unit 26","internal","UI8",null,"0-255",null,"r","r"]
[null,36187,null,72374,"Zone state of unit 27","internal","UI8",null,"0-255",null,"r","r"]
[null,36188,null,72376,"Zone state of unit 28","internal","UI8",null,"0-255",null,"r","r"]
[null,36189,null,72378,"Zone state of unit 29","internal","UI8",null,"0-255",null,"r","r"]
[null,36190,null,72380,"Zone state of unit 30","internal","UI8",null,"0-255",null,"r","r"]
[null,36191,null,72382,"Zone state of unit 31","internal","UI8",null,"0-255",null,"r","r"]
[{"$nulls":3}," "]
[null,36192,null,72384,"Alarm of unit 0","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36193,null,72386,"Alarm of unit 1","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36194,null,72388,"Alarm of unit 2","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36195,null,72390,"Alarm of unit 3","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36196,null,72392,"Alarm of unit 4","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36197,null,72394,"Alarm of unit 5","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36198,null,72396,"Alarm of unit 6","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36199,null,72398,"Alarm of unit 7","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36200,null,72400,"Alarm of unit 8","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36201,null,72402,"Alarm of unit 9","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36202,null,72404,"Alarm of unit 10","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36203,null,72406,"Alarm of unit 11","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36204,null,72408,"Alarm of unit 12","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36205,null,72410,"Alarm of unit 13","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36206,null,72412,"Alarm of unit 14","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36207,null,72414,"Alarm of unit 15","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36208,null,72416,"Alarm of unit 16","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36209,null,72418,"Alarm of unit 17","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36210,null,72420,"Alarm of unit 18","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36211,null,72422,"Alarm of unit 19","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36212,null,72424,"Alarm of unit 20","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36213,null,72426,"Alarm of unit 21","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36214,null,72428,"Alarm of unit 22","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36215,null,72430,"Alarm of unit 23","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36216,null,72432,"Alarm of unit 24","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36217,null,72434,"Alarm of unit 25","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36218,null,72436,"Alarm of unit 26","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36219,null,72438,"Alarm of unit 27","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36220,null,72440,"Alarm of unit 28","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36221,null,72442,"Alarm of unit 29","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36222,null,72444,"Alarm of unit 30","internal","BIT1",null,"0, 1",null,"r","r"]
[null,36223,null,72446,"Alarm of unit 31","internal","BIT1",null,"0, 1",null,"r","r"]
[]
[]
[]
["userdefinable areas of datapoints (definition)",{"$nulls":11},"redirected DP-adr. For TCT:"]
[null,63488,null,63488,"UDDP-conf Bit000","internal link","bit",null,"0, 1",{"$nulls":3},4803]
[null,63489,null,63489,"UDDP-conf Bit001","internal link","bit",null,"0, 1",{"$nulls":3},4403]
[null,63490,null,63490,"UDDP-conf Bit002","internal link","bit",null,"0, 1",{"$nulls":3},6402]
[null,63491,null,63491,"UDDP-conf Bit003","internal link","bit",null,"0, 1",{"$nulls":3},6802]
[null,63492,null,63492,"UDDP-conf Bit004","internal link","bit",null,"0, 1",{"$nulls":3},6902]
[null,63493,null,63493,"UDDP-conf Bit005","internal link","bit",null,"0, 1",{"$nulls":3},5403]
[null,63494,null,63494,"UDDP-conf Bit006","internal link","bit",null,"0, 1",{"$nulls":3},"6202, 5003, 6302"]
[null,63495,null,63495,"UDDP-conf Bit007","internal link","bit",null,"0, 1",{"$nulls":3},4903]
[null,63496,null,63496,"UDDP-conf Bit008","internal link","bit",null,"0, 1",{"$nulls":3},7202]
[null,63497,null,63497,"UDDP-conf Bit009","internal link","bit",null,"0, 1",{"$nulls":3},4405]
[null,63498,null,63498,"UDDP-conf Bit010","internal link","bit",null,"0, 1",{"$nulls":3},4404]
[null,63499,null,63499,"UDDP-conf Bit011","internal link","bit",null,"0, 1",{"$nulls":3},4802]
[null,63500,null,63500,"UDDP-conf Bit012","internal link","bit",null,"0, 1",{"$nulls":3},6403]
[null,63501,null,63501,"UDDP-conf Bit013","internal link","bit",null,"0, 1",{"$nulls":3},6903]
[null,63502,null,63502,"UDDP-conf Bit014","internal link","bit",null,"0, 1",{"$nulls":3},6904]
[null,63503,null,63503,"UDDP-conf Bit015","internal link","bit",null,"0, 1",{"$nulls":3},7502]
[null,63504,null,63504,"UDDP-conf Bit016","internal link","bit",null,"0, 1",{"$nulls":3},4902]
[null,63505,null,63505,"UDDP-conf Bit017","internal link","bit",null,"0, 1",{"$nulls":3},6409]
[null,63506,null,63506,"UDDP-conf Bit018","internal link","bit",null,"0, 1",{"$nulls":3},6403]
[null,63507,null,63507,"UDDP-conf Bit019","internal link","bit",null,"0, 1",{"$nulls":3},5403]
[null,63508,null,63508,"UDDP-conf Bit020","internal link","bit",null,"0, 1",{"$nulls":3},2206]
[null,63509,null,63509,"UDDP-conf Bit021","internal link","bit",null,"0, 1",{"$nulls":3},7602]
[null,63510,null,63510,"UDDP-conf Bit022","internal link","bit",null,"0, 1",{"$nulls":3},7702]
[null,63511,null,63511,"UDDP-conf Bit023","internal link","bit",null,"0, 1",{"$nulls":3},4503]
[null,63512,null,63512,"UDDP-conf Bit024","internal link","bit",null,"0, 1",{"$nulls":3},4505]
[null,63513,null,63513,"UDDP-conf Bit025","internal link","bit",null,"0, 1",{"$nulls":3},4504]
[null,63514,null,63514,"UDDP-conf Bit026","internal link","bit",null,"0, 1",{"$nulls":3},1000]
[null,63515,null,63515,"UDDP-conf Bit027","internal link","bit",null,"0, 1",{"$nulls":3},1001]
[null,63516,null,63516,"UDDP-conf Bit028","internal link","bit",null,"0, 1",{"$nulls":3},1002]
[null,63517,null,63517,"UDDP-conf Bit029","internal link","bit",null,"0, 1",{"$nulls":3},1003]
[null,63518,null,63518,"UDDP-conf Bit030","internal link","bit",null,"0, 1",{"$nulls":3},1004]
[null,63519,null,63519,"UDDP-conf Bit031","internal link","bit",null,"0, 1",{"$nulls":3},1006]
[null,63520,null,63520,"UDDP-conf Bit032","internal link","bit",null,"0, 1",{"$nulls":3},1007]
[null,63521,null,63521,"UDDP-conf Bit033","internal link","bit",null,"0, 1",{"$nulls":3},1008]
[null,63522,null,63522,"UDDP-conf Bit034","internal link","bit",null,"0, 1",{"$nulls":3},2216]
[null,63523,null,63523,"UDDP-conf Bit035","internal link","bit",null,"0, 1",{"$nulls":3},2217]
[null,63524,null,63524,"UDDP-conf Bit036","internal link","bit",null,"0, 1",{"$nulls":3},2218]
[null,63525,null,63525,"UDDP-conf Bit037","internal link","bit",null,"0, 1",{"$nulls":3},2219]
[null,63526,null,63526,"UDDP-conf Bit038","internal link","bit",null,"0, 1",{"$nulls":3},2220]
[null,63527,null,63527,"UDDP-conf Bit039","internal link","bit",null,"0, 1",{"$nulls":3},2221]
[null,63528,null,63528,"UDDP-conf Bit040","internal link","bit",null,"0, 1",{"$nulls":3},2222]
[null,63529,null,63529,"UDDP-conf Bit041","internal link","bit",null,"0, 1",{"$nulls":3},2223]
[null,63530,null,63530,"UDDP-conf Bit042","internal link","bit",null,"0, 1",{"$nulls":3},2224]
[null,63531,null,63531,"UDDP-conf Bit043","internal link","bit",null,"0, 1",{"$nulls":3},2225]
[null,63532,null,63532,"UDDP-conf Bit044","internal link","bit",null,"0, 1",{"$nulls":3},2208]
[null,63533,null,63533,"UDDP-conf Bit045","internal link","bit",null,"0, 1",{"$nulls":3},4800]
[null,63534,null,63534,"UDDP-conf Bit046","internal link","bit",null,"0, 1",{"$nulls":3},4900]
[null,63535,null,63535,"UDDP-conf Bit047","internal link","bit",null,"0, 1",{"$nulls":3},"6200, 5000, 6300"]
[null,63536,null,63536,"UDDP-conf Bit048","internal link","bit",null,"0, 1",{"$nulls":3},5400]
[null,63537,null,63537,"UDDP-conf Bit049","internal link","bit",null,"0, 1",{"$nulls":3},4400]
[null,63538,null,63538,"UDDP-conf Bit050","internal link","bit",null,"0, 1",{"$nulls":3},6800]
[null,63539,null,63539,"UDDP-conf Bit051","internal link","bit",null,"0, 1",{"$nulls":3},6400]
[null,63540,null,63540,"UDDP-conf Bit052","internal link","bit",null,"0, 1",{"$nulls":3},5200]
[null,63541,null,63541,"UDDP-conf Bit053","internal link","bit",null,"0, 1",{"$nulls":3},4500]
[null,63542,null,63542,"UDDP-conf Bit054","internal link","bit",null,"0, 1"]
[null,63543,null,63543,"UDDP-conf Bit055","internal link","bit",null,"0, 1"]
[null,63544,null,63544,"UDDP-conf Bit056","internal link","bit",null,"0, 1"]
[null,63545,null,63545,"UDDP-conf Bit057","internal link","bit",null,"0, 1"]
[null,63546,null,63546,"UDDP-conf Bit058","internal link","bit",null,"0, 1"]
[null,63547,null,63547,"UDDP-conf Bit059","internal link","bit",null,"0, 1"]
[null,63548,null,63548,"UDDP-conf Bit060","internal link","bit",null,"0, 1"]
[null,63549,null,63549,"UDDP-conf Bit061","internal link","bit",null,"0, 1"]
[null,63550,null,63550,"UDDP-conf Bit062","internal link","bit",null,"0, 1"]
[null,63551,null,63551,"UDDP-conf Bit063","internal link","bit",null,"0, 1"]
[null,63552,null,63552,"UDDP-conf Bit064","internal link","bit",null,"0, 1"]
[null,63553,null,63553,"UDDP-conf Bit065","internal link","bit",null,"0, 1"]
[null,63554,null,63554,"UDDP-conf Bit066","internal link","bit",null,"0, 1"]
[null,63555,null,63555,"UDDP-conf Bit067","internal link","bit",null,"0, 1"]
[null,63556,null,63556,"UDDP-conf Bit068","internal link","bit",null,"0, 1"]
[null,63557,null,63557,"UDDP-conf Bit069","internal link","bit",null,"0, 1"]
[null,63558,null,63558,"UDDP-conf Bit070","internal link","bit",null,"0, 1"]
[null,63559,null,63559,"UDDP-conf Bit071","internal link","bit",null,"0, 1"]
[null,63560,null,63560,"UDDP-conf Bit072","internal link","bit",null,"0, 1"]
[null,63561,null,63561,"UDDP-conf Bit073","internal link","bit",null,"0, 1"]
[null,63562,null,63562,"UDDP-conf Bit074","internal link","bit",null,"0, 1"]
[null,63563,null,63563,"UDDP-conf Bit075","internal link","bit",null,"0, 1"]
[null,63564,null,63564,"UDDP-conf Bit076","internal link","bit",null,"0, 1"]
[null,63565,null,63565,"UDDP-conf Bit077","internal link","bit",null,"0, 1"]
[null,63566,null,63566,"UDDP-conf Bit078","internal link","bit",null,"0, 1"]
[null,63567,null,63567,"UDDP-conf Bit079","internal link","bit",null,"0, 1"]
[null,63568,null,63568,"UDDP-conf Bit080","internal link","bit",null,"0, 1"]
[null,63569,null,63569,"UDDP-conf Bit081","internal link","bit",null,"0, 1"]
[null,63570,null,63570,"UDDP-conf Bit082","internal link","bit",null,"0, 1"]
[null,63571,null,63571,"UDDP-conf Bit083","internal link","bit",null,"0, 1"]
[null,63572,null,63572,"UDDP-conf Bit084","internal link","bit",null,"0, 1"]
[null,63573,null,63573,"UDDP-conf Bit085","internal link","bit",null,"0, 1"]
[null,63574,null,63574,"UDDP-conf Bit086","internal link","bit",null,"0, 1"]
[null,63575,null,63575,"UDDP-conf Bit087","internal link","bit",null,"0, 1"]
[null,63576,null,63576,"UDDP-conf Bit088","internal link","bit",null,"0, 1"]
[null,63577,null,63577,"UDDP-conf Bit089","internal link","bit",null,"0, 1"]
[null,63578,null,63578,"UDDP-conf Bit090","internal link","bit",null,"0, 1"]
[null,63579,null,63579,"UDDP-conf Bit091","internal link","bit",null,"0, 1"]
[null,63580,null,63580,"UDDP-conf Bit092","internal link","bit",null,"0, 1"]
[null,63581,null,63581,"UDDP-conf Bit093","internal link","bit",null,"0, 1"]
[null,63582,null,63582,"UDDP-conf Bit094","internal link","bit",null,"0, 1"]
[null,63583,null,63583,"UDDP-conf Bit095","internal link","bit",null,"0, 1"]
[null,63584,null,63584,"UDDP-conf Bit096","internal link","bit",null,"0, 1"]
[null,63585,null,63585,"UDDP-conf Bit097","internal link","bit",null,"0, 1"]
[null,63586,null,63586,"UDDP-conf Bit098","internal link","bit",null,"0, 1"]
[null,63587,null,63587,"UDDP-conf Bit099","internal link","bit",null,"0, 1"]
[null,63588,null,63588,"UDDP-conf Bit100","internal link","bit",null,"0, 1"]
[null,63589,null,63589,"UDDP-conf Bit101","internal link","bit",null,"0, 1"]
[null,63590,null,63590,"UDDP-conf Bit102","internal link","bit",null,"0, 1"]
[null,63591,null,63591,"UDDP-conf Bit103","internal link","bit",null,"0, 1"]
[null,63592,null,63592,"UDDP-conf Bit104","internal link","bit",null,"0, 1"]
[null,63593,null,63593,"UDDP-conf Bit105","internal link","bit",null,"0, 1"]
[null,63594,null,63594,"UDDP-conf Bit106","internal link","bit",null,"0, 1"]
[null,63595,null,63595,"UDDP-conf Bit107","internal link","bit",null,"0, 1"]
[null,63596,null,63596,"UDDP-conf Bit108","internal link","bit",null,"0, 1"]
[null,63597,null,63597,"UDDP-conf Bit109","internal link","bit",null,"0, 1"]
[null,63598,null,63598,"UDDP-conf Bit110","internal link","bit",null,"0, 1"]
[null,63599,null,63599,"UDDP-conf Bit111","internal link","bit",null,"0, 1"]
[null,63600,null,63600,"UDDP-conf Bit112","internal link","bit",null,"0, 1"]
[null,63601,null,63601,"UDDP-conf Bit113","internal link","bit",null,"0, 1"]
[null,63602,null,63602,"UDDP-conf Bit114","internal link","bit",null,"0, 1"]
[null,63603,null,63603,"UDDP-conf Bit115","internal link","bit",null,"0, 1"]
[null,63604,null,63604,"UDDP-conf Bit116","internal link","bit",null,"0, 1"]
[null,63605,null,63605,"UDDP-conf Bit117","internal link","bit",null,"0, 1"]
[null,63606,null,63606,"UDDP-conf Bit118","internal link","bit",null,"0, 1"]
[null,63607,null,63607,"UDDP-conf Bit119","internal link","bit",null,"0, 1"]
[null,63608,null,63608,"UDDP-conf Bit120","internal link","bit",null,"0, 1"]
[null,63609,null,63609,"UDDP-conf Bit121","internal link","bit",null,"0, 1"]
[null,63610,null,63610,"UDDP-conf Bit122","internal link","bit",null,"0, 1"]
[null,63611,null,63611,"UDDP-conf Bit123","internal link","bit",null,"0, 1"]
[null,63612,null,63612,"UDDP-conf Bit124","internal link","bit",null,"0, 1"]
[null,63613,null,63613,"UDDP-conf Bit125","internal link","bit",null,"0, 1"]
[null,63614,null,63614,"UDDP-conf Bit126","internal link","bit",null,"0, 1"]
[null,63615,null,63615,"UDDP-conf Bit127","internal link","bit",null,"0, 1"]
[null,63616,null,127232,"UDDP-conf Byte000","internal link","UI8",null,"0..255",{"$nulls":3},5214]
[null,63617,null,127234,"UDDP-conf Byte001","internal link","UI8",null,"0..255",{"$nulls":3},6315]
[null,63618,null,127236,"UDDP-conf Byte002","internal link","UI8",null,"0..255",{"$nulls":3},6427]
[null,63619,null,127238,"UDDP-conf Byte003","internal link","UI8",null,"0..255",{"$nulls":3},4611]
[null,63620,null,127240,"UDDP-conf Byte004","internal link","UI8",null,"0..255",{"$nulls":3},6932]
[null,63621,null,127242,"UDDP-conf Byte005","internal link","UI8",null,"0..255",{"$nulls":3},1016]
[null,63622,null,127244,"UDDP-conf Byte006","internal link","UI8",null,"0..255",{"$nulls":3},1017]
[null,63623,null,127246,"UDDP-conf Byte007","internal link","UI8",null,"0..255",{"$nulls":3},1018]
[null,63624,null,127248,"UDDP-conf Byte008","internal link","UI8",null,"0..255",{"$nulls":3},1019]
[null,63625,null,127250,"UDDP-conf Byte009","internal link","UI8",null,"0..255",{"$nulls":3},1020]
[null,63626,null,127252,"UDDP-conf Byte010","internal link","UI8",null,"0..255"]
[null,63627,null,127254,"UDDP-conf Byte011","internal link","UI8",null,"0..255"]
[null,63628,null,127256,"UDDP-conf Byte012","internal link","UI8",null,"0..255"]
[null,63629,null,127258,"UDDP-conf Byte013","internal link","UI8",null,"0..255"]
[null,63630,null,127260,"UDDP-conf Byte014","internal link","UI8",null,"0..255"]
[null,63631,null,127262,"UDDP-conf Byte015","internal link","UI8",null,"0..255"]
[null,63632,null,127264,"UDDP-conf Byte016","internal link","UI8",null,"0..255"]
[null,63633,null,127266,"UDDP-conf Byte017","internal link","UI8",null,"0..255"]
[null,63634,null,127268,"UDDP-conf Byte018","internal link","UI8",null,"0..255"]
[null,63635,null,127270,"UDDP-conf Byte019","internal link","UI8",null,"0..255"]
[null,63636,null,127272,"UDDP-conf Byte020","internal link","UI8",null,"0..255"]
[null,63637,null,127274,"UDDP-conf Byte021","internal link","UI8",null,"0..255"]
[null,63638,null,127276,"UDDP-conf Byte022","internal link","UI8",null,"0..255"]
[null,63639,null,127278,"UDDP-conf Byte023","internal link","UI8",null,"0..255"]
[null,63640,null,127280,"UDDP-conf Byte024","internal link","UI8",null,"0..255"]
[null,63641,null,127282,"UDDP-conf Byte025","internal link","UI8",null,"0..255"]
[null,63642,null,127284,"UDDP-conf Byte026","internal link","UI8",null,"0..255"]
[null,63643,null,127286,"UDDP-conf Byte027","internal link","UI8",null,"0..255"]
[null,63644,null,127288,"UDDP-conf Byte028","internal link","UI8",null,"0..255"]
[null,63645,null,127290,"UDDP-conf Byte029","internal link","UI8",null,"0..255"]
[null,63646,null,127292,"UDDP-conf Byte030","internal link","UI8",null,"0..255"]
[null,63647,null,127294,"UDDP-conf Byte031","internal link","UI8",null,"0..255"]
[null,63648,null,127296,"UDDP-conf UINT000","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},1194]
[null,63649,null,127298,"UDDP-conf UINT001","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},1195]
[null,63650,null,127300,"UDDP-conf UINT002","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},1197]
[null,63651,null,127302,"UDDP-conf UINT003","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},3]
[null,63652,null,127304,"UDDP-conf UINT004","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},1176]
[null,63653,null,127306,"UDDP-conf UINT005","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},2245]
[null,63654,null,127308,"UDDP-conf UINT006","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},2246]
[null,63655,null,127310,"UDDP-conf UINT007","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},2247]
[null,63656,null,127312,"UDDP-conf UINT008","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},2248]
[null,63657,null,127314,"UDDP-conf UINT009","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},4417]
[null,63658,null,127316,"UDDP-conf UINT010","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},4609]
[null,63659,null,127318,"UDDP-conf UINT011","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},5211]
[null,63660,null,127320,"UDDP-conf UINT012","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},5209]
[null,63661,null,127322,"UDDP-conf UINT013","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},4810]
[null,63662,null,127324,"UDDP-conf UINT014","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},4910]
[null,63663,null,127326,"UDDP-conf UINT015","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},5010]
[null,63664,null,127328,"UDDP-conf UINT016","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},6312]
[null,63665,null,127330,"UDDP-conf UINT017","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},6811]
[null,63666,null,127332,"UDDP-conf UINT018","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},6419]
[null,63667,null,127334,"UDDP-conf UINT019","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},6420]
[null,63668,null,127336,"UDDP-conf UINT020","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},"?"]
[null,63669,null,127338,"UDDP-conf UINT021","internal link","UI16",null,"0..0xFFFF"]
[null,63670,null,127340,"UDDP-conf UINT022","internal link","UI16",null,"0..0xFFFF"]
[null,63671,null,127342,"UDDP-conf UINT023","internal link","UI16",null,"0..0xFFFF"]
[null,63672,null,127344,"UDDP-conf UINT024","internal link","UI16",null,"0..0xFFFF"]
[null,63673,null,127346,"UDDP-conf UINT025","internal link","UI16",null,"0..0xFFFF"]
[null,63674,null,127348,"UDDP-conf UINT026","internal link","UI16",null,"0..0xFFFF"]
[null,63675,null,127350,"UDDP-conf UINT027","internal link","UI16",null,"0..0xFFFF"]
[null,63676,null,127352,"UDDP-conf UINT028","internal link","UI16",null,"0..0xFFFF"]
[null,63677,null,127354,"UDDP-conf UINT029","internal link","UI16",null,"0..0xFFFF"]
[null,63678,null,127356,"UDDP-conf UINT030","internal link","UI16",null,"0..0xFFFF"]
[null,63679,null,127358,"UDDP-conf UINT031","internal link","UI16",null,"0..0xFFFF"]
[null,63680,null,127360,"UDDP-conf SINT000","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},1191]
[null,63681,null,127362,"UDDP-conf SINT001","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},1192]
[null,63682,null,127364,"UDDP-conf SINT002","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},1193]
[null,63683,null,127366,"UDDP-conf SINT003","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},1196]
[null,63684,null,127368,"UDDP-conf SINT004","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},1173]
[null,63685,null,127370,"UDDP-conf SINT005","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},2239]
[null,63686,null,127372,"UDDP-conf SINT006","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},2240]
[null,63687,null,127374,"UDDP-conf SINT007","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},2241]
[null,63688,null,127376,"UDDP-conf SINT008","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},2242]
[null,63689,null,127378,"UDDP-conf SINT009","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},2243]
[null,63690,null,127380,"UDDP-conf SINT010","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},2244]
[null,63691,null,127382,"UDDP-conf SINT011","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},4416]
[null,63692,null,127384,"UDDP-conf SINT012","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},4608]
[null,63693,null,127386,"UDDP-conf SINT013","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},5409]
[null,63694,null,127388,"UDDP-conf SINT014","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},"?"]
[null,63695,null,127390,"UDDP-conf SINT015","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},"?"]
[null,63696,null,127392,"UDDP-conf SINT016","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},5208]
[null,63697,null,127394,"UDDP-conf SINT017","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},4809]
[null,63698,null,127396,"UDDP-conf SINT018","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},4909]
[null,63699,null,127398,"UDDP-conf SINT019","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},5009]
[null,63700,null,127400,"UDDP-conf SINT020","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},6309]
[null,63701,null,127402,"UDDP-conf SINT021","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},6809]
[null,63702,null,127404,"UDDP-conf SINT022","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},6417]
[null,63703,null,127406,"UDDP-conf SINT023","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},6417]
[null,63704,null,127408,"UDDP-conf SINT024","internal link","SI16",null,"0..0xFFFF"]
[null,63705,null,127410,"UDDP-conf SINT025","internal link","SI16",null,"0..0xFFFF"]
[null,63706,null,127412,"UDDP-conf SINT026","internal link","SI16",null,"0..0xFFFF"]
[null,63707,null,127414,"UDDP-conf SINT027","internal link","SI16",null,"0..0xFFFF"]
[null,63708,null,127416,"UDDP-conf SINT028","internal link","SI16",null,"0..0xFFFF"]
[null,63709,null,127418,"UDDP-conf SINT029","internal link","SI16",null,"0..0xFFFF"]
[null,63710,null,127420,"UDDP-conf SINT030","internal link","SI16",null,"0..0xFFFF"]
[null,63711,null,127422,"UDDP-conf SINT031","internal link","SI16",null,"0..0xFFFF"]
[null,63712,null,127424,"UDDP-conf ULONG000","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63713,null,127426,"UDDP-conf ULONG001","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63714,null,127428,"UDDP-conf ULONG002","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63715,null,127430,"UDDP-conf ULONG003","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63716,null,127432,"UDDP-conf ULONG004","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63717,null,127434,"UDDP-conf ULONG005","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63718,null,127436,"UDDP-conf ULONG006","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63719,null,127438,"UDDP-conf ULONG007","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63720,null,127440,"UDDP-conf ULONG008","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63721,null,127442,"UDDP-conf ULONG009","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63722,null,127444,"UDDP-conf ULONG010","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63723,null,127446,"UDDP-conf ULONG011","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63724,null,127448,"UDDP-conf ULONG012","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63725,null,127450,"UDDP-conf ULONG013","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63726,null,127452,"UDDP-conf ULONG014","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63727,null,127454,"UDDP-conf ULONG015","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63728,null,127456,"UDDP-conf ULONG016","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63729,null,127458,"UDDP-conf ULONG017","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63730,null,127460,"UDDP-conf ULONG018","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63731,null,127462,"UDDP-conf ULONG019","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63732,null,127464,"UDDP-conf ULONG020","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63733,null,127466,"UDDP-conf ULONG021","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63734,null,127468,"UDDP-conf ULONG022","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63735,null,127470,"UDDP-conf ULONG023","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63736,null,127472,"UDDP-conf ULONG024","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63737,null,127474,"UDDP-conf ULONG025","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63738,null,127476,"UDDP-conf ULONG026","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63739,null,127478,"UDDP-conf ULONG027","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63740,null,127480,"UDDP-conf ULONG028","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63741,null,127482,"UDDP-conf ULONG029","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63742,null,127484,"UDDP-conf ULONG030","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,63743,null,127486,"UDDP-conf ULONG031","internal link","UI32",null,"0..0xFFFFFFFF"]
{"$rows_empty":7}
["userdefinable areas of datapoints (definition)",{"$nulls":11},"redirected DP-adr. For TCT:"]
[null,64512,null,64512,"UDDP Bit000",null,"bit",null,"0, 1",{"$nulls":3},4803]
[null,64513,null,64513,"UDDP Bit001",null,"bit",null,"0, 1",{"$nulls":3},4403]
[null,64514,null,64514,"UDDP Bit002",null,"bit",null,"0, 1",{"$nulls":3},6402]
[null,64515,null,64515,"UDDP Bit003",null,"bit",null,"0, 1",{"$nulls":3},6802]
[null,64516,null,64516,"UDDP Bit004",null,"bit",null,"0, 1",{"$nulls":3},6902]
[null,64517,null,64517,"UDDP Bit005","internal link","bit",null,"0, 1",{"$nulls":3},5403]
[null,64518,null,64518,"UDDP Bit006","internal link","bit",null,"0, 1",{"$nulls":3},"6202, 5003, 6302"]
[null,64519,null,64519,"UDDP Bit007","internal link","bit",null,"0, 1",{"$nulls":3},4903]
[null,64520,null,64520,"UDDP Bit008","internal link","bit",null,"0, 1",{"$nulls":3},7202]
[null,64521,null,64521,"UDDP Bit009","internal link","bit",null,"0, 1",{"$nulls":3},4405]
[null,64522,null,64522,"UDDP Bit010","internal link","bit",null,"0, 1",{"$nulls":3},4404]
[null,64523,null,64523,"UDDP Bit011","internal link","bit",null,"0, 1",{"$nulls":3},4802]
[null,64524,null,64524,"UDDP Bit012","internal link","bit",null,"0, 1",{"$nulls":3},6403]
[null,64525,null,64525,"UDDP Bit013","internal link","bit",null,"0, 1",{"$nulls":3},6903]
[null,64526,null,64526,"UDDP Bit014","internal link","bit",null,"0, 1",{"$nulls":3},6904]
[null,64527,null,64527,"UDDP Bit015","internal link","bit",null,"0, 1",{"$nulls":3},7502]
[null,64528,null,64528,"UDDP Bit016","internal link","bit",null,"0, 1",{"$nulls":3},4902]
[null,64529,null,64529,"UDDP Bit017","internal link","bit",null,"0, 1",{"$nulls":3},6409]
[null,64530,null,64530,"UDDP Bit018","internal link","bit",null,"0, 1",{"$nulls":3},6403]
[null,64531,null,64531,"UDDP Bit019","internal link","bit",null,"0, 1",{"$nulls":3},5403]
[null,64532,null,64532,"UDDP Bit020","internal link","bit",null,"0, 1",{"$nulls":3},2206]
[null,64533,null,64533,"UDDP Bit021","internal link","bit",null,"0, 1",{"$nulls":3},7602]
[null,64534,null,64534,"UDDP Bit022","internal link","bit",null,"0, 1",{"$nulls":3},7702]
[null,64535,null,64535,"UDDP Bit023","internal link","bit",null,"0, 1",{"$nulls":3},4503]
[null,64536,null,64536,"UDDP Bit024","internal link","bit",null,"0, 1",{"$nulls":3},4505]
[null,64537,null,64537,"UDDP Bit025","internal link","bit",null,"0, 1",{"$nulls":3},4504]
[null,64538,null,64538,"UDDP Bit026","internal link","bit",null,"0, 1",{"$nulls":3},1000]
[null,64539,null,64539,"UDDP Bit027","internal link","bit",null,"0, 1",{"$nulls":3},1001]
[null,64540,null,64540,"UDDP Bit028","internal link","bit",null,"0, 1",{"$nulls":3},1002]
[null,64541,null,64541,"UDDP Bit029","internal link","bit",null,"0, 1",{"$nulls":3},1003]
[null,64542,null,64542,"UDDP Bit030","internal link","bit",null,"0, 1",{"$nulls":3},1004]
[null,64543,null,64543,"UDDP Bit031","internal link","bit",null,"0, 1",{"$nulls":3},1006]
[null,64544,null,64544,"UDDP Bit032","internal link","bit",null,"0, 1",{"$nulls":3},1007]
[null,64545,null,64545,"UDDP Bit033","internal link","bit",null,"0, 1",{"$nulls":3},1008]
[null,64546,null,64546,"UDDP Bit034","internal link","bit",null,"0, 1",{"$nulls":3},2216]
[null,64547,null,64547,"UDDP Bit035","internal link","bit",null,"0, 1",{"$nulls":3},2217]
[null,64548,null,64548,"UDDP Bit036","internal link","bit",null,"0, 1",{"$nulls":3},2218]
[null,64549,null,64549,"UDDP Bit037","internal link","bit",null,"0, 1",{"$nulls":3},2219]
[null,64550,null,64550,"UDDP Bit038","internal link","bit",null,"0, 1",{"$nulls":3},2220]
[null,64551,null,64551,"UDDP Bit039","internal link","bit",null,"0, 1",{"$nulls":3},2221]
[null,64552,null,64552,"UDDP Bit040","internal link","bit",null,"0, 1",{"$nulls":3},2222]
[null,64553,null,64553,"UDDP Bit041","internal link","bit",null,"0, 1",{"$nulls":3},2223]
[null,64554,null,64554,"UDDP Bit042","internal link","bit",null,"0, 1",{"$nulls":3},2224]
[null,64555,null,64555,"UDDP Bit043","internal link","bit",null,"0, 1",{"$nulls":3},2225]
[null,64556,null,64556,"UDDP Bit044","internal link","bit",null,"0, 1",{"$nulls":3},2208]
[null,64557,null,64557,"UDDP Bit045","internal link","bit",null,"0, 1",{"$nulls":3},4800]
[null,64558,null,64558,"UDDP Bit046","internal link","bit",null,"0, 1",{"$nulls":3},4900]
[null,64559,null,64559,"UDDP Bit047","internal link","bit",null,"0, 1",{"$nulls":3},"6200, 5000, 6300"]
[null,64560,null,64560,"UDDP Bit048","internal link","bit",null,"0, 1",{"$nulls":3},5400]
[null,64561,null,64561,"UDDP Bit049","internal link","bit",null,"0, 1",{"$nulls":3},4400]
[null,64562,null,64562,"UDDP Bit050","internal link","bit",null,"0, 1",{"$nulls":3},6800]
[null,64563,null,64563,"UDDP Bit051","internal link","bit",null,"0, 1",{"$nulls":3},6400]
[null,64564,null,64564,"UDDP Bit052","internal link","bit",null,"0, 1",{"$nulls":3},5200]
[null,64565,null,64565,"UDDP Bit053","internal link","bit",null,"0, 1",{"$nulls":3},4500]
[null,64566,null,64566,"UDDP Bit054","internal link","bit",null,"0, 1"]
[null,64567,null,64567,"UDDP Bit055","internal link","bit",null,"0, 1"]
[null,64568,null,64568,"UDDP Bit056","internal link","bit",null,"0, 1"]
[null,64569,null,64569,"UDDP Bit057","internal link","bit",null,"0, 1"]
[null,64570,null,64570,"UDDP Bit058","internal link","bit",null,"0, 1"]
[null,64571,null,64571,"UDDP Bit059","internal link","bit",null,"0, 1"]
[null,64572,null,64572,"UDDP Bit060","internal link","bit",null,"0, 1"]
[null,64573,null,64573,"UDDP Bit061","internal link","bit",null,"0, 1"]
[null,64574,null,64574,"UDDP Bit062","internal link","bit",null,"0, 1"]
[null,64575,null,64575,"UDDP Bit063","internal link","bit",null,"0, 1"]
[null,64576,null,64576,"UDDP Bit064","internal link","bit",null,"0, 1"]
[null,64577,null,64577,"UDDP Bit065","internal link","bit",null,"0, 1"]
[null,64578,null,64578,"UDDP Bit066","internal link","bit",null,"0, 1"]
[null,64579,null,64579,"UDDP Bit067","internal link","bit",null,"0, 1"]
[null,64580,null,64580,"UDDP Bit068","internal link","bit",null,"0, 1"]
[null,64581,null,64581,"UDDP Bit069","internal link","bit",null,"0, 1"]
[null,64582,null,64582,"UDDP Bit070","internal link","bit",null,"0, 1"]
[null,64583,null,64583,"UDDP Bit071","internal link","bit",null,"0, 1"]
[null,64584,null,64584,"UDDP Bit072","internal link","bit",null,"0, 1"]
[null,64585,null,64585,"UDDP Bit073","internal link","bit",null,"0, 1"]
[null,64586,null,64586,"UDDP Bit074","internal link","bit",null,"0, 1"]
[null,64587,null,64587,"UDDP Bit075","internal link","bit",null,"0, 1"]
[null,64588,null,64588,"UDDP Bit076","internal link","bit",null,"0, 1"]
[null,64589,null,64589,"UDDP Bit077","internal link","bit",null,"0, 1"]
[null,64590,null,64590,"UDDP Bit078","internal link","bit",null,"0, 1"]
[null,64591,null,64591,"UDDP Bit079","internal link","bit",null,"0, 1"]
[null,64592,null,64592,"UDDP Bit080","internal link","bit",null,"0, 1"]
[null,64593,null,64593,"UDDP Bit081","internal link","bit",null,"0, 1"]
[null,64594,null,64594,"UDDP Bit082","internal link","bit",null,"0, 1"]
[null,64595,null,64595,"UDDP Bit083","internal link","bit",null,"0, 1"]
[null,64596,null,64596,"UDDP Bit084","internal link","bit",null,"0, 1"]
[null,64597,null,64597,"UDDP Bit085","internal link","bit",null,"0, 1"]
[null,64598,null,64598,"UDDP Bit086","internal link","bit",null,"0, 1"]
[null,64599,null,64599,"UDDP Bit087","internal link","bit",null,"0, 1"]
[null,64600,null,64600,"UDDP Bit088","internal link","bit",null,"0, 1"]
[null,64601,null,64601,"UDDP Bit089","internal link","bit",null,"0, 1"]
[null,64602,null,64602,"UDDP Bit090","internal link","bit",null,"0, 1"]
[null,64603,null,64603,"UDDP Bit091","internal link","bit",null,"0, 1"]
[null,64604,null,64604,"UDDP Bit092","internal link","bit",null,"0, 1"]
[null,64605,null,64605,"UDDP Bit093","internal link","bit",null,"0, 1"]
[null,64606,null,64606,"UDDP Bit094","internal link","bit",null,"0, 1"]
[null,64607,null,64607,"UDDP Bit095","internal link","bit",null,"0, 1"]
[null,64608,null,64608,"UDDP Bit096","internal link","bit",null,"0, 1"]
[null,64609,null,64609,"UDDP Bit097","internal link","bit",null,"0, 1"]
[null,64610,null,64610,"UDDP Bit098","internal link","bit",null,"0, 1"]
[null,64611,null,64611,"UDDP Bit099","internal link","bit",null,"0, 1"]
[null,64612,null,64612,"UDDP Bit100","internal link","bit",null,"0, 1"]
[null,64613,null,64613,"UDDP Bit101","internal link","bit",null,"0, 1"]
[null,64614,null,64614,"UDDP Bit102","internal link","bit",null,"0, 1"]
[null,64615,null,64615,"UDDP Bit103","internal link","bit",null,"0, 1"]
[null,64616,null,64616,"UDDP Bit104","internal link","bit",null,"0, 1"]
[null,64617,null,64617,"UDDP Bit105","internal link","bit",null,"0, 1"]
[null,64618,null,64618,"UDDP Bit106","internal link","bit",null,"0, 1"]
[null,64619,null,64619,"UDDP Bit107","internal link","bit",null,"0, 1"]
[null,64620,null,64620,"UDDP Bit108","internal link","bit",null,"0, 1"]
[null,64621,null,64621,"UDDP Bit109","internal link","bit",null,"0, 1"]
[null,64622,null,64622,"UDDP Bit110","internal link","bit",null,"0, 1"]
[null,64623,null,64623,"UDDP Bit111","internal link","bit",null,"0, 1"]
[null,64624,null,64624,"UDDP Bit112","internal link","bit",null,"0, 1"]
[null,64625,null,64625,"UDDP Bit113","internal link","bit",null,"0, 1"]
[null,64626,null,64626,"UDDP Bit114","internal link","bit",null,"0, 1"]
[null,64627,null,64627,"UDDP Bit115","internal link","bit",null,"0, 1"]
[null,64628,null,64628,"UDDP Bit116","internal link","bit",null,"0, 1"]
[null,64629,null,64629,"UDDP Bit117","internal link","bit",null,"0, 1"]
[null,64630,null,64630,"UDDP Bit118","internal link","bit",null,"0, 1"]
[null,64631,null,64631,"UDDP Bit119","internal link","bit",null,"0, 1"]
[null,64632,null,64632,"UDDP Bit120","internal link","bit",null,"0, 1"]
[null,64633,null,64633,"UDDP Bit121","internal link","bit",null,"0, 1"]
[null,64634,null,64634,"UDDP Bit122","internal link","bit",null,"0, 1"]
[null,64635,null,64635,"UDDP Bit123","internal link","bit",null,"0, 1"]
[null,64636,null,64636,"UDDP Bit124","internal link","bit",null,"0, 1"]
[null,64637,null,64637,"UDDP Bit125","internal link","bit",null,"0, 1"]
[null,64638,null,64638,"UDDP Bit126","internal link","bit",null,"0, 1"]
[null,64639,null,64639,"UDDP Bit127","internal link","bit",null,"0, 1"]
[null,64640,null,129280,"UDDP Byte000","internal link","UI8",null,"0..255",{"$nulls":3},5214]
[null,64641,null,129282,"UDDP Byte001","internal link","UI8",null,"0..255",{"$nulls":3},6315]
[null,64642,null,129284,"UDDP Byte002","internal link","UI8",null,"0..255",{"$nulls":3},6427]
[null,64643,null,129286,"UDDP Byte003","internal link","UI8",null,"0..255",{"$nulls":3},4611]
[null,64644,null,129288,"UDDP Byte004","internal link","UI8",null,"0..255",{"$nulls":3},6932]
[null,64645,null,129290,"UDDP Byte005","internal link","UI8",null,"0..255",{"$nulls":3},1016]
[null,64646,null,129292,"UDDP Byte006","internal link","UI8",null,"0..255",{"$nulls":3},1017]
[null,64647,null,129294,"UDDP Byte007","internal link","UI8",null,"0..255",{"$nulls":3},1018]
[null,64648,null,129296,"UDDP Byte008","internal link","UI8",null,"0..255",{"$nulls":3},1019]
[null,64649,null,129298,"UDDP Byte009","internal link","UI8",null,"0..255",{"$nulls":3},1020]
[null,64650,null,129300,"UDDP Byte010","internal link","UI8",null,"0..255"]
[null,64651,null,129302,"UDDP Byte011","internal link","UI8",null,"0..255"]
[null,64652,null,129304,"UDDP Byte012","internal link","UI8",null,"0..255"]
[null,64653,null,129306,"UDDP Byte013","internal link","UI8",null,"0..255"]
[null,64654,null,129308,"UDDP Byte014","internal link","UI8",null,"0..255"]
[null,64655,null,129310,"UDDP Byte015","internal link","UI8",null,"0..255"]
[null,64656,null,129312,"UDDP Byte016","internal link","UI8",null,"0..255"]
[null,64657,null,129314,"UDDP Byte017","internal link","UI8",null,"0..255"]
[null,64658,null,129316,"UDDP Byte018","internal link","UI8",null,"0..255"]
[null,64659,null,129318,"UDDP Byte019","internal link","UI8",null,"0..255"]
[null,64660,null,129320,"UDDP Byte020","internal link","UI8",null,"0..255"]
[null,64661,null,129322,"UDDP Byte021","internal link","UI8",null,"0..255"]
[null,64662,null,129324,"UDDP Byte022","internal link","UI8",null,"0..255"]
[null,64663,null,129326,"UDDP Byte023","internal link","UI8",null,"0..255"]
[null,64664,null,129328,"UDDP Byte024","internal link","UI8",null,"0..255"]
[null,64665,null,129330,"UDDP Byte025","internal link","UI8",null,"0..255"]
[null,64666,null,129332,"UDDP Byte026","internal link","UI8",null,"0..255"]
[null,64667,null,129334,"UDDP Byte027","internal link","UI8",null,"0..255"]
[null,64668,null,129336,"UDDP Byte028","internal link","UI8",null,"0..255"]
[null,64669,null,129338,"UDDP Byte029","internal link","UI8",null,"0..255"]
[null,64670,null,129340,"UDDP Byte030","internal link","UI8",null,"0..255"]
[null,64671,null,129342,"UDDP Byte031","internal link","UI8",null,"0..255"]
[null,64672,null,129344,"UDDP UINT000","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},1194]
[null,64673,null,129346,"UDDP UINT001","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},1195]
[null,64674,null,129348,"UDDP UINT002","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},1197]
[null,64675,null,129350,"UDDP UINT003","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},3]
[null,64676,null,129352,"UDDP UINT004","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},1176]
[null,64677,null,129354,"UDDP UINT005","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},2245]
[null,64678,null,129356,"UDDP UINT006","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},2246]
[null,64679,null,129358,"UDDP UINT007","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},2247]
[null,64680,null,129360,"UDDP UINT008","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},2248]
[null,64681,null,129362,"UDDP UINT009","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},4417]
[null,64682,null,129364,"UDDP UINT010","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},4609]
[null,64683,null,129366,"UDDP UINT011","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},5211]
[null,64684,null,129368,"UDDP UINT012","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},5209]
[null,64685,null,129370,"UDDP UINT013","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},4810]
[null,64686,null,129372,"UDDP UINT014","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},4910]
[null,64687,null,129374,"UDDP UINT015","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},5010]
[null,64688,null,129376,"UDDP UINT016","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},6312]
[null,64689,null,129378,"UDDP UINT017","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},6811]
[null,64690,null,129380,"UDDP UINT018","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},6419]
[null,64691,null,129382,"UDDP UINT019","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},6420]
[null,64692,null,129384,"UDDP UINT020","internal link","UI16",null,"0..0xFFFF",{"$nulls":3},"?"]
[null,64693,null,129386,"UDDP UINT021","internal link","UI16",null,"0..0xFFFF"]
[null,64694,null,129388,"UDDP UINT022","internal link","UI16",null,"0..0xFFFF"]
[null,64695,null,129390,"UDDP UINT023","internal link","UI16",null,"0..0xFFFF"]
[null,64696,null,129392,"UDDP UINT024","internal link","UI16",null,"0..0xFFFF"]
[null,64697,null,129394,"UDDP UINT025","internal link","UI16",null,"0..0xFFFF"]
[null,64698,null,129396,"UDDP UINT026","internal link","UI16",null,"0..0xFFFF"]
[null,64699,null,129398,"UDDP UINT027","internal link","UI16",null,"0..0xFFFF"]
[null,64700,null,129400,"UDDP UINT028","internal link","UI16",null,"0..0xFFFF"]
[null,64701,null,129402,"UDDP UINT029","internal link","UI16",null,"0..0xFFFF"]
[null,64702,null,129404,"UDDP UINT030","internal link","UI16",null,"0..0xFFFF"]
[null,64703,null,129406,"UDDP UINT031","internal link","UI16",null,"0..0xFFFF"]
[null,64704,null,129408,"UDDP SINT000","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},1191]
[null,64705,null,129410,"UDDP SINT001","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},1192]
[null,64706,null,129412,"UDDP SINT002","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},1193]
[null,64707,null,129414,"UDDP SINT003","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},1196]
[null,64708,null,129416,"UDDP SINT004","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},1173]
[null,64709,null,129418,"UDDP SINT005","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},2239]
[null,64710,null,129420,"UDDP SINT006","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},2240]
[null,64711,null,129422,"UDDP SINT007","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},2241]
[null,64712,null,129424,"UDDP SINT008","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},2242]
[null,64713,null,129426,"UDDP SINT009","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},2243]
[null,64714,null,129428,"UDDP SINT010","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},2244]
[null,64715,null,129430,"UDDP SINT011","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},4416]
[null,64716,null,129432,"UDDP SINT012","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},4608]
[null,64717,null,129434,"UDDP SINT013","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},5409]
[null,64718,null,129436,"UDDP SINT014","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},"?"]
[null,64719,null,129438,"UDDP SINT015","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},"?"]
[null,64720,null,129440,"UDDP SINT016","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},5208]
[null,64721,null,129442,"UDDP SINT017","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},4809]
[null,64722,null,129444,"UDDP SINT018","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},4909]
[null,64723,null,129446,"UDDP SINT019","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},5009]
[null,64724,null,129448,"UDDP SINT020","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},6309]
[null,64725,null,129450,"UDDP SINT021","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},6809]
[null,64726,null,129452,"UDDP SINT022","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},6417]
[null,64727,null,129454,"UDDP SINT023","internal link","SI16",null,"0..0xFFFF",{"$nulls":3},6417]
[null,64728,null,129456,"UDDP SINT024","internal link","SI16",null,"0..0xFFFF"]
[null,64729,null,129458,"UDDP SINT025","internal link","SI16",null,"0..0xFFFF"]
[null,64730,null,129460,"UDDP SINT026","internal link","SI16",null,"0..0xFFFF"]
[null,64731,null,129462,"UDDP SINT027","internal link","SI16",null,"0..0xFFFF"]
[null,64732,null,129464,"UDDP SINT028","internal link","SI16",null,"0..0xFFFF"]
[null,64733,null,129466,"UDDP SINT029","internal link","SI16",null,"0..0xFFFF"]
[null,64734,null,129468,"UDDP SINT030","internal link","SI16",null,"0..0xFFFF"]
[null,64735,null,129470,"UDDP SINT031","internal link","SI16",null,"0..0xFFFF"]
[null,64736,null,129472,"UDDP ULONG000","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64737,null,129474,"UDDP ULONG001","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64738,null,129476,"UDDP ULONG002","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64739,null,129478,"UDDP ULONG003","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64740,null,129480,"UDDP ULONG004","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64741,null,129482,"UDDP ULONG005","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64742,null,129484,"UDDP ULONG006","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64743,null,129486,"UDDP ULONG007","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64744,null,129488,"UDDP ULONG008","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64745,null,129490,"UDDP ULONG009","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64746,null,129492,"UDDP ULONG010","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64747,null,129494,"UDDP ULONG011","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64748,null,129496,"UDDP ULONG012","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64749,null,129498,"UDDP ULONG013","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64750,null,129500,"UDDP ULONG014","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64751,null,129502,"UDDP ULONG015","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64752,null,129504,"UDDP ULONG016","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64753,null,129506,"UDDP ULONG017","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64754,null,129508,"UDDP ULONG018","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64755,null,129510,"UDDP ULONG019","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64756,null,129512,"UDDP ULONG020","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64757,null,129514,"UDDP ULONG021","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64758,null,129516,"UDDP ULONG022","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64759,null,129518,"UDDP ULONG023","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64760,null,129520,"UDDP ULONG024","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64761,null,129522,"UDDP ULONG025","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64762,null,129524,"UDDP ULONG026","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64763,null,129526,"UDDP ULONG027","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64764,null,129528,"UDDP ULONG028","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64765,null,129530,"UDDP ULONG029","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64766,null,129532,"UDDP ULONG030","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64767,null,129534,"UDDP ULONG031","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64761,null,129522,"UDDP ULONG025","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64762,null,129524,"UDDP ULONG026","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64763,null,129526,"UDDP ULONG027","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64764,null,129528,"UDDP ULONG028","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64765,null,129530,"UDDP ULONG029","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64766,null,129532,"UDDP ULONG030","internal link","UI32",null,"0..0xFFFFFFFF"]
[null,64767,null,129534,"UDDP ULONG031","internal link","UI32",null,"0..0xFFFFFFFF"]

{"sheet":"C7000AT","index":4,"n_rows":864,"n_cols":16,"rows_kept":864,"flags":["formulas_cached_only"]}
[{"$nulls":5},"input","word",null,null,"r","r","r",null,null,"r","r"]
[{"$nulls":5},"output","byte",null,null,"w","w","RTC",null,null,"w","w"]
[{"$nulls":5},"internal","bit",null,null,"rw","rw","rw",null,null,"rw","rw"]
[{"$nulls":6},"string",null,null,"--","--","--",null,null,"--","--"]
[{"$nulls":6},"float"]
[null,"DP-","( Bit-)sub-","MODBUS-","C7000AT",null,"data-",null,null,"bus-","BMS-","stored in"]
[null,"Adress","adress","Adresse","Description","source-type","type","allowed range","mapped meaning","access","access","nv-memory ?","comment","menus in AT","WIB Access","WIB am 01.03."]
[null,0," "]
[null,"...",null,null,"see combined list C7000 common"]
[null,999]
[]
[null,1000,0,null,"remote on/off","input","bit","--","--","--","--","--",null,"not available","--","--"]
[null,1001,0,null,"master reset in","output","bit",null,null,"r","r","--",null,"not available","r","r"]
[null,1002,0,null,"fire/smoke","input","bit",null,null,"r","r","--",null,"not available","r","r"]
[null,1003,0,{"$nulls":3},"bit"]
[null,1004,0,{"$nulls":3},"bit"]
[null,1005,0,{"$nulls":3},"bit"]
[null,1006,0,{"$nulls":3},"bit"]
[null,1007,0,{"$nulls":3},"bit"]
[null,1008]
[null,1009]
[null,1010]
[null,1011]
[null,1012]
[null,1013]
[null,1014," "]
[null,1015," "]
[null,1016," ",null,"AT year","internal","byte",null,null,"rw","r","RTC",null,"not available","rw","rw"]
[null,1017," ",null,"AT month","internal","byte",null,null,"rw","r","RTC",null,"not available","rw","rw"]
[null,1018," ",null,"AT day","internal","byte",null,null,"rw","r","RTC",null,"not available","rw","rw"]
[null,1019," ",null,"AT hour","internal","byte",null,null,"rw","r","RTC",null,"statusline","rw","rw"]
[null,1020," ",null,"AT minute","internal","byte",null,null,"rw","r","RTC",null,"statusline","rw","rw"]
[null,1021," ",null,"AT second","internal","byte",null,null,"rw","r","RTC",null,"not available","rw","rw"]
[null,1022,0,null,"AT temperature phys. Unit","internal","bit","0/1","Celsius/Fahrenheit","rw","r","rw",null,"not available","rw","rw"]
[null,1023,0,null,"AT date format","internal","bit","0/1","german/american","rw","r","rw",null,"not available","rw","rw"]
[null,1024,0,{"$nulls":3},"bit"]
[null,1025,0,{"$nulls":3},"bit"]
[null,1026,0,{"$nulls":3},"bit"]
[null,1027,0,{"$nulls":3},"bit"]
[null,1028,0,{"$nulls":3},"bit"]
[null,1029,0,{"$nulls":3},"bit"]
[null,1030," ",null,"AT service language","internal","byte",null,null,"r","r","rw",null,"system","r","r"]
[null,1031," ",null,"AT display language","internal","byte",null,null,"rw","r","rw",null,"system","rw","rw"]
[null,1032,0,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1033,1,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1034,2,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1035,3,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1036,4,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1037,5,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1038,6,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1039,7,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1040,0,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1041,1,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1042,2,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1043,3,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1044,4,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1045,5,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1046,6,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1047,7,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1048,0,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1049,1,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1050,2,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1051,3,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1052,4,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1053,5,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1054,6,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1055,7,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1056,0,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1057,1,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1058,2,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1059,3,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1060,4,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1061,5,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1062,6,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1063,7,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1064,0,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1065,1,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1066,2,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1067,3,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1068,4,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1069,5,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1070,6,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1071,7,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1072,0,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1073,1,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1074,2,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1075,3,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1076,4,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1077,5,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1078,6,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1079,7,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1080,0,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1081,1,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1082,2,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1083,3,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1084,4,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1085,5,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1086,6,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1087,7,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1088,0,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1089,1,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1090,2,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1091,3,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1092,4,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1093,5,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1094,6,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1095,7,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1096,0,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1097,1,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1098,2,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1099,3,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1100,4,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1101,5,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1102,6,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1103,7,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1104,0,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1105,1,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1106,2,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1107,3,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1108,4,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1109,5,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1110,6,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1111,7,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1112,0,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1113,1,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1114,2,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1115,3,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1116,4,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1117,5,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1118,6,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1119,7,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1120,0,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1121,1,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1122,2,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1123,3,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1124,4,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1125,5,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1126,6,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1127,7,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1128,0,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1129,1,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1130,2,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1131,3,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1132,4,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1133,5,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1134,6,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1135,7,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1136,0,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1137,1,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1138,2,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1139,3,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1140,4,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1141,5,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1142,6,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1143,7,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1144,0,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1145,1,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1146,2,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1147,3,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1148,4,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1149,5,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1150,6,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1151,7,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1152,0,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1153,1,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1154,2,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1155,3,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1156,4,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1157,5,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1158,6,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[null,1159,7,null,"AT firmware-options","internal","bit","0/1",null,"rw","r","rw",null,"system","rw"]
[]
[]
[null,1170,null,null,"buzzerActive","internal","bit","0/1",null,"--","--","--",null,"system"]
[null,1171,{"$nulls":4},"bit","0/1",null,"--","--","--"]
[null,1172,{"$nulls":4},"bit","0/1",null,"--","--","--"]
[null,1173,{"$nulls":4},"bit","0/1",null,"--","--","--"]
[null,1174,{"$nulls":4},"bit","0/1",null,"--","--","--"]
[null,1175,{"$nulls":4},"bit","0/1",null,"--","--","--"]
[null,1176,{"$nulls":4},"bit","0/1",null,"--","--","--"]
[null,1177,{"$nulls":4},"bit","0/1",null,"--","--","--"]
[null,1178,null,null,"buzzerTone","internal","byte","0..255",null,"rw","--","rw",null,"system"]
[]
[]
[]
[]
[null,1200," ",null,"BMS port","internal","byte",null,null,"r","r","rw",null,"bms"]
[null,1201," ",null,"BMS protocol","internal","byte",null,null,"r","r","rw",null,"bms"]
[null,1202," ",null,"BMS baudrate","internal","word","300..57600","300..57600","r","r","rw","no continuous range but some discrete values"]
[null,1203,null,null,"BMS handshake","internal","byte",null,null,"r","r","rw"]
[null,1204,null,null,"BMS parity","internal","byte",null,null,"r","r","rw"]
[null,1205,null,null,"BMS databits","internal","byte",null,null,"r","r","rw"]
[null,1206,null,null,"BMS stopbits","internal","byte",null,null,"r","r","rw"]
[null,1207,null,null,"BMS IEEE word-order","internal","bit","0/1","LSW/MSW first","rw","r",null,"word-order in modbus-commands","bms"]
[null,1208,null,null,"BMS modem","internal","bit","0/1","inactive/active","rw","r",null,null,"bms"]
[null,1209,{"$nulls":4},"bit"]
[null,1210,null,null,"BMS write-enable","internal","bit","0/1","inactive/active","r","r",null,"changeable by service-port only for higher safety","bms","r","r"]
[null,1211,{"$nulls":4},"bit"]
[null,1212,{"$nulls":4},"bit"]
[null,1213,{"$nulls":4},"bit"]
[null,1214,{"$nulls":4},"bit"]
[null,1215,null,null,"BMS password","internal","long",null,null,"rw","--",null,null,"bms","rw","rw"]
[null,1216,null,null,"BMS modem autoinit","internal","byte","0/1..255","inactive/minutes","rw","r",null,null,"bms","rw","rw"]
[null,1217]
[null,1218]
[null,1219]
[null,1220,null,null,"BMS tel1","internal","string15",null,null,"rw","r",null,null,"bms","rw","rw"]
[null,1235,null,null,"BMS tel2","internal","string15",null,null,"rw","r",null,null,"bms","rw","rw"]
[null,1250,null,null,"BMS tel3","internal","string15",null,null,"rw","r",null,null,"bms","rw","rw"]
[null,1265,null,null,"BMS tel4","internal","string15",null,null,"rw","r",null,null,"bms","rw","rw"]
[null,1280,null,null,"BMS modem initstring","internal","string32",null,null,"rw","r",null,"changeable by service-port only ","bms","rw","rw"]
[null,1320]
{"$rows_empty":18}
["Global Zone Data:",null,null," "]
[{"$nulls":3}," "]
[null,35200,null,70400,"Bitmap of zone 1 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35201,null,70402,"Bitmap of zone 2 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35202,null,70404,"Bitmap of zone 3 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35203,null,70406,"Bitmap of zone 4 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35204,null,70408,"Bitmap of zone 5 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35205,null,70410,"Bitmap of zone 6 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35206,null,70412,"Bitmap of zone 7 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35207,null,70414,"Bitmap of zone 8 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35208,null,70416,"Bitmap of zone 9 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35209,null,70418,"Bitmap of zone 10 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35210,null,70420,"Bitmap of zone 11 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35211,null,70422,"Bitmap of zone 12 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35212,null,70424,"Bitmap of zone 13 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35213,null,70426,"Bitmap of zone 14 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35214,null,70428,"Bitmap of zone 15 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35215,null,70430,"Bitmap of zone 16 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35216,null,70432,"Bitmap of zone 17 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35217,null,70434,"Bitmap of zone 18 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35218,null,70436,"Bitmap of zone 19 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35219,null,70438,"Bitmap of zone 20 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35220,null,70440,"Bitmap of zone 21 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35221,null,70442,"Bitmap of zone 22 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35222,null,70444,"Bitmap of zone 23 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35223,null,70446,"Bitmap of zone 24 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35224,null,70448,"Bitmap of zone 25 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35225,null,70450,"Bitmap of zone 26 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35226,null,70452,"Bitmap of zone 27 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35227,null,70454,"Bitmap of zone 28 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35228,null,70456,"Bitmap of zone 29 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35229,null,70458,"Bitmap of zone 30 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35230,null,70460,"Bitmap of zone 31 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35231,null,70462,"Bitmap of zone 32 members","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[{"$nulls":3}," "]
[null,35232,null,70464,"Sequencing time of zone 1","internal","UI16","0..0xFFFF","hours","rw","r","Time in hours"]
[null,35233,null,70466,"Sequencing time of zone 2","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35234,null,70468,"Sequencing time of zone 3","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35235,null,70470,"Sequencing time of zone 4","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35236,null,70472,"Sequencing time of zone 5","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35237,null,70474,"Sequencing time of zone 6","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35238,null,70476,"Sequencing time of zone 7","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35239,null,70478,"Sequencing time of zone 8","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35240,null,70480,"Sequencing time of zone 9","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35241,null,70482,"Sequencing time of zone 10","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35242,null,70484,"Sequencing time of zone 11","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35243,null,70486,"Sequencing time of zone 12","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35244,null,70488,"Sequencing time of zone 13","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35245,null,70490,"Sequencing time of zone 14","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35246,null,70492,"Sequencing time of zone 15","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35247,null,70494,"Sequencing time of zone 16","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35248,null,70496,"Sequencing time of zone 17","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35249,null,70498,"Sequencing time of zone 18","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35250,null,70500,"Sequencing time of zone 19","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35251,null,70502,"Sequencing time of zone 20","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35252,null,70504,"Sequencing time of zone 21","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35253,null,70506,"Sequencing time of zone 22","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35254,null,70508,"Sequencing time of zone 23","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35255,null,70510,"Sequencing time of zone 24","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35256,null,70512,"Sequencing time of zone 25","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35257,null,70514,"Sequencing time of zone 26","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35258,null,70516,"Sequencing time of zone 27","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35259,null,70518,"Sequencing time of zone 28","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35260,null,70520,"Sequencing time of zone 29","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35261,null,70522,"Sequencing time of zone 30","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35262,null,70524,"Sequencing time of zone 31","internal","UI16","0..0xFFFF","hours","rw","r"]
[null,35263,null,70526,"Sequencing time of zone 32","internal","UI16","0..0xFFFF","hours","rw","r"]
[{"$nulls":3}," "]
[null,35264,null,70528,"Valid alarms 1 of zone 1","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35265,null,70530,"Valid alarms 1 of zone 2","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35266,null,70532,"Valid alarms 1 of zone 3","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35267,null,70534,"Valid alarms 1 of zone 4","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35268,null,70536,"Valid alarms 1 of zone 5","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35269,null,70538,"Valid alarms 1 of zone 6","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35270,null,70540,"Valid alarms 1 of zone 7","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35271,null,70542,"Valid alarms 1 of zone 8","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35272,null,70544,"Valid alarms 1 of zone 9","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35273,null,70546,"Valid alarms 1 of zone 10","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35274,null,70548,"Valid alarms 1 of zone 11","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35275,null,70550,"Valid alarms 1 of zone 12","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35276,null,70552,"Valid alarms 1 of zone 13","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35277,null,70554,"Valid alarms 1 of zone 14","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35278,null,70556,"Valid alarms 1 of zone 15","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35279,null,70558,"Valid alarms 1 of zone 16","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35280,null,70560,"Valid alarms 1 of zone 17","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35281,null,70562,"Valid alarms 1 of zone 18","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35282,null,70564,"Valid alarms 1 of zone 19","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35283,null,70566,"Valid alarms 1 of zone 20","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35284,null,70568,"Valid alarms 1 of zone 21","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35285,null,70570,"Valid alarms 1 of zone 22","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35286,null,70572,"Valid alarms 1 of zone 23","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35287,null,70574,"Valid alarms 1 of zone 24","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35288,null,70576,"Valid alarms 1 of zone 25","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35289,null,70578,"Valid alarms 1 of zone 26","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35290,null,70580,"Valid alarms 1 of zone 27","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35291,null,70582,"Valid alarms 1 of zone 28","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35292,null,70584,"Valid alarms 1 of zone 29","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35293,null,70586,"Valid alarms 1 of zone 30","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35294,null,70588,"Valid alarms 1 of zone 31","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35295,null,70590,"Valid alarms 1 of zone 32","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[{"$nulls":3}," "]
[null,35296,null,70592,"Valid alarms 2 of zone 1","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35297,null,70594,"Valid alarms 2 of zone 2","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35298,null,70596,"Valid alarms 2 of zone 3","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35299,null,70598,"Valid alarms 2 of zone 4","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35300,null,70600,"Valid alarms 2 of zone 5","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35301,null,70602,"Valid alarms 2 of zone 6","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35302,null,70604,"Valid alarms 2 of zone 7","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35303,null,70606,"Valid alarms 2 of zone 8","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35304,null,70608,"Valid alarms 2 of zone 9","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35305,null,70610,"Valid alarms 2 of zone 10","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35306,null,70612,"Valid alarms 2 of zone 11","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35307,null,70614,"Valid alarms 2 of zone 12","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35308,null,70616,"Valid alarms 2 of zone 13","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35309,null,70618,"Valid alarms 2 of zone 14","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35310,null,70620,"Valid alarms 2 of zone 15","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35311,null,70622,"Valid alarms 2 of zone 16","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35312,null,70624,"Valid alarms 2 of zone 17","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35313,null,70626,"Valid alarms 2 of zone 18","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35314,null,70628,"Valid alarms 2 of zone 19","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35315,null,70630,"Valid alarms 2 of zone 20","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35316,null,70632,"Valid alarms 2 of zone 21","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35317,null,70634,"Valid alarms 2 of zone 22","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35318,null,70636,"Valid alarms 2 of zone 23","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35319,null,70638,"Valid alarms 2 of zone 24","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35320,null,70640,"Valid alarms 2 of zone 25","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35321,null,70642,"Valid alarms 2 of zone 26","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35322,null,70644,"Valid alarms 2 of zone 27","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35323,null,70646,"Valid alarms 2 of zone 28","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35324,null,70648,"Valid alarms 2 of zone 29","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35325,null,70650,"Valid alarms 2 of zone 30","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35326,null,70652,"Valid alarms 2 of zone 31","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[null,35327,null,70654,"Valid alarms 2 of zone 32","internal","UI32","0-0xFFFFFFFF","bit-coded","rw","r"]
[{"$nulls":3}," "]
[null,35328,null,70656,"5 min testsequencing active in zone 1","internal","BIT1","0..1",null,"rw","r"]
[null,35329,null,70658,"5 min testsequencing active in zone 2","internal","BIT1","0..1",null,"rw","r"]
[null,35330,null,70660,"5 min testsequencing active in zone 3","internal","BIT1","0..1",null,"rw","r"]
[null,35331,null,70662,"5 min testsequencing active in zone 4","internal","BIT1","0..1",null,"rw","r"]
[null,35332,null,70664,"5 min testsequencing active in zone 5","internal","BIT1","0..1",null,"rw","r"]
[null,35333,null,70666,"5 min testsequencing active in zone 6","internal","BIT1","0..1",null,"rw","r"]
[null,35334,null,70668,"5 min testsequencing active in zone 7","internal","BIT1","0..1",null,"rw","r"]
[null,35335,null,70670,"5 min testsequencing active in zone 8","internal","BIT1","0..1",null,"rw","r"]
[null,35336,null,70672,"5 min testsequencing active in zone 9","internal","BIT1","0..1",null,"rw","r"]
[null,35337,null,70674,"5 min testsequencing active in zone 10","internal","BIT1","0..1",null,"rw","r"]
[null,35338,null,70676,"5 min testsequencing active in zone 11","internal","BIT1","0..1",null,"rw","r"]
[null,35339,null,70678,"5 min testsequencing active in zone 12","internal","BIT1","0..1",null,"rw","r"]
[null,35340,null,70680,"5 min testsequencing active in zone 13","internal","BIT1","0..1",null,"rw","r"]
[null,35341,null,70682,"5 min testsequencing active in zone 14","internal","BIT1","0..1",null,"rw","r"]
[null,35342,null,70684,"5 min testsequencing active in zone 15","internal","BIT1","0..1",null,"rw","r"]
[null,35343,null,70686,"5 min testsequencing active in zone 16","internal","BIT1","0..1",null,"rw","r"]
[null,35344,null,70688,"5 min testsequencing active in zone 17","internal","BIT1","0..1",null,"rw","r"]
[null,35345,null,70690,"5 min testsequencing active in zone 18","internal","BIT1","0..1",null,"rw","r"]
[null,35346,null,70692,"5 min testsequencing active in zone 19","internal","BIT1","0..1",null,"rw","r"]
[null,35347,null,70694,"5 min testsequencing active in zone 20","internal","BIT1","0..1",null,"rw","r"]
[null,35348,null,70696,"5 min testsequencing active in zone 21","internal","BIT1","0..1",null,"rw","r"]
[null,35349,null,70698,"5 min testsequencing active in zone 22","internal","BIT1","0..1",null,"rw","r"]
[null,35350,null,70700,"5 min testsequencing active in zone 23","internal","BIT1","0..1",null,"rw","r"]
[null,35351,null,70702,"5 min testsequencing active in zone 24","internal","BIT1","0..1",null,"rw","r"]
[null,35352,null,70704,"5 min testsequencing active in zone 25","internal","BIT1","0..1",null,"rw","r"]
[null,35353,null,70706,"5 min testsequencing active in zone 26","internal","BIT1","0..1",null,"rw","r"]
[null,35354,null,70708,"5 min testsequencing active in zone 27","internal","BIT1","0..1",null,"rw","r"]
[null,35355,null,70710,"5 min testsequencing active in zone 28","internal","BIT1","0..1",null,"rw","r"]
[null,35356,null,70712,"5 min testsequencing active in zone 29","internal","BIT1","0..1",null,"rw","r"]
[null,35357,null,70714,"5 min testsequencing active in zone 30","internal","BIT1","0..1",null,"rw","r"]
[null,35358,null,70716,"5 min testsequencing active in zone 31","internal","BIT1","0..1",null,"rw","r"]
[null,35359,null,70718,"5 min testsequencing active in zone 32","internal","BIT1","0..1",null,"rw","r"]
[{"$nulls":3}," "]
[null,35360,null,70720,"Number of error units of zone 1","internal","UI8","0-32",null,"rw","r"]
[null,35361,null,70722,"Number of error units of zone 2","internal","UI8","0-32",null,"rw","r"]
[null,35362,null,70724,"Number of error units of zone 3","internal","UI8","0-32",null,"rw","r"]
[null,35363,null,70726,"Number of error units of zone 4","internal","UI8","0-32",null,"rw","r"]
[null,35364,null,70728,"Number of error units of zone 5","internal","UI8","0-32",null,"rw","r"]
[null,35365,null,70730,"Number of error units of zone 6","internal","UI8","0-32",null,"rw","r"]
[null,35366,null,70732,"Number of error units of zone 7","internal","UI8","0-32",null,"rw","r"]
[null,35367,null,70734,"Number of error units of zone 8","internal","UI8","0-32",null,"rw","r"]
[null,35368,null,70736,"Number of error units of zone 9","internal","UI8","0-32",null,"rw","r"]
[null,35369,null,70738,"Number of error units of zone 10","internal","UI8","0-32",null,"rw","r"]
[null,35370,null,70740,"Number of error units of zone 11","internal","UI8","0-32",null,"rw","r"]
[null,35371,null,70742,"Number of error units of zone 12","internal","UI8","0-32",null,"rw","r"]
[null,35372,null,70744,"Number of error units of zone 13","internal","UI8","0-32",null,"rw","r"]
[null,35373,null,70746,"Number of error units of zone 14","internal","UI8","0-32",null,"rw","r"]
[null,35374,null,70748,"Number of error units of zone 15","internal","UI8","0-32",null,"rw","r"]
[null,35375,null,70750,"Number of error units of zone 16","internal","UI8","0-32",null,"rw","r"]
[null,35376,null,70752,"Number of error units of zone 17","internal","UI8","0-32",null,"rw","r"]
[null,35377,null,70754,"Number of error units of zone 18","internal","UI8","0-32",null,"rw","r"]
[null,35378,null,70756,"Number of error units of zone 19","internal","UI8","0-32",null,"rw","r"]
[null,35379,null,70758,"Number of error units of zone 20","internal","UI8","0-32",null,"rw","r"]
[null,35380,null,70760,"Number of error units of zone 21","internal","UI8","0-32",null,"rw","r"]
[null,35381,null,70762,"Number of error units of zone 22","internal","UI8","0-32",null,"rw","r"]
[null,35382,null,70764,"Number of error units of zone 23","internal","UI8","0-32",null,"rw","r"]
[null,35383,null,70766,"Number of error units of zone 24","internal","UI8","0-32",null,"rw","r"]
[null,35384,null,70768,"Number of error units of zone 25","internal","UI8","0-32",null,"rw","r"]
[null,35385,null,70770,"Number of error units of zone 26","internal","UI8","0-32",null,"rw","r"]
[null,35386,null,70772,"Number of error units of zone 27","internal","UI8","0-32",null,"rw","r"]
[null,35387,null,70774,"Number of error units of zone 28","internal","UI8","0-32",null,"rw","r"]
[null,35388,null,70776,"Number of error units of zone 29","internal","UI8","0-32",null,"rw","r"]
[null,35389,null,70778,"Number of error units of zone 30","internal","UI8","0-32",null,"rw","r"]
[null,35390,null,70780,"Number of error units of zone 31","internal","UI8","0-32",null,"rw","r"]
[null,35391,null,70782,"Number of error units of zone 32","internal","UI8","0-32",null,"rw","r"]
[{"$nulls":3}," "]
[null,35392,null,70784,"Emergency temperature of zone 1","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35393,null,70786,"Emergency temperature of zone 2","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35394,null,70788,"Emergency temperature of zone 3","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35395,null,70790,"Emergency temperature of zone 4","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35396,null,70792,"Emergency temperature of zone 5","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35397,null,70794,"Emergency temperature of zone 6","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35398,null,70796,"Emergency temperature of zone 7","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35399,null,70798,"Emergency temperature of zone 8","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35400,null,70800,"Emergency temperature of zone 9","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35401,null,70802,"Emergency temperature of zone 10","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35402,null,70804,"Emergency temperature of zone 11","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35403,null,70806,"Emergency temperature of zone 12","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35404,null,70808,"Emergency temperature of zone 13","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35405,null,70810,"Emergency temperature of zone 14","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35406,null,70812,"Emergency temperature of zone 15","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35407,null,70814,"Emergency temperature of zone 16","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35408,null,70816,"Emergency temperature of zone 17","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35409,null,70818,"Emergency temperature of zone 18","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35410,null,70820,"Emergency temperature of zone 19","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35411,null,70822,"Emergency temperature of zone 20","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35412,null,70824,"Emergency temperature of zone 21","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35413,null,70826,"Emergency temperature of zone 22","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35414,null,70828,"Emergency temperature of zone 23","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35415,null,70830,"Emergency temperature of zone 24","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35416,null,70832,"Emergency temperature of zone 25","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35417,null,70834,"Emergency temperature of zone 26","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35418,null,70836,"Emergency temperature of zone 27","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35419,null,70838,"Emergency temperature of zone 28","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35420,null,70840,"Emergency temperature of zone 29","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35421,null,70842,"Emergency temperature of zone 30","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35422,null,70844,"Emergency temperature of zone 31","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[null,35423,null,70846,"Emergency temperature of zone 32","internal","SI16","0..400","0,0..40,0°C","rw","r"]
[{"$nulls":3}," "]
[null,35424,null,70848,"Emergency operation of zone 1 active","internal","BIT1","0, 1",null,"r","r"]
[null,35425,null,70850,"Emergency operation of zone 2 active","internal","BIT1","0, 1",null,"r","r"]
[null,35426,null,70852,"Emergency operation of zone 3 active","internal","BIT1","0, 1",null,"r","r"]
[null,35427,null,70854,"Emergency operation of zone 4 active","internal","BIT1","0, 1",null,"r","r"]
[null,35428,null,70856,"Emergency operation of zone 5 active","internal","BIT1","0, 1",null,"r","r"]
[null,35429,null,70858,"Emergency operation of zone 6 active","internal","BIT1","0, 1",null,"r","r"]
[null,35430,null,70860,"Emergency operation of zone 7 active","internal","BIT1","0, 1",null,"r","r"]
[null,35431,null,70862,"Emergency operation of zone 8 active","internal","BIT1","0, 1",null,"r","r"]
[null,35432,null,70864,"Emergency operation of zone 9 active","internal","BIT1","0, 1",null,"r","r"]
[null,35433,null,70866,"Emergency operation of zone 10 active","internal","BIT1","0, 1",null,"r","r"]
[null,35434,null,70868,"Emergency operation of zone 11 active","internal","BIT1","0, 1",null,"r","r"]
[null,35435,null,70870,"Emergency operation of zone 12 active","internal","BIT1","0, 1",null,"r","r"]
[null,35436,null,70872,"Emergency operation of zone 13 active","internal","BIT1","0, 1",null,"r","r"]
[null,35437,null,70874,"Emergency operation of zone 14 active","internal","BIT1","0, 1",null,"r","r"]
[null,35438,null,70876,"Emergency operation of zone 15 active","internal","BIT1","0, 1",null,"r","r"]
[null,35439,null,70878,"Emergency operation of zone 16 active","internal","BIT1","0, 1",null,"r","r"]
[null,35440,null,70880,"Emergency operation of zone 17 active","internal","BIT1","0, 1",null,"r","r"]
[null,35441,null,70882,"Emergency operation of zone 18 active","internal","BIT1","0, 1",null,"r","r"]
[null,35442,null,70884,"Emergency operation of zone 19 active","internal","BIT1","0, 1",null,"r","r"]
[null,35443,null,70886,"Emergency operation of zone 20 active","internal","BIT1","0, 1",null,"r","r"]
[null,35444,null,70888,"Emergency operation of zone 21 active","internal","BIT1","0, 1",null,"r","r"]
[null,35445,null,70890,"Emergency operation of zone 22 active","internal","BIT1","0, 1",null,"r","r"]
[null,35446,null,70892,"Emergency operation of zone 23 active","internal","BIT1","0, 1",null,"r","r"]
[null,35447,null,70894,"Emergency operation of zone 24 active","internal","BIT1","0, 1",null,"r","r"]
[null,35448,null,70896,"Emergency operation of zone 25 active","internal","BIT1","0, 1",null,"r","r"]
[null,35449,null,70898,"Emergency operation of zone 26 active","internal","BIT1","0, 1",null,"r","r"]
[null,35450,null,70900,"Emergency operation of zone 27 active","internal","BIT1","0, 1",null,"r","r"]
[null,35451,null,70902,"Emergency operation of zone 28 active","internal","BIT1","0, 1",null,"r","r"]
[null,35452,null,70904,"Emergency operation of zone 29 active","internal","BIT1","0, 1",null,"r","r"]
[null,35453,null,70906,"Emergency operation of zone 30 active","internal","BIT1","0, 1",null,"r","r"]
[null,35454,null,70908,"Emergency operation of zone 31 active","internal","BIT1","0, 1",null,"r","r"]
[null,35455,null,70910,"Emergency operation of zone 32 active","internal","BIT1","0, 1",null,"r","r"]
[{"$nulls":3}," "]
[null,35456,null,70912,"nMax of zone 1","internal","UI8","0-100%",null,"rw","r"]
[null,35457,null,70914,"nMax of zone 2","internal","UI8","0-100%",null,"rw","r"]
[null,35458,null,70916,"nMax of zone 3","internal","UI8","0-100%",null,"rw","r"]
[null,35459,null,70918,"nMax of zone 4","internal","UI8","0-100%",null,"rw","r"]
[null,35460,null,70920,"nMax of zone 5","internal","UI8","0-100%",null,"rw","r"]
[null,35461,null,70922,"nMax of zone 6","internal","UI8","0-100%",null,"rw","r"]
[null,35462,null,70924,"nMax of zone 7","internal","UI8","0-100%",null,"rw","r"]
[null,35463,null,70926,"nMax of zone 8","internal","UI8","0-100%",null,"rw","r"]
[null,35464,null,70928,"nMax of zone 9","internal","UI8","0-100%",null,"rw","r"]
[null,35465,null,70930,"nMax of zone 10","internal","UI8","0-100%",null,"rw","r"]
[null,35466,null,70932,"nMax of zone 11","internal","UI8","0-100%",null,"rw","r"]
[null,35467,null,70934,"nMax of zone 12","internal","UI8","0-100%",null,"rw","r"]
[null,35468,null,70936,"nMax of zone 13","internal","UI8","0-100%",null,"rw","r"]
[null,35469,null,70938,"nMax of zone 14","internal","UI8","0-100%",null,"rw","r"]
[null,35470,null,70940,"nMax of zone 15","internal","UI8","0-100%",null,"rw","r"]
[null,35471,null,70942,"nMax of zone 16","internal","UI8","0-100%",null,"rw","r"]
[null,35472,null,70944,"nMax of zone 17","internal","UI8","0-100%",null,"rw","r"]
[null,35473,null,70946,"nMax of zone 18","internal","UI8","0-100%",null,"rw","r"]
[null,35474,null,70948,"nMax of zone 19","internal","UI8","0-100%",null,"rw","r"]
[null,35475,null,70950,"nMax of zone 20","internal","UI8","0-100%",null,"rw","r"]
[null,35476,null,70952,"nMax of zone 21","internal","UI8","0-100%",null,"rw","r"]
[null,35477,null,70954,"nMax of zone 22","internal","UI8","0-100%",null,"rw","r"]
[null,35478,null,70956,"nMax of zone 23","internal","UI8","0-100%",null,"rw","r"]
[null,35479,null,70958,"nMax of zone 24","internal","UI8","0-100%",null,"rw","r"]
[null,35480,null,70960,"nMax of zone 25","internal","UI8","0-100%",null,"rw","r"]
[null,35481,null,70962,"nMax of zone 26","internal","UI8","0-100%",null,"rw","r"]
[null,35482,null,70964,"nMax of zone 27","internal","UI8","0-100%",null,"rw","r"]
[null,35483,null,70966,"nMax of zone 28","internal","UI8","0-100%",null,"rw","r"]
[null,35484,null,70968,"nMax of zone 29","internal","UI8","0-100%",null,"rw","r"]
[null,35485,null,70970,"nMax of zone 30","internal","UI8","0-100%",null,"rw","r"]
[null,35486,null,70972,"nMax of zone 31","internal","UI8","0-100%",null,"rw","r"]
[null,35487,null,70974,"nMax of zone 32","internal","UI8","0-100%",null,"rw","r"]
[{"$nulls":3}," "]
[null,35488,null,70976,"CW energy save mode of zone 1","internal","BIT1","0, 1",null,"rw","r"]
[null,35489,null,70978,"CW energy save mode of zone 2","internal","BIT1","0, 1",null,"rw","r"]
[null,35490,null,70980,"CW energy save mode of zone 3","internal","BIT1","0, 1",null,"rw","r"]
[null,35491,null,70982,"CW energy save mode of zone 4","internal","BIT1","0, 1",null,"rw","r"]
[null,35492,null,70984,"CW energy save mode of zone 5","internal","BIT1","0, 1",null,"rw","r"]
[null,35493,null,70986,"CW energy save mode of zone 6","internal","BIT1","0, 1",null,"rw","r"]
[null,35494,null,70988,"CW energy save mode of zone 7","internal","BIT1","0, 1",null,"rw","r"]
[null,35495,null,70990,"CW energy save mode of zone 8","internal","BIT1","0, 1",null,"rw","r"]
[null,35496,null,70992,"CW energy save mode of zone 9","internal","BIT1","0, 1",null,"rw","r"]
[null,35497,null,70994,"CW energy save mode of zone 10","internal","BIT1","0, 1",null,"rw","r"]
[null,35498,null,70996,"CW energy save mode of zone 11","internal","BIT1","0, 1",null,"rw","r"]
[null,35499,null,70998,"CW energy save mode of zone 12","internal","BIT1","0, 1",null,"rw","r"]
[null,35500,null,71000,"CW energy save mode of zone 13","internal","BIT1","0, 1",null,"rw","r"]
[null,35501,null,71002,"CW energy save mode of zone 14","internal","BIT1","0, 1",null,"rw","r"]
[null,35502,null,71004,"CW energy save mode of zone 15","internal","BIT1","0, 1",null,"rw","r"]
[null,35503,null,71006,"CW energy save mode of zone 16","internal","BIT1","0, 1",null,"rw","r"]
[null,35504,null,71008,"CW energy save mode of zone 17","internal","BIT1","0, 1",null,"rw","r"]
[null,35505,null,71010,"CW energy save mode of zone 18","internal","BIT1","0, 1",null,"rw","r"]
[null,35506,null,71012,"CW energy save mode of zone 19","internal","BIT1","0, 1",null,"rw","r"]
[null,35507,null,71014,"CW energy save mode of zone 20","internal","BIT1","0, 1",null,"rw","r"]
[null,35508,null,71016,"CW energy save mode of zone 21","internal","BIT1","0, 1",null,"rw","r"]
[null,35509,null,71018,"CW energy save mode of zone 22","internal","BIT1","0, 1",null,"rw","r"]
[null,35510,null,71020,"CW energy save mode of zone 23","internal","BIT1","0, 1",null,"rw","r"]
[null,35511,null,71022,"CW energy save mode of zone 24","internal","BIT1","0, 1",null,"rw","r"]
[null,35512,null,71024,"CW energy save mode of zone 25","internal","BIT1","0, 1",null,"rw","r"]
[null,35513,null,71026,"CW energy save mode of zone 26","internal","BIT1","0, 1",null,"rw","r"]
[null,35514,null,71028,"CW energy save mode of zone 27","internal","BIT1","0, 1",null,"rw","r"]
[null,35515,null,71030,"CW energy save mode of zone 28","internal","BIT1","0, 1",null,"rw","r"]
[null,35516,null,71032,"CW energy save mode of zone 29","internal","BIT1","0, 1",null,"rw","r"]
[null,35517,null,71034,"CW energy save mode of zone 30","internal","BIT1","0, 1",null,"rw","r"]
[null,35518,null,71036,"CW energy save mode of zone 31","internal","BIT1","0, 1",null,"rw","r"]
[null,35519,null,71038,"CW energy save mode of zone 32","internal","BIT1","0, 1",null,"rw","r"]
[{"$nulls":3}," "]
[null,35520,null,71040,"Remaining time to switch of zone 1","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35521,null,71042,"Remaining time to switch of zone 2","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35522,null,71044,"Remaining time to switch of zone 3","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35523,null,71046,"Remaining time to switch of zone 4","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35524,null,71048,"Remaining time to switch of zone 5","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35525,null,71050,"Remaining time to switch of zone 6","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35526,null,71052,"Remaining time to switch of zone 7","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35527,null,71054,"Remaining time to switch of zone 8","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35528,null,71056,"Remaining time to switch of zone 9","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35529,null,71058,"Remaining time to switch of zone 10","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35530,null,71060,"Remaining time to switch of zone 11","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35531,null,71062,"Remaining time to switch of zone 12","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35532,null,71064,"Remaining time to switch of zone 13","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35533,null,71066,"Remaining time to switch of zone 14","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35534,null,71068,"Remaining time to switch of zone 15","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35535,null,71070,"Remaining time to switch of zone 16","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35536,null,71072,"Remaining time to switch of zone 17","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35537,null,71074,"Remaining time to switch of zone 18","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35538,null,71076,"Remaining time to switch of zone 19","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35539,null,71078,"Remaining time to switch of zone 20","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35540,null,71080,"Remaining time to switch of zone 21","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35541,null,71082,"Remaining time to switch of zone 22","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35542,null,71084,"Remaining time to switch of zone 23","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35543,null,71086,"Remaining time to switch of zone 24","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35544,null,71088,"Remaining time to switch of zone 25","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35545,null,71090,"Remaining time to switch of zone 26","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35546,null,71092,"Remaining time to switch of zone 27","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35547,null,71094,"Remaining time to switch of zone 28","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35548,null,71096,"Remaining time to switch of zone 29","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35549,null,71098,"Remaining time to switch of zone 30","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35550,null,71100,"Remaining time to switch of zone 31","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[null,35551,null,71102,"Remaining time to switch of zone 32","internal","UI32","0-0xFFFFFFFF","minutes","rw","r"]
[{"$nulls":3}," "]
[null,35552,null,71104,"Sequencing switch of zone 1","internal","BIT1","0, 1",null,"rw","r"]
[null,35553,null,71106,"Sequencing switch of zone 2","internal","BIT1","0, 1",null,"rw","r"]
[null,35554,null,71108,"Sequencing switch of zone 3","internal","BIT1","0, 1",null,"rw","r"]
[null,35555,null,71110,"Sequencing switch of zone 4","internal","BIT1","0, 1",null,"rw","r"]
[null,35556,null,71112,"Sequencing switch of zone 5","internal","BIT1","0, 1",null,"rw","r"]
[null,35557,null,71114,"Sequencing switch of zone 6","internal","BIT1","0, 1",null,"rw","r"]
[null,35558,null,71116,"Sequencing switch of zone 7","internal","BIT1","0, 1",null,"rw","r"]
[null,35559,null,71118,"Sequencing switch of zone 8","internal","BIT1","0, 1",null,"rw","r"]
[null,35560,null,71120,"Sequencing switch of zone 9","internal","BIT1","0, 1",null,"rw","r"]
[null,35561,null,71122,"Sequencing switch of zone 10","internal","BIT1","0, 1",null,"rw","r"]
[null,35562,null,71124,"Sequencing switch of zone 11","internal","BIT1","0, 1",null,"rw","r"]
[null,35563,null,71126,"Sequencing switch of zone 12","internal","BIT1","0, 1",null,"rw","r"]
[null,35564,null,71128,"Sequencing switch of zone 13","internal","BIT1","0, 1",null,"rw","r"]
[null,35565,null,71130,"Sequencing switch of zone 14","internal","BIT1","0, 1",null,"rw","r"]
[null,35566,null,71132,"Sequencing switch of zone 15","internal","BIT1","0, 1",null,"rw","r"]
[null,35567,null,71134,"Sequencing switch of zone 16","internal","BIT1","0, 1",null,"rw","r"]
[null,35568,null,71136,"Sequencing switch of zone 17","internal","BIT1","0, 1",null,"rw","r"]
[null,35569,null,71138,"Sequencing switch of zone 18","internal","BIT1","0, 1",null,"rw","r"]
[null,35570,null,71140,"Sequencing switch of zone 19","internal","BIT1","0, 1",null,"rw","r"]
[null,35571,null,71142,"Sequencing switch of zone 20","internal","BIT1","0, 1",null,"rw","r"]
[null,35572,null,71144,"Sequencing switch of zone 21","internal","BIT1","0, 1",null,"rw","r"]
[null,35573,null,71146,"Sequencing switch of zone 22","internal","BIT1","0, 1",null,"rw","r"]
[null,35574,null,71148,"Sequencing switch of zone 23","internal","BIT1","0, 1",null,"rw","r"]
[null,35575,null,71150,"Sequencing switch of zone 24","internal","BIT1","0, 1",null,"rw","r"]
[null,35576,null,71152,"Sequencing switch of zone 25","internal","BIT1","0, 1",null,"rw","r"]
[null,35577,null,71154,"Sequencing switch of zone 26","internal","BIT1","0, 1",null,"rw","r"]
[null,35578,null,71156,"Sequencing switch of zone 27","internal","BIT1","0, 1",null,"rw","r"]
[null,35579,null,71158,"Sequencing switch of zone 28","internal","BIT1","0, 1",null,"rw","r"]
[null,35580,null,71160,"Sequencing switch of zone 29","internal","BIT1","0, 1",null,"rw","r"]
[null,35581,null,71162,"Sequencing switch of zone 30","internal","BIT1","0, 1",null,"rw","r"]
[null,35582,null,71164,"Sequencing switch of zone 31","internal","BIT1","0, 1",null,"rw","r"]
[null,35583,null,71166,"Sequencing switch of zone 32","internal","BIT1","0, 1",null,"rw","r"]
[{"$nulls":3}," "]
[null,35900,null,null,"Sequencing Stop Bitmap of all zone","internal","UI32","0..0xFFFFFFFF","bit-coded","rw","r"]
[{"$nulls":3}," "]
["Global Unit Data:",null,null," "]
[{"$nulls":3}," "]
[null,36000,null,72000,"Room temperature of unit 0","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36001,null,72002,"Room temperature of unit 1","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36002,null,72004,"Room temperature of unit 2","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36003,null,72006,"Room temperature of unit 3","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36004,null,72008,"Room temperature of unit 4","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36005,null,72010,"Room temperature of unit 5","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36006,null,72012,"Room temperature of unit 6","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36007,null,72014,"Room temperature of unit 7","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36008,null,72016,"Room temperature of unit 8","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36009,null,72018,"Room temperature of unit 9","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36010,null,72020,"Room temperature of unit 10","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36011,null,72022,"Room temperature of unit 11","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36012,null,72024,"Room temperature of unit 12","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36013,null,72026,"Room temperature of unit 13","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36014,null,72028,"Room temperature of unit 14","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36015,null,72030,"Room temperature of unit 15","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36016,null,72032,"Room temperature of unit 16","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36017,null,72034,"Room temperature of unit 17","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36018,null,72036,"Room temperature of unit 18","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36019,null,72038,"Room temperature of unit 19","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36020,null,72040,"Room temperature of unit 20","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36021,null,72042,"Room temperature of unit 21","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36022,null,72044,"Room temperature of unit 22","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36023,null,72046,"Room temperature of unit 23","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36024,null,72048,"Room temperature of unit 24","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36025,null,72050,"Room temperature of unit 25","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36026,null,72052,"Room temperature of unit 26","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36027,null,72054,"Room temperature of unit 27","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36028,null,72056,"Room temperature of unit 28","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36029,null,72058,"Room temperature of unit 29","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36030,null,72060,"Room temperature of unit 30","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36031,null,72062,"Room temperature of unit 31","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[{"$nulls":3}," "]
[null,36032,null,72064,"Room humidity of unit 0","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36033,null,72066,"Room humidity of unit 1","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36034,null,72068,"Room humidity of unit 2","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36035,null,72070,"Room humidity of unit 3","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36036,null,72072,"Room humidity of unit 4","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36037,null,72074,"Room humidity of unit 5","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36038,null,72076,"Room humidity of unit 6","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36039,null,72078,"Room humidity of unit 7","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36040,null,72080,"Room humidity of unit 8","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36041,null,72082,"Room humidity of unit 9","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36042,null,72084,"Room humidity of unit 10","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36043,null,72086,"Room humidity of unit 11","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36044,null,72088,"Room humidity of unit 12","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36045,null,72090,"Room humidity of unit 13","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36046,null,72092,"Room humidity of unit 14","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36047,null,72094,"Room humidity of unit 15","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36048,null,72096,"Room humidity of unit 16","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36049,null,72098,"Room humidity of unit 17","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36050,null,72100,"Room humidity of unit 18","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36051,null,72102,"Room humidity of unit 19","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36052,null,72104,"Room humidity of unit 20","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36053,null,72106,"Room humidity of unit 21","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36054,null,72108,"Room humidity of unit 22","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36055,null,72110,"Room humidity of unit 23","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36056,null,72112,"Room humidity of unit 24","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36057,null,72114,"Room humidity of unit 25","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36058,null,72116,"Room humidity of unit 26","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36059,null,72118,"Room humidity of unit 27","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36060,null,72120,"Room humidity of unit 28","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36061,null,72122,"Room humidity of unit 29","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36062,null,72124,"Room humidity of unit 30","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36063,null,72126,"Room humidity of unit 31","internal","word","0..1000","0,0..100,0%rF","r","r"]
[{"$nulls":3}," "]
[null,36064,null,72128,"Supply temperature of unit 0","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36065,null,72130,"Supply temperature of unit 1","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36066,null,72132,"Supply temperature of unit 2","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36067,null,72134,"Supply temperature of unit 3","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36068,null,72136,"Supply temperature of unit 4","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36069,null,72138,"Supply temperature of unit 5","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36070,null,72140,"Supply temperature of unit 6","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36071,null,72142,"Supply temperature of unit 7","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36072,null,72144,"Supply temperature of unit 8","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36073,null,72146,"Supply temperature of unit 9","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36074,null,72148,"Supply temperature of unit 10","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36075,null,72150,"Supply temperature of unit 11","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36076,null,72152,"Supply temperature of unit 12","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36077,null,72154,"Supply temperature of unit 13","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36078,null,72156,"Supply temperature of unit 14","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36079,null,72158,"Supply temperature of unit 15","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36080,null,72160,"Supply temperature of unit 16","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36081,null,72162,"Supply temperature of unit 17","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36082,null,72164,"Supply temperature of unit 18","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36083,null,72166,"Supply temperature of unit 19","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36084,null,72168,"Supply temperature of unit 20","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36085,null,72170,"Supply temperature of unit 21","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36086,null,72172,"Supply temperature of unit 22","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36087,null,72174,"Supply temperature of unit 23","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36088,null,72176,"Supply temperature of unit 24","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36089,null,72178,"Supply temperature of unit 25","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36090,null,72180,"Supply temperature of unit 26","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36091,null,72182,"Supply temperature of unit 27","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36092,null,72184,"Supply temperature of unit 28","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36093,null,72186,"Supply temperature of unit 29","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36094,null,72188,"Supply temperature of unit 30","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[null,36095,null,72190,"Supply temperature of unit 31","internal","word","-1000..1000","-100,0..100,0°C","r","r"]
[{"$nulls":3}," "]
[null,36096,null,72192,"Supply humidity of unit 0","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36097,null,72194,"Supply humidity of unit 1","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36098,null,72196,"Supply humidity of unit 2","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36099,null,72198,"Supply humidity of unit 3","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36100,null,72200,"Supply humidity of unit 4","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36101,null,72202,"Supply humidity of unit 5","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36102,null,72204,"Supply humidity of unit 6","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36103,null,72206,"Supply humidity of unit 7","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36104,null,72208,"Supply humidity of unit 8","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36105,null,72210,"Supply humidity of unit 9","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36106,null,72212,"Supply humidity of unit 10","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36107,null,72214,"Supply humidity of unit 11","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36108,null,72216,"Supply humidity of unit 12","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36109,null,72218,"Supply humidity of unit 13","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36110,null,72220,"Supply humidity of unit 14","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36111,null,72222,"Supply humidity of unit 15","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36112,null,72224,"Supply humidity of unit 16","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36113,null,72226,"Supply humidity of unit 17","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36114,null,72228,"Supply humidity of unit 18","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36115,null,72230,"Supply humidity of unit 19","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36116,null,72232,"Supply humidity of unit 20","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36117,null,72234,"Supply humidity of unit 21","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36118,null,72236,"Supply humidity of unit 22","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36119,null,72238,"Supply humidity of unit 23","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36120,null,72240,"Supply humidity of unit 24","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36121,null,72242,"Supply humidity of unit 25","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36122,null,72244,"Supply humidity of unit 26","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36123,null,72246,"Supply humidity of unit 27","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36124,null,72248,"Supply humidity of unit 28","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36125,null,72250,"Supply humidity of unit 29","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36126,null,72252,"Supply humidity of unit 30","internal","word","0..1000","0,0..100,0%rF","r","r"]
[null,36127,null,72254,"Supply humidity of unit 31","internal","word","0..1000","0,0..100,0%rF","r","r"]
[{"$nulls":3}," "]
[null,36128,null,72256,"Overload switch of unit 0","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36129,null,72258,"Overload switch of unit 1","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36130,null,72260,"Overload switch of unit 2","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36131,null,72262,"Overload switch of unit 3","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36132,null,72264,"Overload switch of unit 4","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36133,null,72266,"Overload switch of unit 5","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36134,null,72268,"Overload switch of unit 6","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36135,null,72270,"Overload switch of unit 7","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36136,null,72272,"Overload switch of unit 8","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36137,null,72274,"Overload switch of unit 9","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36138,null,72276,"Overload switch of unit 10","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36139,null,72278,"Overload switch of unit 11","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36140,null,72280,"Overload switch of unit 12","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36141,null,72282,"Overload switch of unit 13","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36142,null,72284,"Overload switch of unit 14","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36143,null,72286,"Overload switch of unit 15","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36144,null,72288,"Overload switch of unit 16","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36145,null,72290,"Overload switch of unit 17","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36146,null,72292,"Overload switch of unit 18","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36147,null,72294,"Overload switch of unit 19","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36148,null,72296,"Overload switch of unit 20","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36149,null,72298,"Overload switch of unit 21","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36150,null,72300,"Overload switch of unit 22","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36151,null,72302,"Overload switch of unit 23","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36152,null,72304,"Overload switch of unit 24","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36153,null,72306,"Overload switch of unit 25","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36154,null,72308,"Overload switch of unit 26","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36155,null,72310,"Overload switch of unit 27","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36156,null,72312,"Overload switch of unit 28","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36157,null,72314,"Overload switch of unit 29","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36158,null,72316,"Overload switch of unit 30","internal","SI16","0..99","0,0..9,9K","r","r"]
[null,36159,null,72318,"Overload switch of unit 31","internal","SI16","0..99","0,0..9,9K","r","r"]
[{"$nulls":3}," "]
[null,36160,null,72320,"Zone state of unit 0","internal","UI8","0-255",null,"r","r"]
[null,36161,null,72322,"Zone state of unit 1","internal","UI8","0-255",null,"r","r"]
[null,36162,null,72324,"Zone state of unit 2","internal","UI8","0-255",null,"r","r"]
[null,36163,null,72326,"Zone state of unit 3","internal","UI8","0-255",null,"r","r"]
[null,36164,null,72328,"Zone state of unit 4","internal","UI8","0-255",null,"r","r"]
[null,36165,null,72330,"Zone state of unit 5","internal","UI8","0-255",null,"r","r"]
[null,36166,null,72332,"Zone state of unit 6","internal","UI8","0-255",null,"r","r"]
[null,36167,null,72334,"Zone state of unit 7","internal","UI8","0-255",null,"r","r"]
[null,36168,null,72336,"Zone state of unit 8","internal","UI8","0-255",null,"r","r"]
[null,36169,null,72338,"Zone state of unit 9","internal","UI8","0-255",null,"r","r"]
[null,36170,null,72340,"Zone state of unit 10","internal","UI8","0-255",null,"r","r"]
[null,36171,null,72342,"Zone state of unit 11","internal","UI8","0-255",null,"r","r"]
[null,36172,null,72344,"Zone state of unit 12","internal","UI8","0-255",null,"r","r"]
[null,36173,null,72346,"Zone state of unit 13","internal","UI8","0-255",null,"r","r"]
[null,36174,null,72348,"Zone state of unit 14","internal","UI8","0-255",null,"r","r"]
[null,36175,null,72350,"Zone state of unit 15","internal","UI8","0-255",null,"r","r"]
[null,36176,null,72352,"Zone state of unit 16","internal","UI8","0-255",null,"r","r"]
[null,36177,null,72354,"Zone state of unit 17","internal","UI8","0-255",null,"r","r"]
[null,36178,null,72356,"Zone state of unit 18","internal","UI8","0-255",null,"r","r"]
[null,36179,null,72358,"Zone state of unit 19","internal","UI8","0-255",null,"r","r"]
[null,36180,null,72360,"Zone state of unit 20","internal","UI8","0-255",null,"r","r"]
[null,36181,null,72362,"Zone state of unit 21","internal","UI8","0-255",null,"r","r"]
[null,36182,null,72364,"Zone state of unit 22","internal","UI8","0-255",null,"r","r"]
[null,36183,null,72366,"Zone state of unit 23","internal","UI8","0-255",null,"r","r"]
[null,36184,null,72368,"Zone state of unit 24","internal","UI8","0-255",null,"r","r"]
[null,36185,null,72370,"Zone state of unit 25","internal","UI8","0-255",null,"r","r"]
[null,36186,null,72372,"Zone state of unit 26","internal","UI8","0-255",null,"r","r"]
[null,36187,null,72374,"Zone state of unit 27","internal","UI8","0-255",null,"r","r"]
[null,36188,null,72376,"Zone state of unit 28","internal","UI8","0-255",null,"r","r"]
[null,36189,null,72378,"Zone state of unit 29","internal","UI8","0-255",null,"r","r"]
[null,36190,null,72380,"Zone state of unit 30","internal","UI8","0-255",null,"r","r"]
[null,36191,null,72382,"Zone state of unit 31","internal","UI8","0-255",null,"r","r"]
[{"$nulls":3}," "]
[null,36192,null,72384,"Alarm of unit 0","internal","BIT1","0, 1",null,"r","r"]
[null,36193,null,72386,"Alarm of unit 1","internal","BIT1","0, 1",null,"r","r"]
[null,36194,null,72388,"Alarm of unit 2","internal","BIT1","0, 1",null,"r","r"]
[null,36195,null,72390,"Alarm of unit 3","internal","BIT1","0, 1",null,"r","r"]
[null,36196,null,72392,"Alarm of unit 4","internal","BIT1","0, 1",null,"r","r"]
[null,36197,null,72394,"Alarm of unit 5","internal","BIT1","0, 1",null,"r","r"]
[null,36198,null,72396,"Alarm of unit 6","internal","BIT1","0, 1",null,"r","r"]
[null,36199,null,72398,"Alarm of unit 7","internal","BIT1","0, 1",null,"r","r"]
[null,36200,null,72400,"Alarm of unit 8","internal","BIT1","0, 1",null,"r","r"]
[null,36201,null,72402,"Alarm of unit 9","internal","BIT1","0, 1",null,"r","r"]
[null,36202,null,72404,"Alarm of unit 10","internal","BIT1","0, 1",null,"r","r"]
[null,36203,null,72406,"Alarm of unit 11","internal","BIT1","0, 1",null,"r","r"]
[null,36204,null,72408,"Alarm of unit 12","internal","BIT1","0, 1",null,"r","r"]
[null,36205,null,72410,"Alarm of unit 13","internal","BIT1","0, 1",null,"r","r"]
[null,36206,null,72412,"Alarm of unit 14","internal","BIT1","0, 1",null,"r","r"]
[null,36207,null,72414,"Alarm of unit 15","internal","BIT1","0, 1",null,"r","r"]
[null,36208,null,72416,"Alarm of unit 16","internal","BIT1","0, 1",null,"r","r"]
[null,36209,null,72418,"Alarm of unit 17","internal","BIT1","0, 1",null,"r","r"]
[null,36210,null,72420,"Alarm of unit 18","internal","BIT1","0, 1",null,"r","r"]
[null,36211,null,72422,"Alarm of unit 19","internal","BIT1","0, 1",null,"r","r"]
[null,36212,null,72424,"Alarm of unit 20","internal","BIT1","0, 1",null,"r","r"]
[null,36213,null,72426,"Alarm of unit 21","internal","BIT1","0, 1",null,"r","r"]
[null,36214,null,72428,"Alarm of unit 22","internal","BIT1","0, 1",null,"r","r"]
[null,36215,null,72430,"Alarm of unit 23","internal","BIT1","0, 1",null,"r","r"]
[null,36216,null,72432,"Alarm of unit 24","internal","BIT1","0, 1",null,"r","r"]
[null,36217,null,72434,"Alarm of unit 25","internal","BIT1","0, 1",null,"r","r"]
[null,36218,null,72436,"Alarm of unit 26","internal","BIT1","0, 1",null,"r","r"]
[null,36219,null,72438,"Alarm of unit 27","internal","BIT1","0, 1",null,"r","r"]
[null,36220,null,72440,"Alarm of unit 28","internal","BIT1","0, 1",null,"r","r"]
[null,36221,null,72442,"Alarm of unit 29","internal","BIT1","0, 1",null,"r","r"]
[null,36222,null,72444,"Alarm of unit 30","internal","BIT1","0, 1",null,"r","r"]
[null,36223,null,72446,"Alarm of unit 31","internal","BIT1","0, 1",null,"r","r"]
[]
["Ende"]