{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":134,"n_cols":76,"rows_kept":134,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","4.19.38.1","ups_newave_1_EstimatedMinutes","1号UPS电池剩余时间","1","0","0","1","0","cmd-1","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Min","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","1","0",{"$nulls":10},"0","0","10000","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["2","4.19.38.1","ups_newave_1_EstimatedCharge","1号UPS电池充电量","1","0","0","1","0","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["3","4.19.38.1","ups_newave_1_InputVoltageA","1号UPSA相输入电压","1","0","0","1","0","cmd-3","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["4","4.19.38.1","ups_newave_1_InputVoltageB","1号UPSB相输入电压","1","0","0","1","0","cmd-4","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["5","4.19.38.1","ups_newave_1_InputVoltageC","1号UPSC相输入电压","1","0","0","1","0","cmd-5","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["6","4.19.38.1","ups_newave_1_OutputVoltageA","1号UPSA相输出电压","1","0","0","1","0","cmd-6","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["7","4.19.38.1","ups_newave_1_OutputVoltageB","1号UPSB相输出电压","1","0","0","1","0","cmd-7","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["8","4.19.38.1","ups_newave_1_OutputVoltageC","1号UPSC相输出电压","1","0","0","1","0","cmd-8","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["9","4.19.38.1","ups_newave_1_OutputCurrentA","1号UPSA相输出电流","1","0","0","1","0","cmd-9","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["10","4.19.38.1","ups_newave_1_OutputCurrentB","1号UPSB相输出电流","1","0","0","1","0","cmd-10","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["11","4.19.38.1","ups_newave_1_OutputCurrentC","1号UPSC相输出电流","1","0","0","1","0","cmd-11","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["12","4.19.38.1","ups_newave_1_OutputLoadA","1号UPSA相输出负载","1","0","0","1","0","cmd-12","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["13","4.19.38.1","ups_newave_1_OutputLoadB","1号UPSB相输出负载","1","0","0","1","0","cmd-13","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["14","4.19.38.1","ups_newave_1_OutputLoadC","1号UPSC相输出负载","1","0","0","1","0","cmd-14","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["15","4.19.38.1","ups_newave_1_RectMnsInput","1号UPS整流器电源输入开关","1","0","0","1","0","cmd-15","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["16","4.19.38.1","ups_newave_1_BypMnsInput","1号UPS旁路电源输入开关","1","0","0","1","0","cmd-16","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["17","4.19.38.1","ups_newave_1_RectIsOn","1号UPS整流器工作","1","0","0","1","0","cmd-17","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["18","4.19.38.1","ups_newave_1_InvIsOn","1号UPS逆变器工作","1","0","0","1","0","cmd-18","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["19","4.19.38.1","ups_newave_1_BypIsOn","1号UPS旁路工作","1","0","0","1","0","cmd-19","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["20","4.19.38.1","ups_newave_1_BoosterIsOn","1号UPS助推器工作","1","0","0","1","0","cmd-20","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["21","4.19.38.1","ups_newave_1_BatteryIsCharging","1号UPS电池充电","1","0","0","1","0","cmd-21","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["22","4.19.38.1","ups_newave_1_BatteryIsDischar","1号UPS电池放电","1","0","0","1","0","cmd-22","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["23","4.19.38.1","ups_newave_1_BatteryIsLow","1号UPS电池低","1","0","0","1","0","cmd-23","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["24","4.19.38.1","ups_newave_1_OutputBreaker","1号UPS输出断路器(开/关)","1","0","0","1","0","cmd-24","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","3","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["25","4.19.38.1","ups_newave_1_MainsBypBreaker","1号UPS旁路电源断路器(开/关)","1","0","0","1","0","cmd-25","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["26","4.19.38.1","ups_newave_1_InvK2Breaker","1号UPS逆变K2断路器(开/关)","1","0","0","1","0","cmd-26","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["27","4.19.38.1","ups_newave_1_BatteryBreaker","1号UPS电池断路器(开/关)","1","0","0","1","0","cmd-27","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["28","4.19.38.1","ups_newave_1_RectInBreaker","1号UPS整流器输入断路器(开/关)","1","0","0","1","0","cmd-28","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["29","4.19.38.1","ups_newave_1_BypInBreaker","1号UPS旁路输入断路器(开/关)","1","0","0","1","0","cmd-29","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["30","4.19.38.1","ups_newave_1_LoadIsSupplied","1号UPS负载供电","1","0","0","1","0","cmd-30","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["31","4.19.38.1","ups_newave_1_UPSOutSwitch","1号UPS输出(开/关)","1","0","0","1","0","cmd-31","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["32","4.19.38.1","ups_newave_1_EcoMode","1号UPS电力模式(开/关)","1","0","0","1","0","cmd-32","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["33","4.19.38.1","ups_newave_1_EnergyMgnt","1号UPS能源管理(开/关)","1","0","0","1","0","cmd-33","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","3","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["34","4.19.38.1","ups_newave_1_GlobalParallelVal","1号UPS全局并联值","1","0","0","1","0","cmd-34","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["35","4.19.38.1","ups_newave_1_Buzzer","1号UPS蜂鸣器报警","1","0","0","1","0","cmd-35","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["36","4.19.38.1","ups_newave_1_GeneralAlarm","1号UPS一般报警","1","0","0","1","0","cmd-36","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["37","4.19.38.1","ups_newave_1_GenAlarm1","1号UPS一般报警1(0:正常 1:故障)","1","0","0","1","0","cmd-37","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["38","4.19.38.1","ups_newave_1_TempAlarm","1号UPS温度报警(0:正常 1:过高)","1","0","0","1","0","cmd-38","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["39","4.19.38.1","ups_newave_1_InputAlarm","1号UPS输入故障(0:正常 1:故障)","1","0","0","1","0","cmd-39","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["40","4.19.38.1","ups_newave_1_OutputAlarm","1号UPS输出故障(0:正常 1:故障)","1","0","0","1","0","cmd-40","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["41","4.19.38.1","ups_newave_1_OverLoadAlarm","1号UPS输出过载(0:正常 1:过载)","1","0","0","1","0","cmd-41","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["42","4.19.38.1","ups_newave_1_BypassBad","1号UPS旁路故障(0:正常 1:故障)","1","0","0","1","0","cmd-42","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["43","4.19.38.1","ups_newave_1_OutputSwitch","1号UPS输出状态(开/关)(0:开 1:关)","1","0","0","1","0","cmd-43","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["44","4.19.38.1","ups_newave_1_UPSShutDn","1号UPS关闭(0:开 1:关)","1","0","0","1","0","cmd-44","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["45","4.19.38.1","ups_newave_1_ChargerFault","1号UPS充电器故障(0:正常 1:故障)","1","0","0","1","0","cmd-45","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["46","4.19.38.1","ups_newave_1_SystemAlarm","1号UPS系统关闭(0:开 1:关)","1","0","0","1","0","cmd-46","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["47","4.19.38.1","ups_newave_1_FanFault","1号UPS风机故障(0:正常 1:故障)","1","0","0","1","0","cmd-47","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["48","4.19.38.1","ups_newave_1_FuseFault","1号UPS保险丝故障(0:正常 1:故障)","1","0","0","1","0","cmd-48","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["49","4.19.38.1","ups_newave_1_GeneralFault","1号UPS一般系统故障(0:正常 1:故障)","1","0","0","1","0","cmd-49","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["50","4.19.38.1","ups_newave_1_AwaitingPower","1号UPS等待电源(0:不等待 1:等待)","1","0","0","1","0","cmd-50","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["51","4.19.38.1","ups_newave_1_ShutdPending","1号UPS关机待定(0:不待定 1:待定)","1","0","0","1","0","cmd-51","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["52","4.19.38.1","ups_newave_1_ShutdImminent","1号UPS立即关机(0:不立即 1:立即)","1","0","0","1","0","cmd-52","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["53","4.19.38.1","ups_newave_1_AmbientTempAlarm","1号UPS环境温度报警(0:正常 1:过高/过低)","1","0","0","1","0","cmd-53","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["54","4.19.38.1","ups_newave_1_InverterTempAlarm","1号UPS逆变器温度报警(0:正常 1:过高/过低)","1","0","0","1","0","cmd-54","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["55","4.19.38.1","ups_newave_1_BypTempAlarm","1号UPS旁路温度报警(0:正常 1:过高/过低)","1","0","0","1","0","cmd-55","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["56","4.19.38.1","ups_newave_1_BatteryTempAlarm","1号UPS电池温度报警(0:正常 1:过高/过低)","1","0","0","1","0","cmd-56","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["57","4.19.38.1","ups_newave_1_InverterFault","1号UPS逆变器故障(0:正常 1:故障)","1","0","0","1","0","cmd-57","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["58","4.19.38.1","ups_newave_1_EmrgncyPwr","1号UPS应急电源(开/关)(0:关闭 1:开启)","1","0","0","1","0","cmd-58","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["59","4.19.38.1","ups_newave_1_BatteryGrndingErr","1号UPS电池接地错误(0:正常 1:故障)","1","0","0","1","0","cmd-59","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["60","4.19.38.1","ups_newave_1_BatteryBrk","1号UPS电池断路器(开/关)(0:关 1:开)","1","0","0","1","0","cmd-60","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["61","4.19.38.1","ups_newave_1_SyncError","1号UPS同步错误(0:正常 1:故障)","1","0","0","1","0","cmd-61","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["62","4.19.38.1","ups_newave_1_LossRedudancy","1号UPS冗余亏损错误(0:正常 1:流失)","1","0","0","1","0","cmd-62","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["63","4.19.38.1","ups_newave_1_GeneratorSwitch","1号UPS发电机状态(0:关 1:开)","1","0","0","1","0","cmd-63","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["64","4.19.38.1","ups_newave_1_BatteryCodt","1号UPS电池条件(0:良好 1:差 2:需要替换)","1","0","0","1","0","cmd-64","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","3","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["65","4.19.38.1","ups_newave_1_BatterySat","1号UPS电池状态(0:正常 1:电池低 2:电池耗尽)","1","0","0","1","0","cmd-65","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["66","4.19.38.1","ups_newave_1_OutputSource","1号UPS输出源(0:正常 1:电池输出 2:旁路在线)","1","0","0","1","0","cmd-66","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
[]
["1","4.19.38.2","ups_newave_2_EstimatedMinutes","2号UPS电池剩余时间","1","0","0","1","0","cmd-1","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Min","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","1","0",{"$nulls":10},"0","0","10000","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["2","4.19.38.2","ups_newave_2_EstimatedCharge","2号UPS电池充电量","1","0","0","1","0","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["3","4.19.38.2","ups_newave_2_InputVoltageA","2号UPSA相输入电压","1","0","0","1","0","cmd-3","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["4","4.19.38.2","ups_newave_2_InputVoltageB","2号UPSB相输入电压","1","0","0","1","0","cmd-4","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["5","4.19.38.2","ups_newave_2_InputVoltageC","2号UPSC相输入电压","1","0","0","1","0","cmd-5","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["6","4.19.38.2","ups_newave_2_OutputVoltageA","2号UPSA相输出电压","1","0","0","1","0","cmd-6","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["7","4.19.38.2","ups_newave_2_OutputVoltageB","2号UPSB相输出电压","1","0","0","1","0","cmd-7","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["8","4.19.38.2","ups_newave_2_OutputVoltageC","2号UPSC相输出电压","1","0","0","1","0","cmd-8","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["9","4.19.38.2","ups_newave_2_OutputCurrentA","2号UPSA相输出电流","1","0","0","1","0","cmd-9","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["10","4.19.38.2","ups_newave_2_OutputCurrentB","2号UPSB相输出电流","1","0","0","1","0","cmd-10","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["11","4.19.38.2","ups_newave_2_OutputCurrentC","2号UPSC相输出电流","1","0","0","1","0","cmd-11","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["12","4.19.38.2","ups_newave_2_OutputLoadA","2号UPSA相输出负载","1","0","0","1","0","cmd-12","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["13","4.19.38.2","ups_newave_2_OutputLoadB","2号UPSB相输出负载","1","0","0","1","0","cmd-13","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["14","4.19.38.2","ups_newave_2_OutputLoadC","2号UPSC相输出负载","1","0","0","1","0","cmd-14","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["15","4.19.38.2","ups_newave_2_RectMnsInput","2号UPS整流器电源输入开关","1","0","0","1","0","cmd-15","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["16","4.19.38.2","ups_newave_2_BypMnsInput","2号UPS旁路电源输入开关","1","0","0","1","0","cmd-16","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["17","4.19.38.2","ups_newave_2_RectIsOn","2号UPS整流器工作","1","0","0","1","0","cmd-17","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["18","4.19.38.2","ups_newave_2_InvIsOn","2号UPS逆变器工作","1","0","0","1","0","cmd-18","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["19","4.19.38.2","ups_newave_2_BypIsOn","2号UPS旁路工作","1","0","0","1","0","cmd-19","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["20","4.19.38.2","ups_newave_2_BoosterIsOn","2号UPS助推器工作","1","0","0","1","0","cmd-20","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["21","4.19.38.2","ups_newave_2_BatteryIsCharging","2号UPS电池充电","1","0","0","1","0","cmd-21","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["22","4.19.38.2","ups_newave_2_BatteryIsDischar","2号UPS电池放电","1","0","0","1","0","cmd-22","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["23","4.19.38.2","ups_newave_2_BatteryIsLow","2号UPS电池低","1","0","0","1","0","cmd-23","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["24","4.19.38.2","ups_newave_2_OutputBreaker","2号UPS输出断路器(开/关)","1","0","0","1","0","cmd-24","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","3","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["25","4.19.38.2","ups_newave_2_MainsBypBreaker","2号UPS旁路电源断路器(开/关)","1","0","0","1","0","cmd-25","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["26","4.19.38.2","ups_newave_2_InvK2Breaker","2号UPS逆变K2断路器(开/关)","1","0","0","1","0","cmd-26","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["27","4.19.38.2","ups_newave_2_BatteryBreaker","2号UPS电池断路器(开/关)","1","0","0","1","0","cmd-27","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["28","4.19.38.2","ups_newave_2_RectInBreaker","2号UPS整流器输入断路器(开/关)","1","0","0","1","0","cmd-28","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["29","4.19.38.2","ups_newave_2_BypInBreaker","2号UPS旁路输入断路器(开/关)","1","0","0","1","0","cmd-29","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["30","4.19.38.2","ups_newave_2_LoadIsSupplied","2号UPS负载供电","1","0","0","1","0","cmd-30","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["31","4.19.38.2","ups_newave_2_UPSOutSwitch","2号UPS输出(开/关)","1","0","0","1","0","cmd-31","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["32","4.19.38.2","ups_newave_2_EcoMode","2号UPS电力模式(开/关)","1","0","0","1","0","cmd-32","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["33","4.19.38.2","ups_newave_2_EnergyMgnt","2号UPS能源管理(开/关)","1","0","0","1","0","cmd-33","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","3","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["34","4.19.38.2","ups_newave_2_GlobalParallelVal","2号UPS全局并联值","1","0","0","1","0","cmd-34","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["35","4.19.38.2","ups_newave_2_Buzzer","2号UPS蜂鸣器报警","1","0","0","1","0","cmd-35","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["36","4.19.38.2","ups_newave_2_GeneralAlarm","2号UPS一般报警","1","0","0","1","0","cmd-36","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","告警,"]
["37","4.19.38.2","ups_newave_2_GenAlarm1","2号UPS一般报警1(0:正常 1:故障)","1","0","0","1","0","cmd-37","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["38","4.19.38.2","ups_newave_2_TempAlarm","2号UPS温度报警(0:正常 1:过高)","1","0","0","1","0","cmd-38","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["39","4.19.38.2","ups_newave_2_InputAlarm","2号UPS输入故障(0:正常 1:故障)","1","0","0","1","0","cmd-39","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["40","4.19.38.2","ups_newave_2_OutputAlarm","2号UPS输出故障(0:正常 1:故障)","1","0","0","1","0","cmd-40","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["41","4.19.38.2","ups_newave_2_OverLoadAlarm","2号UPS输出过载(0:正常 1:过载)","1","0","0","1","0","cmd-41","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["42","4.19.38.2","ups_newave_2_BypassBad","2号UPS旁路故障(0:正常 1:故障)","1","0","0","1","0","cmd-42","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["43","4.19.38.2","ups_newave_2_OutputSwitch","2号UPS输出状态(开/关)(0:开 1:关)","1","0","0","1","0","cmd-43","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["44","4.19.38.2","ups_newave_2_UPSShutDn","2号UPS关闭(0:开 1:关)","1","0","0","1","0","cmd-44","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["45","4.19.38.2","ups_newave_2_ChargerFault","2号UPS充电器故障(0:正常 1:故障)","1","0","0","1","0","cmd-45","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["46","4.19.38.2","ups_newave_2_SystemAlarm","2号UPS系统关闭(0:开 1:关)","1","0","0","1","0","cmd-46","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["47","4.19.38.2","ups_newave_2_FanFault","2号UPS风机故障(0:正常 1:故障)","1","0","0","1","0","cmd-47","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["48","4.19.38.2","ups_newave_2_FuseFault","2号UPS保险丝故障(0:正常 1:故障)","1","0","0","1","0","cmd-48","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["49","4.19.38.2","ups_newave_2_GeneralFault","2号UPS一般系统故障(0:正常 1:故障)","1","0","0","1","0","cmd-49","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["50","4.19.38.2","ups_newave_2_AwaitingPower","2号UPS等待电源(0:不等待 1:等待)","1","0","0","1","0","cmd-50","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["51","4.19.38.2","ups_newave_2_ShutdPending","2号UPS关机待定(0:不待定 1:待定)","1","0","0","1","0","cmd-51","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["52","4.19.38.2","ups_newave_2_ShutdImminent","2号UPS立即关机(0:不立即 1:立即)","1","0","0","1","0","cmd-52","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["53","4.19.38.2","ups_newave_2_AmbientTempAlarm","2号UPS环境温度报警(0:正常 1:过高/过低)","1","0","0","1","0","cmd-53","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["54","4.19.38.2","ups_newave_2_InverterTempAlarm","2号UPS逆变器温度报警(0:正常 1:过高/过低)","1","0","0","1","0","cmd-54","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["55","4.19.38.2","ups_newave_2_BypTempAlarm","2号UPS旁路温度报警(0:正常 1:过高/过低)","1","0","0","1","0","cmd-55","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["56","4.19.38.2","ups_newave_2_BatteryTempAlarm","2号UPS电池温度报警(0:正常 1:过高/过低)","1","0","0","1","0","cmd-56","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["57","4.19.38.2","ups_newave_2_InverterFault","2号UPS逆变器故障(0:正常 1:故障)","1","0","0","1","0","cmd-57","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["58","4.19.38.2","ups_newave_2_EmrgncyPwr","2号UPS应急电源(开/关)(0:关闭 1:开启)","1","0","0","1","0","cmd-58","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["59","4.19.38.2","ups_newave_2_BatteryGrndingErr","2号UPS电池接地错误(0:正常 1:故障)","1","0","0","1","0","cmd-59","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["60","4.19.38.2","ups_newave_2_BatteryBrk","2号UPS电池断路器(开/关)(0:关 1:开)","1","0","0","1","0","cmd-60","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["61","4.19.38.2","ups_newave_2_SyncError","2号UPS同步错误(0:正常 1:故障)","1","0","0","1","0","cmd-61","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["62","4.19.38.2","ups_newave_2_LossRedudancy","2号UPS冗余亏损错误(0:正常 1:流失)","1","0","0","1","0","cmd-62","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["63","4.19.38.2","ups_newave_2_GeneratorSwitch","2号UPS发电机状态(0:关 1:开)","1","0","0","1","0","cmd-63","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["64","4.19.38.2","ups_newave_2_BatteryCodt","2号UPS电池条件(0:良好 1:差 2:需要替换)","1","0","0","1","0","cmd-64","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","3","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["65","4.19.38.2","ups_newave_2_BatterySat","2号UPS电池状态(0:正常 1:电池低 2:电池耗尽)","1","0","0","1","0","cmd-65","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["66","4.19.38.2","ups_newave_2_OutputSource","2号UPS输出源(0:正常 1:电池输出 2:旁路在线)","1","0","0","1","0","cmd-66","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]