{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":45,"n_cols":76,"rows_kept":45,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","4.19.38.1","Ups1_A_InPhase","A相输入电压","101","4","0","1","0","cmd-1","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","4.19.38.1","Ups1_A_InCurr","A相输入电流","101","4","1","1","0","cmd-12","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","4.19.38.1","Ups1_InFreq","输入频率","101","4","1","1","0","cmd-15","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","4.19.38.1","Ups1_A_OutPhase","A相输出电压","101","4","1","1","0","cmd-4","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","4.19.38.1","Ups1_A_OutCurr","A相输出电流","101","4","1","1","0","cmd-7","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","4.19.38.1","Ups1_A_OutPower","A相输出有功功率","101","4","1","1","0","cmd-21","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","kw","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","4.19.38.1","Ups1_A_OutFreq","输出频率","101","4","1","1","0","cmd-11","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","4.19.38.1","Ups1_BattPhase","电池电压","101","4","1","1","0","cmd-10","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","4.19.38.1","Ups1_BattCurr","电池电流","101","4","1","1","0","cmd-20","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","4.19.38.1","Ups1_AOut_Load","A相输出负载百分比","101","4","1","1","0","cmd-27","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","4.19.38.1","Ups1_BOut_Load","B相输出负载百分比","101","4","1","1","0","cmd-28","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","4.19.38.1","Ups1_COut_Load","C相输出负载百分比","101","4","1","1","0","cmd-29","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","4.19.38.1","Ups1_BattContactFailure","电池接触器故障","2","1","1","1","0","cmd-69","type-1","0","5","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","4.19.38.1","Ups1_MainFuseStop","主路熔丝断","2","1","1","1","0","cmd-73","type-1","0","5","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","4.19.38.1","Ups1_ChargeFailure","充电器故障","2","1","1","1","0","cmd-95","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","4.19.38.1","Ups1_C_InPhase","C相输入电压","101","4","0","1","0","cmd-3","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","4.19.38.1","Ups1_B_InPhase","B相输入电压","101","4","0","1","0","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","4.19.38.1","Ups1_B_InCurr","B相输入电流","101","4","1","1","0","cmd-13","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","4.19.38.1","Ups1_C_InCurr","C相输入电流","101","4","1","1","0","cmd-14","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","4.19.38.1","Ups1_B_OutPhase","B相输出电压","101","4","1","1","0","cmd-5","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","4.19.38.1","Ups1_C_OutPhase","C相输出电压","101","4","1","1","0","cmd-6","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","4.19.38.1","Ups1_B_OutCurr","B相输出电流","101","4","1","1","0","cmd-8","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","4.19.38.1","Ups1_C_OutCurr","C相输出电流","101","4","1","1","0","cmd-9","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","4.19.38.1","Ups1_Battery_Remain_Time","电池后备时间","101","4","1","1","0","cmd-42","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hour","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","4.19.38.1","Ups1_BattTemp","电池温度","101","4","1","1","0","cmd-43","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","4.19.38.1","Ups1_BattChargeStatus","电池充电状态","1","1","1","1","0","cmd-47","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","4.19.38.1","Ups1_Pan_Fre","旁路频率","101","4","1","1","0","cmd-19","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","4.19.38.1","Ups1_Pan_A_Phase","旁路A相电压","101","4","1","1","0","cmd-16","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","4.19.38.1","Ups1_Pan_B_Phase","旁路B相电压","101","4","1","1","0","cmd-17","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","4.19.38.1","Ups1_Pan_C_Phase","旁路C相电压","101","4","1","1","0","cmd-18","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","4.19.38.1","Ups1_Supply_Power_Mode","供电方式","2","1","1","1","0","cmd-45","type-1","0","5","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","4.19.38.1","Ups1_Supply_Power","UPS供电方式","2","1","1","1","0","cmd-49","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","4.19.38.1","Ups1_In_Switch_Status","输入开关状态","2","1","1","1","0","cmd-51","type-1","0","5","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","4.19.38.1","Ups1_Repair_Pan_Switch_Status","维修旁路空开状态","2","1","1","1","0","cmd-52","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","4.19.38.1","Ups1_Pan_Switch_Status","旁路开关状态","2","1","1","1","0","cmd-53","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["36","4.19.38.1","Ups1_Main_Vol_Fault","主路电压异常","2","1","1","1","0","cmd-58","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["37","4.19.38.1","Ups1_Fan_Status","旁路情况","2","1","1","1","0","cmd-61","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["38","4.19.38.1","Ups1_Out_To_Pan","负载冲击转旁路","2","1","1","1","0","cmd-93","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["39","4.19.38.1","Ups1_Hurry_ShutDown","紧急关机","2","1","1","1","0","cmd-97","type-1","0","1","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["40","4.19.38.1","Ups1_Battery_status","蓄电池状态","2","1","1","1","0","cmd-62","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["41","4.19.38.1","Ups1_Battery_Temp_Upper","电池温度过高","2","1","1","1","0","cmd-98","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["42","4.19.38.1","Ups1_Battery_Life","蓄电池寿命情况","2","1","1","1","0","cmd-96","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["43","4.19.38.1","Ups1_B_OutPower","B相输出有功功率","101","4","1","1","0","cmd-22","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","kw","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["44","4.19.38.1","Ups1_C_OutPower","C相输出有功功率","101","4","1","1","0","cmd-23","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","kw","300","1","3","0","0","0","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]