{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":89,"n_cols":76,"rows_kept":89,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["27","4.19.136.1","LTS1_Src1_ALine_Vol","LTS1源1AB线电压","3","2","1","3","1000",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","4.19.136.1","LTS1_Src1_BLine_Vol","LTS1源1BC线电压","3","2","1","3","1001",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","4.19.136.1","LTS1_Src1_CLine_Vol","LTS1源1CA线电压","3","2","1","3","1002",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","4.19.136.1","LTS1_Src1_APhaseCurr","LTS源1A相电流","3","2","1","3","1003",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","4.19.136.1","LTS1_Src1_BPhaseCurr","LTS源1B相电流","3","2","1","3","1004",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","4.19.136.1","LTS1_Src1_CPhaseCurr","LTS源1C相电流","3","2","1","3","1005",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","4.19.136.1","LTS1_Src1_Freq","LTS源1频率","3","2","1","3","1006",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","4.19.136.1","LTS1_Src2_ALine_Vol","LTS1源2AB线电压","3","2","1","3","1007",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","4.19.136.1","LTS1_Src2_BLine_Vol","LTS1源2BC线电压","3","2","1","3","1008",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["36","4.19.136.1","LTS1_Src2_CLine_Vol","LTS1源2AC线电压","3","2","1","3","1009",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["37","4.19.136.1","LTS1_Src2_APhaseCurr","LTS源2A相电流","3","2","1","3","1010",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["38","4.19.136.1","LTS1_Src2_BPhaseCurr","LTS源2B相电流","3","2","1","3","1011",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["39","4.19.136.1","LTS1_Src2_CPhaseCurr","LTS源2C相电流","3","2","1","3","1012",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["40","4.19.136.1","LTS1_Src2_Freq","LTS源2频率","3","2","1","3","1013",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["41","4.19.136.1","LTS1_Out_ALineVol","LTS输出AB线电压","3","2","1","3","1015",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["42","4.19.136.1","LTS1_Out_BLineVol","LTS输出BC线电压","3","2","1","3","1016",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["43","4.19.136.1","LTS1_Out_CLineVol","LTS输出CA线电压","3","2","1","3","1017",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["44","4.19.136.1","LTS1_Out_APhase_Curr","LTS输出A相电流","3","2","1","3","1018",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["45","4.19.136.1","LTS1_Out_BPhase_Curr","LTS输出B相电流","3","2","1","3","1019",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["46","4.19.136.1","LTS1_Out_CPhase_Curr","LTS输出C相电流","3","2","1","3","1020",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["47","4.19.136.1","LTS1_Out_Freq","LTS输出频率","3","2","1","3","1021",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["48","4.19.136.1","LTS1_APhaseLoad","LTSA相负载百分比","3","2","1","3","1022",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["49","4.19.136.1","LTS1_BPhaseLoad","LTSB相负载百分比","3","2","1","3","1023",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["50","4.19.136.1","LTS1_CPhaseLoad","LTSC相负载百分比","3","2","1","3","1024",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["51","4.19.136.1","LTS1_Total_Kw","LTS总有功功率","3","2","1","3","1026",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["52","4.19.136.1","LTS1_Src1_SCR_Short","LTS源1晶闸管短路故障","3","2","1","3","1060",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","1","136",null,null,"0","1","1",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["53","4.19.136.1","LTS1_Src2_SCR_Short","LTS源2晶闸管短路故障","3","2","1","3","1060",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","2","136",null,null,"0","2","2",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["54","4.19.136.1","LTS1_Src1_SCR_Open","LTS源1晶闸管开路故障","3","2","1","3","1060",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","3","136",null,null,"0","3","3",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["55","4.19.136.1","LTS1_Src2_SCR_Open","LTS源2晶闸管开路故障","3","2","1","3","1060",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","4","136",null,null,"0","4","4",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["56","4.19.136.1","LTS1_Src1_UV_Fast","LTS源1快速欠压","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","3","136",null,null,"0","3","3",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["57","4.19.136.1","LTS1_Src1_UV_Slow","LTS源1慢速欠压","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","4","136",null,null,"0","4","4",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["58","4.19.136.1","LTS1_Src1_OverVol","LTS源1过压","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","5","136",null,null,"0","5","5",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["59","4.19.136.1","LTS1_Src1_FreqAbnormal","LTS源1频率异常","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","6","136",null,null,"0","6","6",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["60","4.19.136.1","LTS1_Src1_Abnormal","LTS源1异常","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","7","136",null,null,"0","7","7",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["61","4.19.136.1","LTS1_Src2_UV_Fast","LTS源2快速欠压","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","8","136",null,null,"0","8","8",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["62","4.19.136.1","LTS1_Src2_UV_Slow","LTS源2慢速欠压","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","9","136",null,null,"0","9","9",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["63","4.19.136.1","LTS1_Src2_OverVol","LTS源2过压","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","10","136",null,null,"0","10","10",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["64","4.19.136.1","LTS1_Src2_FreqAbnormal","LTS源2频率异常","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","11","136",null,null,"0","11","11",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["65","4.19.136.1","LTS1_Src2_Abnormal","LTS源2异常","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","12","136",null,null,"0","12","12",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["66","4.19.136.1","LTS1_Src1_OverCurr","LTS源1过流","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","13","136",null,null,"0","13","13",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["67","4.19.136.1","LTS1_Src2_OverCurr","LTS源2过流","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","14","136",null,null,"0","14","14",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["68","4.19.136.1","LTS1_Output_UnderVol","LTS输出欠压","3","2","1","3","1065",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","13","136",null,null,"0","13","13",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["69","4.19.136.1","LTS1_EmergencyShut","LTS紧急关机","3","2","1","3","1066",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","13","136",null,null,"0","13","13",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["51","4.19.136.1","LTS2_Src1_ALine_Vol","(gd)LTS2源1AB线电压","3","2","1","3","1000",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["52","4.19.136.1","LTS2_Src1_BLine_Vol","(gd)LTS2源1BC线电压","3","2","1","3","1001",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["53","4.19.136.1","LTS2_Src1_CLine_Vol","(gd)LTS2源1CA线电压","3","2","1","3","1002",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["54","4.19.136.1","LTS2_Src1_APhaseCurr","(gd)LTS源1A相电流","3","2","1","3","1003",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["55","4.19.136.1","LTS2_Src1_BPhaseCurr","(gd)LTS源1B相电流","3","2","1","3","1004",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["56","4.19.136.1","LTS2_Src1_CPhaseCurr","(gd)LTS源1C相电流","3","2","1","3","1005",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["57","4.19.136.1","LTS2_Src1_Freq","(gd)LTS源1频率","3","2","1","3","1006",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["58","4.19.136.1","LTS2_Src2_ALine_Vol","(gd)LTS2源2AB线电压","3","2","1","3","1007",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["59","4.19.136.1","LTS2_Src2_BLine_Vol","(gd)LTS2源2BC线电压","3","2","1","3","1008",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["60","4.19.136.1","LTS2_Src2_CLine_Vol","(gd)LTS2源2AC线电压","3","2","1","3","1009",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["61","4.19.136.1","LTS2_Src2_APhaseCurr","(gd)LTS源2A相电流","3","2","1","3","1010",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["62","4.19.136.1","LTS2_Src2_BPhaseCurr","(gd)LTS源2B相电流","3","2","1","3","1011",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["63","4.19.136.1","LTS2_Src2_CPhaseCurr","(gd)LTS源2C相电流","3","2","1","3","1012",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["64","4.19.136.1","LTS2_Src2_Freq","(gd)LTS源2频率","3","2","1","3","1013",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["65","4.19.136.1","LTS2_Out_ALineVol","(gd)LTS输出AB线电压","3","2","1","3","1015",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["66","4.19.136.1","LTS2_Out_BLineVol","(gd)LTS输出BC线电压","3","2","1","3","1016",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["67","4.19.136.1","LTS2_Out_CLineVol","(gd)LTS输出CA线电压","3","2","1","3","1017",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["68","4.19.136.1","LTS2_Out_APhase_Curr","(gd)LTS输出A相电流","3","2","1","3","1018",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["69","4.19.136.1","LTS2_Out_BPhase_Curr","(gd)LTS输出B相电流","3","2","1","3","1019",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["70","4.19.136.1","LTS2_Out_CPhase_Curr","(gd)LTS输出C相电流","3","2","1","3","1020",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["71","4.19.136.1","LTS2_Out_Freq","(gd)LTS输出频率","3","2","1","3","1021",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["72","4.19.136.1","LTS2_APhaseLoad","(gd)LTSA相负载百分比","3","2","1","3","1022",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["73","4.19.136.1","LTS2_BPhaseLoad","(gd)LTSB相负载百分比","3","2","1","3","1023",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["74","4.19.136.1","LTS2_CPhaseLoad","(gd)LTSC相负载百分比","3","2","1","3","1024",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["75","4.19.136.1","LTS2_Total_Kw","(gd)LTS总有功功率","3","2","1","3","1026",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["76","4.19.136.1","LTS2_BPhase_Kw","(gd)LTSB相有功功率","3","2","1","3","1033",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["77","4.19.136.1","LTS2_CPhase_Kw","(gd)LTSC相有功功率","3","2","1","3","1034",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["118","4.19.136.1","LTS2_Src1_SCR_Short","(gd)LTS源1晶闸管短路故障","3","2","1","3","1060",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","1","136",null,null,"0","1","1",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["119","4.19.136.1","LTS2_Src2_SCR_Short","(gd)LTS源2晶闸管短路故障","3","2","1","3","1060",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","2","136",null,null,"0","2","2",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["120","4.19.136.1","LTS2_Src1_SCR_Open","(gd)LTS源1晶闸管开路故障","3","2","1","3","1060",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","3","136",null,null,"0","3","3",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["121","4.19.136.1","LTS2_Src2_SCR_Open","(gd)LTS源2晶闸管开路故障","3","2","1","3","1060",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","4","136",null,null,"0","4","4",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["122","4.19.136.1","LTS2_Src1_UV_Fast","(gd)LTS源1快速欠压","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","3","136",null,null,"0","3","3",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["123","4.19.136.1","LTS2_Src1_UV_Slow","(gd)LTS源1慢速欠压","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","4","136",null,null,"0","4","4",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["124","4.19.136.1","LTS2_Src1_OverVol","(gd)LTS源1过压","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","5","136",null,null,"0","5","5",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["125","4.19.136.1","LTS2_Src1_FreqAbnormal","(gd)LTS源1频率异常","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","6","136",null,null,"0","6","6",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["126","4.19.136.1","LTS2_Src1_Abnormal","(gd)LTS源1异常","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","7","136",null,null,"0","7","7",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["127","4.19.136.1","LTS2_Src2_UV_Fast","(gd)LTS源2快速欠压","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","8","136",null,null,"0","8","8",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["128","4.19.136.1","LTS2_Src2_UV_Slow","(gd)LTS源2慢速欠压","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","9","136",null,null,"0","9","9",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["129","4.19.136.1","LTS2_Src2_OverVol","(gd)LTS源2过压","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","10","136",null,null,"0","10","10",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["130","4.19.136.1","LTS2_Src2_FreqAbnormal","(gd)LTS源2频率异常","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","11","136",null,null,"0","11","11",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["131","4.19.136.1","LTS2_Src2_Abnormal","(gd)LTS源2异常","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","12","136",null,null,"0","12","12",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["132","4.19.136.1","LTS2_Src1_OverCurr","(gd)LTS源1过流","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","13","136",null,null,"0","13","13",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["133","4.19.136.1","LTS2_Src2_OverCurr","(gd)LTS源2过流","3","2","1","3","1064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","14","136",null,null,"0","14","14",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["134","4.19.136.1","LTS2_Output_UnderVol","(gd)LTS输出欠压","3","2","1","3","1065",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","13","136",null,null,"0","13","13",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["135","4.19.136.1","LTS2_EmergencyShut","(gd)LTS紧急关机","3","2","1","3","1066",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","0","0","0","0","0","13","136",null,null,"0","13","13",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]