{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["变量dat文件","CSpreadSheetBackup"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":40,"n_cols":76,"rows_kept":40,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["346","4.30.185.1","RC_netmate_BatteryPowerSupplyTimeleft","UPS电池供电剩余时间","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.26.0","public","0","0","0","0","0","0","0","0","0","Min","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["347","4.30.185.1","RC_netmate_BatteryVol","UPS电池电压","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.29.0","public","0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["348","4.30.185.1","RC_netmate_BatteryCurr","UPS电池电流","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.30.0","public","0","0","0","0","0","0","0","0","0","A","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["349","4.30.185.1","RC_netmate_UPSTemperature","UPS温度","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.75.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["350","4.30.185.1","RC_netmate_line1InputFrequency","UPS线1输入频率","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.34.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["351","4.30.185.1","RC_netmate_line1InputVoltage","UPS线1输入电压","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.35.0","public","0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["352","4.30.185.1","RC_netmate_line1InputCurrent","UPS线1输入电流","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.36.0","public","0","0","0","0","0","0","0","0","0","A","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["353","4.30.185.1","RC_netmate_line2InputVoltage","UPS线2输入电压","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.39.0","public","0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["354","4.30.185.1","RC_netmate_line2InputCurrent","UPS线2输入电流","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.40.0","public","0","0","0","0","0","0","0","0","0","A","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["355","4.30.185.1","RC_netmate_line3InputVoltage","UPS线3输入电压","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.43.0","public","0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["356","4.30.185.1","RC_netmate_line3InputCurrent","UPS线3输入电流","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.44.0","public","0","0","0","0","0","0","0","0","0","A","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["357","4.30.185.1","RC_netmate_line1OutputVoltage","UPS线1输出电压","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.49.0","public","0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["358","4.30.185.1","RC_netmate_line1OutputCurrent","UPS线1输出电流","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.50.0","public","0","0","0","0","0","0","0","0","0","A","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["359","4.30.185.1","RC_netmate_line1OutputPower","UPS线1输出功率","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.51.0","public","0","0","0","0","0","0","0","0","0","Kw","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["360","4.30.185.1","RC_netmate_line1OutputLoad","UPS线1输出负载百分比","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.52.0","public","0","0","0","0","0","0","0","0","0","%","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["361","4.30.185.1","RC_netmate_line2OutputVoltage","UPS线2输出电压","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.53.0","public","0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["362","4.30.185.1","RC_netmate_line2OutputCurrent","UPS线2输出电流","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.54.0","public","0","0","0","0","0","0","0","0","0","A","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["363","4.30.185.1","RC_netmate_line2OutputPower","UPS线2输出功率","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.55.0","public","0","0","0","0","0","0","0","0","0","Kw","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["364","4.30.185.1","RC_netmate_line2OutputLoad","UPS线2输出负载百分比","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.56.0","public","0","0","0","0","0","0","0","0","0","%","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["365","4.30.185.1","RC_netmate_line3OutputVoltage","UPS线3输出电压","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.57.0","public","0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["366","4.30.185.1","RC_netmate_line3OutputCurrent","UPS线3输出电流","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.58.0","public","0","0","0","0","0","0","0","0","0","A","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["367","4.30.185.1","RC_netmate_line3OutputPower","UPS线3输出功率","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.59.0","public","0","0","0","0","0","0","0","0","0","Kw","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["368","4.30.185.1","RC_netmate_line3OutputLoad","UPS线3输出负载百分比","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.60.0","public","0","0","0","0","0","0","0","0","0","%","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["369","4.30.185.1","RC_netmate_line1BypassVoltage","UPS线1旁路电压","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.63.0","public","0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["370","4.30.185.1","RC_netmate_line1BypassCurrent","UPS线1旁路电流","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.64.0","public","0","0","0","0","0","0","0","0","0","A","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["371","4.30.185.1","RC_netmate_line2BypassVoltage","UPS线2旁路电压","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.66.0","public","0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["372","4.30.185.1","RC_netmate_line2BypassCurrent","UPS线2旁路电流","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.67.0","public","0","0","0","0","0","0","0","0","0","A","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["373","4.30.185.1","RC_netmate_line3BypassVoltage","UPS线3旁路电压","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.69.0","public","0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["374","4.30.185.1","RC_netmate_line3BypassCurrent","UPS线3旁路电流","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.1.70.0","public","0","0","0","0","0","0","0","0","0","A","900","0.0099999998","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["375","4.30.185.1","RC_netmate_TemperatureStatus","UPS温度状态","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.2.17.0","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["376","4.30.185.1","RC_netmate_InputStatus","UPS输入故障状态","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.2.18.0","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["377","4.30.185.1","RC_netmate_OutputStatus","UPS输出故障状态","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.2.19.0","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["378","4.30.185.1","RC_netmate_OverLoadStatus","UPS过载状态","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.2.20.0","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["379","4.30.185.1","RC_netmate_BypassStatus","UPS旁路状态","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.2.21.0","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["380","4.30.185.1","RC_netmate_ChargeStatus","UPS充电故障状态","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.2.24.0","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["381","4.30.185.1","RC_netmate_FanStatus","UPS风扇故障状态","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.2.26.0","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["382","4.30.185.1","RC_netmate_FuseStatus","UPS熔丝故障状态","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.2.27.0","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["383","4.30.185.1","RC_netmate_BatteryStatus","UPS电池故障状态","1","0","0","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.2350.1.1.2.33.0","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","185",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["415","4.30.185.1","RC_netmate_1","UPS通信","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]

{"sheet":"CSpreadSheetBackup","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}