{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":84,"n_cols":9,"rows_kept":84,"flags":["formulas_cached_only"]}
["序号","分类","变量名","变量类型","UID号","状态","权限（读写）","中文描述","英文描述"]
["1","airIRRCGroupStatus","airIRRCGroupStatusCoolOutput","数据量","1.3.6.1.4.1.318.1.1.13.3.2.1.1.1",null,"ReadOnly","制冷量","Group coolant output in tenths of kW"]
["2",null,"airIRRCGroupStatusCoolDemand","数据量","1.3.6.1.4.1.318.1.1.13.3.2.1.1.2",null,"ReadOnly","冷却剂需求量","Group coolant demand in tenths of kW."]
["3",null,"airIRRCGroupStatusAirFlowUS","数据量","1.3.6.1.4.1.318.1.1.13.3.2.1.1.3",null,"ReadOnly","每分钟送风量","Group air flow in cubic feet per minute."]
["4",null,"airIRRCGroupStatusAirFlowMetric","数据量","1.3.6.1.4.1.318.1.1.13.3.2.1.1.4",null,"ReadOnly","每秒送风量","Group air flow in liters per second"]
["5",null,"airIRRCGroupStatusMaxRackInletTempUS ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.1.1.5",null,"ReadOnly","最大机架温度（华氏度）","Group maximum rack inlet temperature in tenths of degrees Fahrenheit"]
["6",null,"airIRRCGroupStatusMaxRackInletTempMetric","数据量","1.3.6.1.4.1.318.1.1.13.3.2.1.1.6",null,"ReadOnly","最大机架温度（摄氏度）","Group maximum rack inlet temperature in tenths of degrees Celsius"]
["7",null,"airIRRCGroupStatusMinRackInletTempUS","数据量","1.3.6.1.4.1.318.1.1.13.3.2.1.1.7",null,"ReadOnly","最小机架温度（华氏度）","Group minimum rack inlet temperature in tenths of degrees Fahrenheit."]
["8",null,"airIRRCGroupStatusMinRackInletTempMetric","数据量","1.3.6.1.4.1.318.1.1.13.3.2.1.1.8",null,"ReadOnly","最小机架温度（摄氏度）","Group minimum rack inlet temperature in tenths of degrees Celsius"]
["9","airIRRCGroupSetpoints ","airIRRCGroupSetpointsCoolUS","数据量","1.3.6.1.4.1.318.1.1.13.3.2.1.2.1",null,"ReadWrite","制冷设定点（华氏度）","Group cooling setpoint in tenths of degrees Fahrenheit"]
["10",null,"airIRRCGroupSetpointsCoolMetric ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.1.2.2",null,"ReadWrite","制冷设定点（摄氏度）","Group cooling setpoint in tenths of degrees Celsius"]
["11",null,"airIRRCGroupSetpointsSupplyAirUS","数据量","1.3.6.1.4.1.318.1.1.13.3.2.1.2.3",null,"ReadWrite","送风温度设定点（华氏度）","Group supply air setpoint in tenths of degrees Fahrenheit"]
["12",null,"airIRRCGroupSetpointsSupplyAirMetric ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.1.2.4",null,"ReadWrite","送风温度设定点（摄氏度）","Group supply air setpoint in tenths of degrees Celsius"]
["13",null,"airIRRCGroupSetpointsFanSpeedPreference","状态量","1.3.6.1.4.1.318.1.1.13.3.2.1.2.5","low (1)\nmed-low (2)\nmed (3)\nmed-high (4)\nhigh (5)","ReadWrite","风扇转速设定","The preferred fan speed setting"]
["14","airIRRCGroupConfig ","airIRRCGroupConfigNumberofCoolingUnits","数据量","1.3.6.1.4.1.318.1.1.13.3.2.1.3.1","\n","ReadWrite","机组冷却值","The number of cooling units present in the group"]
["15",null,"airIRRCGroupConfigConfigurationType ","状态量","1.3.6.1.4.1.318.1.1.13.3.2.1.3.2","racs (1)\nhacs (2)\nin-row (3)","ReadWrite","机组配置类型","The group configuration type"]
["16",null,"airIRRCGroupConfigPctGlycol ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.1.3.3",null,"ReadWrite","乙醇含量","The glycol mixture in percent"]
["17",null,"airIRRCGroupConfigCoolGainP ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.1.3.4",null,"ReadWrite","增益组件","The gain component of the PID in hundredths"]
["18",null,"airIRRCGroupConfigCoolResetRateI ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.1.3.5",null,"ReadWrite","PID控制","The integral component of the PID in hundredths"]
["19",null,"airIRRCGroupConfigCoolDerivativeD ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.1.3.6",null,"ReadWrite","PID","The derivative component of the PID in hundredths"]
["20",null,"airIRRCGroupConfigMaxFanSpeed ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.1.3.7",null,"ReadWrite","最高理想风扇转速","The maximum desired fan speed setting in percent"]
["21","airIRRCUnitIdent ","airIRRCUnitIdentID ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.1.1",null,"ReadWrite","识别码","The unit identification number"]
["22",null,"airIRRCUnitIdentName ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.1.2",null,"ReadWrite","名称","A character string identifying the unit name"]
["23",null,"airIRRCUnitIdentLocation ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.1.3",null,"ReadWrite","位置","A character string identifying the unit location"]
["24",null,"airIRRCUnitIdentModelNumber ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.1.4",null,"ReadOnly","模块号","A character string identifying the unit model number"]
["25",null,"airIRRCUnitIdentSerialNumber ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.1.5",null,"ReadOnly","序列号","A character string identifying the unit serial number"]
["26",null,"airIRRCUnitIdentFirmwareRevision ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.1.6",null,"ReadOnly","硬件版本","A character string identifying the unit firmware version"]
["27",null,"airIRRCUnitIdentHardwareRevision ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.1.7",null,"ReadOnly","硬件升级","A character string identifying the unit controller hardware revision"]
["28",null,"airIRRCUnitIdentManufactureDate ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.1.8",null,"ReadOnly","生产日期","A character string identifying the unit manufacture date"]
["29","airIRRCUnitStatus ","airIRRCUnitStatusOperateMode ","状态量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.1","standby (1)\non (2)\nidle (3)\n","ReadOnly","制冷运行模式","The cooling unit operating mode"]
["30",null,"airIRRCUnitStatusCoolOutput ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.2",null,"ReadOnly","制冷量","The unit cooling output in tenths of kW"]
["31",null,"airIRRCUnitStatusCoolDemand ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.3",null,"ReadOnly","冷却剂需求量","The unit cooling demand in tenths of kW"]
["32",null,"airIRRCUnitStatusAirFlowUS ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.4",null,"ReadOnly","每分钟送风量","The unit air flow in cubic feet per minute"]
["33",null,"airIRRCUnitStatusAirFlowMetric ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.5",null,"ReadOnly","每秒送风量","The unit air flow in hundredths of liters per second."]
["34",null,"airIRRCUnitStatusRackInletTempUS ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.6",null,"ReadOnly","机架温度（华氏度）","The unit rack inlet temperature in tenths of degrees Fahrenheit"]
["35",null,"airIRRCUnitStatusRackInletTempMetric ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.7",null,"ReadOnly","机架温度（摄氏度）","The unit rack inlet temperature in tenths of degrees Celsius"]
["36",null,"airIRRCUnitStatusSupplyAirTempUS ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.8",null,"ReadOnly","送风温度（华氏度）","The unit supply air temperature in tenths of degrees Fahrenheit"]
["37",null,"airIRRCUnitStatusSupplyAirTempMetric ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.9",null,"ReadOnly","送风温度（摄氏度）","The unit supply air temperature in tenths of degrees Celsius"]
["38",null,"airIRRCUnitStatusReturnAirTempUS ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.10",null,"ReadOnly","回风温度（华氏度）","The unit return air temperature in tenths of degrees Fahrenheit"]
["39",null,"airIRRCUnitStatusReturnAirTempMetric ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.11",null,"ReadOnly","回风温度（摄氏度）","The unit return air temperature in tenths of degrees Celsius"]
["40",null,"airIRRCUnitStatusContainmtDPUS ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.12",null,"ReadOnly","水压差","The unit containment differential pressure in hundredths of inches of water"]
["41",null,"airIRRCUnitStatusContainmtDPMetric ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.13",null,"ReadOnly","水压","The unit containment differential pressure in Pa"]
["42",null,"airIRRCUnitStatusFilterDPUS ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.14",null,"ReadOnly","空气过滤器水下压强","The unit air filter differential pressure in hundredths of inches of water"]
["43",null,"airIRRCUnitStatusFilterDPMetric ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.15",null,"ReadOnly","空气过滤器压强","The unit air filter differential pressure in Pa"]
["44",null,"airIRRCUnitStatusFanSpeed ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.16",null,"ReadOnly","风扇转速","The unit average fan speed in tenths of percent"]
["45",null,"airIRRCUnitStatusInputState ","状态量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.17","open (1)\nclosed (2)\n","ReadOnly","输入连接状态","The state of the input contact"]
["46",null,"airIRRCUnitStatusOutputState ","状态量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.18","open (1)\nclosed (2)\n","ReadOnly","输出继电器状态","The state of the output relay"]
["47",null,"airIRRCUnitStatusActivePowerSource ","状态量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.19","sourceA (1)\nsourceB (2)\n","ReadOnly","供电单元","The power source that is powering the unit"]
["48",null,"airIRRCUnitStatusFluidValvePosition ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.20",null,"ReadOnly","液体阀","The fluid valve position in percent open"]
["49",null,"airIRRCUnitStatusFluidFlowUS ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.21",null,"ReadOnly","每分钟水流量","The fluid flow in tenths of gallons per minute"]
["50",null,"airIRRCUnitStatusFluidFlowMetric ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.22",null,"ReadOnly","每秒水流量","The fluid flow in hundredths of liters per second"]
["51",null,"airIRRCUnitStatusEnteringFluidTemperatureUS ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.23",null,"ReadOnly","进水温度（华氏度）","The temperature of the entering fluid in tenths of degrees Fahrenheit"]
["52",null,"airIRRCUnitStatusEnteringFluidTemperatureMetric ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.24",null,"ReadOnly","进水温度（摄氏度）","The temperature of the entering fluid in tenths of degrees Celsius"]
["53",null,"airIRRCUnitStatusLeavingFluidTemperatureUS ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.25",null,"ReadOnly","出水温度（华氏度）","The temperature of the Leaving fluid in tenths of degrees Fahrenheit"]
["54",null,"airIRRCUnitStatusLeavingFluidTemperatureMetric ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.2.26",null,"ReadOnly","出水温度（摄氏度）","The temperature of the Leaving fluid in tenths of degrees Celsius"]
["55","airIRRCUnitRunHours","airIRRCUnitRunHoursAirFilter ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.3.1",null,"ReadOnly","空气过滤器机组运行时间","Unit air filter run hours"]
["56",null,"airIRRCUnitRunHoursFan1 ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.3.2",null,"ReadOnly","风扇1运行时间","Unit fan 1 run hours"]
["57",null,"airIRRCUnitRunHoursFan2 ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.3.3",null,"ReadOnly","风扇2运行时间","Unit fan 2 run hours"]
["58",null,"airIRRCUnitRunHoursFan3","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.3.4",null,"ReadOnly","风扇3运行时间","Unit fan 3 run hours"]
["59",null,"airIRRCUnitRunHoursFan4","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.3.5",null,"ReadOnly","风扇4运行时间","Unit fan 4 run hours"]
["60",null,"airIRRCUnitRunHoursFan5","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.3.6",null,"ReadOnly","风扇5运行时间","Unit fan 5 run hours"]
["61",null,"airIRRCUnitRunHoursFan6","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.3.7",null,"ReadOnly","风扇6运行时间","Unit fan 6 run hours"]
["62",null,"airIRRCUnitRunHoursFan7","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.3.8",null,"ReadOnly","风扇7运行时间","Unit fan 7 run hours"]
["63",null,"airIRRCUnitRunHoursFan8","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.3.9",null,"ReadOnly","风扇8运行时间","Unit fan 8 run hours"]
["64",null,"airIRRCUnitRunHoursFanPowerSupplyLeft ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.3.10",null,"ReadOnly",null,"Unit fan left power supply run hours"]
["65",null,"airIRRCUnitRunHoursFanPowerSupplyRight ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.3.11",null,"ReadOnly",null,"Unit fan right power supply run hours"]
["66",null,"airIRRCUnitRunHoursCondensatePump ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.3.12",null,"ReadOnly","机组凝水泵运行时间","Unit condensate pump run hours"]
["67","airIRRCUnitServiceIntervals ","airIRRCUnitServiceIntervalsAirFilter ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.4.1",null,"ReadWrite","空气过滤器服务区间","Air filter service interval in weeks"]
["68",null,"airIRRCUnitServiceIntervalsAirFilterAlarm ","状态量","1.3.6.1.4.1.318.1.1.13.3.2.2.4.2","enable (1)\ndisable (2)","ReadWrite","空气过滤器服务区间报警启用/禁用","The air filter service interval alarm enable/disable"]
["69","airIRRCUnitThresholds ","airIRRCUnitThresholdsRackInletHighTempUS ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.5.1",null,"ReadWrite","机架进气高温阀值（华氏度）","Unit rack inlet air high temperature threshold in tenths of degrees Fahrenheit"]
["70",null,"airIRRCUnitThresholdsRackInletHighTempMetric ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.5.2",null,"ReadWrite","机架进气高温阀值（摄氏度）","Unit rack inlet air high temperature threshold in tenths of degrees Celsius"]
["71",null,"airIRRCUnitThresholdsSupplyAirHighTempUS ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.5.3",null,"ReadWrite","送风高温阈值（华氏度）","Unit supply air high temperature threshold in tenths of degrees Fahrenheit"]
["72",null,"airIRRCUnitThresholdsSupplyAirHighTempMetric ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.5.4",null,"ReadWrite","送风高温阈值（摄氏度）","Unit supply air high temperature threshold in tenths of degrees Celsius"]
["73",null,"airIRRCUnitThresholdsReturnAirHighTempUS ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.5.5",null,"ReadWrite","回风高温阀值（华氏度）","Unit return air high temperature threshold in tenths of degrees Fahrenheit"]
["74",null,"airIRRCUnitThresholdsReturnAirHighTempMetric ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.5.6",null,"ReadWrite","回风高温阀值（摄氏度）","Unit return air high temperature threshold in tenths of degrees Celsius"]
["75",null,"airIRRCUnitThresholdsEnteringFluidHighTempUS ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.5.7",null,"ReadWrite","进水高温阀值（华氏度）","Unit entering fluid high temperature threshold in tenths of degrees Fahrenheit"]
["76",null,"airIRRCUnitThresholdsEnteringFluidHighTempMetric ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.5.8",null,"ReadWrite","进水高温阀值（摄氏度）","Unit incoming fluid high temperature threshold in tenths of degrees Celsius"]
["77","airIRRCUnitConfig ","airIRRCUnitConfigCoolCapacity ","状态量","1.3.6.1.4.1.318.1.1.13.3.2.2.6.1","automatic (1)\nmaximum (2)","ReadWrite","冷却容量选择设置","The cooling capacity options setting"]
["78",null,"airIRRCUnitConfigStartupDelay ","数据量","1.3.6.1.4.1.318.1.1.13.3.2.2.6.2",null,"ReadWrite","启动延时（秒）","The startup delay in seconds"]
["79",null,"airIRRCUnitConfigIdleOnLeakDetect ","状态量","1.3.6.1.4.1.318.1.1.13.3.2.2.6.3","yes (1)\nno (2)","ReadWrite","空闲泄露选项设置","The idle on leak options setting"]
[null,null,"airIRRCUnitConfigPowerSource ","状态量","1.3.6.1.4.1.318.1.1.13.3.2.2.6.4","sourceA (1)\nsourceB (2)\nsourceAandB (3)","ReadWrite","配置电源状态","The configured power source of the unit"]
[null,null,"airIRRCUnitConfigInputNormalState ","状态量","1.3.6.1.4.1.318.1.1.13.3.2.2.6.5","open (1)\nclosed (2)","ReadWrite","输入状态","The normal state of the input contact"]
[null,null,"airIRRCUnitConfigOutputNormalState ","状态量","1.3.6.1.4.1.318.1.1.13.3.2.2.6.6","open (1)\nclosed (2)","ReadWrite","输出状态","The normal state of the output r"]
[null,null,"airIRRCUnitConfigOutputSource ","状态量","1.3.6.1.4.1.318.1.1.13.3.2.2.6.7","anyAlarm (1)\ncriticalAlarm (2)","ReadWrite","继电器的输出变化的根源","The source of output relay change"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}