{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":36,"n_cols":76,"rows_kept":36,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","6.35.136.1","Air_Out1_In1_Power_Set","机组1_1号内机开关机","4","2","1","5","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","1","1","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","6.35.136.1","Air_Out1_In2_Power_Set","机组1_2号内机开关机","4","2","1","5","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","1","1","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.35.136.1","Air_Out1_In3_Power_Set","机组1_3号内机开关机","4","2","1","5","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","1","1","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.35.136.1","Air_Out1_In1_WorkMode","机组1_1号内机工作模式","4","2","1","4","6078",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.35.136.1","Air_Out1_In1_FanSpeed","机组1_1号内机风速","4","2","1","4","6076",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.35.136.1","Air_Out1_In1_ReturnAir_Temp","机组1_1号内机回风温度","4","2","1","4","6073",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.35.136.1","Air_Out1_In1_Temp_Set","机组1_1号内机温度设置","4","2","1","6","3003",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","1","1","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.35.136.1","Air_Out1_In2_WorkMode","机组1_2号内机工作模式","4","2","1","4","6091",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.35.136.1","Air_Out1_In2_FanSpeed","机组1_2号内机风速","4","2","1","4","6089",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.35.136.1","Air_Out1_In2_ReturnAirTemp","机组1_2号内机回风温度","4","2","1","4","6086",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","6.35.136.1","Air_Out1_In2_Temp_Set","机组1_2号内机温度设置","4","2","1","6","3011",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","1","1","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","6.35.136.1","Air_Out1_In3_WorkMode","机组1_3号内机工作模式","4","2","1","4","6104",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","6.35.136.1","Air_Out1_In3_FanSpeed","机组1_3号内机风速","4","2","1","4","6102",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","6.35.136.1","Air_Out1_In3_ReturnAirTemp","机组1_3号内机回风温度","4","2","1","4","6099",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","6.35.136.1","Air_Out1_In3_Temp_Set","机组1_3号内机温度设置","4","2","1","6","3019",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","1","1","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","6.35.136.1","Air_Out1_In1_Commucation_Alarm","机组1_1号内机通讯故障","4","2","1","4","6022",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","1","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","6.35.136.1","Air_Out1_In2_Commucation_Alarm","机组1_2号内机通讯故障","4","2","1","4","6022",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","2","136",null,null,"0","1","1",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","6.35.136.1","Air_Out1_In3_Commucation_Alarm","机组1_3号内机通讯故障","4","2","1","4","6022",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","3","136",null,null,"0","2","2",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","6.35.136.1","Air_Out1_In1_Sys1_High_Pressure","机组1_1号内机系统1高压故障","4","2","1","4","6079",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","1","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","6.35.136.1","Air_Out1_In1_Sys1_Low_Pressure","机组1_1号内机系统1低压故障","4","2","1","4","6079",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","2","136",null,null,"0","1","1",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","6.35.136.1","Air_Out1_In1_Sys1_Over","机组1_1号内机系统1过载","4","2","1","4","6079",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","3","136",null,null,"0","2","2",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","6.35.136.1","Air_Out1_In1_Sys2_Low_Pressure","机组1_1号内机系统2低压故障","4","2","1","4","6079",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","4","136",null,null,"0","3","3",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","6.35.136.1","Air_Out1_In1_Sys2_High_Pressure","机组1_1号内机系统2高压故障","4","2","1","4","6079",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","5","136",null,null,"0","4","4",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","6.35.136.1","Air_Out1_In1_Sys2_Over","机组1_1号内机系统2过载","4","2","1","4","6079",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","6","136",null,null,"0","5","5",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","6.35.136.1","Air_Out1_In1_Sys2_WaterTemp_High","机组1_1号内机系统2水温过高","4","2","1","4","6079",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","7","136",null,null,"0","6","6",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","6.35.136.1","Air_Out1_In1_WaterFlowCut","机组1_1号内机水流开关断开","4","2","1","4","6079",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","11","136",null,null,"0","10","10",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","6.35.136.1","Air_Out1_In1_LevelSwitchFault","机组1_1号内机水位开关故障","4","2","1","4","6079",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","13","136",null,null,"0","12","12",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","6.35.136.1","Air_Out1_In1_Sys1_WaterTemp_High","机组1_1号内机系统1水温过高","4","2","1","4","6079",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","14","136",null,null,"0","13","13",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","6.35.136.1","Air_Out1_In1_Sys1_Refri_Leak","机组1_1号内机系统1冷媒泄漏","4","2","1","4","6079",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","15","136",null,null,"0","14","14",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","6.35.136.1","Air_Out1_In1_Sys2_Refri_Leak","机组1_1号内机系统2冷媒泄漏","4","2","1","4","6079",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","16","136",null,null,"0","15","15",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","6.35.136.1","Air_Out1_In1_Temp","机组1_1号内机温度","4","2","1","3","3003",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","6.35.136.1","Air_Out1_In2_Temp","机组1_2号内机温度","4","2","1","3","3011",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","6.35.136.1","Air_Out1_In3_Temp","机组1_3号内机温度","4","2","1","3","3019",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["50","6.35.136.1","Air_Out1_In2_Power_Status","机组1_2号内机状态","1","1","1","1","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["51","6.35.136.1","Air_Out1_In3_Power_Status","机组1_3号内机状态","1","1","1","1","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]