{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":86,"n_cols":76,"rows_kept":86,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
[null,"Liebert PEX版本:PAL 1.04.026.STD"]
["1","6.16.109.1","PexNum1_TempSetPoint","1号空调温度设定点","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.1.0","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","6.16.109.1","PexNum1_TempMeasurement","1号空调温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.3.1.3.1","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.16.109.1","PexNum1_TempDailyHigh","1号空调日最高温","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.3.1.7.1","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.16.109.1","PexNum1_TempDailyLow","1号空调日最低温","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.3.1.8.1","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.16.109.1","PexNum1_HumiditySetPoint","1号空调湿度设定点","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.1.0","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.16.109.1","PexNum1_HumidityMeasurement","1号空调湿度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.3.1.3.1","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.16.109.1","PexNum1_HumidityDailyHigh","1号空调日最高湿度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.3.1.7.1","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.16.109.1","PexNum1_HumidityDailyLow","1号空调日最低湿度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.3.1.8.1","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.16.109.1","PexNum1_StateCooling","1号空调制冷状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.2.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","8","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.16.109.1","PexNum1_StateDehumidify","1号空调除湿状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.5.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","6.16.109.1","PexNum1_StateFan","1号空调风机状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.7.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","6.16.109.1","PexNum1_StateHotWater","1号空调热水器状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.22.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","6.16.109.1","PexNum1_StateSystem","1号空调系统状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.1.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","2,","报警,"]
["14","6.16.109.1","PexNum1_StateElectricHeater","1号空调电加热器状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.21.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","6.16.109.1","PexNum1_StateHumidify","1号空调加湿器状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.4.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","6.16.109.1","PexNum1_Communications","1号空调通讯状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","8","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
[]
["18","6.16.109.2","PexNum2_TempSetPoint","2号空调温度设定点","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.1.0","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","6.16.109.2","PexNum2_TempMeasurement","2号空调温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.3.1.3.1","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","6.16.109.2","PexNum2_TempDailyHigh","2号空调日最高温","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.3.1.7.1","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","6.16.109.2","PexNum2_TempDailyLow","2号空调日最低温","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.3.1.8.1","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","6.16.109.2","PexNum2_HumiditySetPoint","2号空调湿度设定点","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.1.0","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","6.16.109.2","PexNum2_HumidityMeasurement","2号空调湿度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.3.1.3.1","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","6.16.109.2","PexNum2_HumidityDailyHigh","2号空调日最高湿度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.3.1.7.1","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","6.16.109.2","PexNum2_HumidityDailyLow","2号空调日最低湿度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.3.1.8.1","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","6.16.109.2","PexNum2_StateCooling","2号空调制冷状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.2.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","8","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","6.16.109.2","PexNum2_StateDehumidify","2号空调除湿状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.5.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","6.16.109.2","PexNum2_StateFan","2号空调风机状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.7.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","6.16.109.2","PexNum2_StateHotWater","2号空调热水器状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.22.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","6.16.109.2","PexNum2_StateSystem","2号空调系统状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.1.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","2,","报警,"]
["31","6.16.109.2","PexNum2_StateElectricHeater","2号空调电加热器状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.21.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","6.16.109.2","PexNum2_StateHumidify","2号空调加湿器状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.4.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","6.16.109.2","PexNum2_Communications","2号空调通讯状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","8","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
[]
["18","6.16.109.3","PexNum3_TempSetPoint","3号空调温度设定点","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.1.0","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","6.16.109.3","PexNum3_TempMeasurement","3号空调温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.3.1.3.1","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","6.16.109.3","PexNum3_TempDailyHigh","3号空调日最高温","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.3.1.7.1","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","6.16.109.3","PexNum3_TempDailyLow","3号空调日最低温","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.3.1.8.1","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","6.16.109.3","PexNum3_HumiditySetPoint","3号空调湿度设定点","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.1.0","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","6.16.109.3","PexNum3_HumidityMeasurement","3号空调湿度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.3.1.3.1","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","6.16.109.3","PexNum3_HumidityDailyHigh","3号空调日最高湿度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.3.1.7.1","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","6.16.109.3","PexNum3_HumidityDailyLow","3号空调日最低湿度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.3.1.8.1","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","6.16.109.3","PexNum3_StateCooling","3号空调制冷状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.2.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","8","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","6.16.109.3","PexNum3_StateDehumidify","3号空调除湿状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.5.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","6.16.109.3","PexNum3_StateFan","3号空调风机状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.7.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","6.16.109.3","PexNum3_StateHotWater","3号空调热水器状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.22.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","6.16.109.3","PexNum3_StateSystem","3号空调系统状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.1.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","2,","报警,"]
["31","6.16.109.3","PexNum3_StateElectricHeater","3号空调电加热器状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.21.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","6.16.109.3","PexNum3_StateHumidify","3号空调加湿器状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.4.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","6.16.109.3","PexNum3_Communications","3号空调通讯状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","8","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
[]
["18","6.16.109.4","PexNum4_TempSetPoint","4号空调温度设定点","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.1.0","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","6.16.109.4","PexNum4_TempMeasurement","4号空调温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.3.1.3.1","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","6.16.109.4","PexNum4_TempDailyHigh","4号空调日最高温","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.3.1.7.1","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","6.16.109.4","PexNum4_TempDailyLow","4号空调日最低温","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.3.1.8.1","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","6.16.109.4","PexNum4_HumiditySetPoint","4号空调湿度设定点","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.1.0","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","6.16.109.4","PexNum4_HumidityMeasurement","4号空调湿度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.3.1.3.1","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","6.16.109.4","PexNum4_HumidityDailyHigh","4号空调日最高湿度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.3.1.7.1","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","6.16.109.4","PexNum4_HumidityDailyLow","4号空调日最低湿度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.3.1.8.1","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","6.16.109.4","PexNum4_StateCooling","4号空调制冷状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.2.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","8","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","6.16.109.4","PexNum4_StateDehumidify","4号空调除湿状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.5.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","6.16.109.4","PexNum4_StateFan","4号空调风机状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.7.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","6.16.109.4","PexNum4_StateHotWater","4号空调热水器状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.22.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","6.16.109.4","PexNum4_StateSystem","4号空调系统状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.1.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","2,","报警,"]
["31","6.16.109.4","PexNum4_StateElectricHeater","4号空调电加热器状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.21.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","6.16.109.4","PexNum4_StateHumidify","4号空调加湿器状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.4.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","6.16.109.4","PexNum4_Communications","4号空调通讯状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","8","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
[]
["18","6.16.109.5","PexNum5_TempSetPoint","5号空调温度设定点","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.1.0","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","6.16.109.5","PexNum5_TempMeasurement","5号空调温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.3.1.3.1","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","6.16.109.5","PexNum5_TempDailyHigh","5号空调日最高温","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.3.1.7.1","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","6.16.109.5","PexNum5_TempDailyLow","5号空调日最低温","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.1.3.3.1.8.1","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","6.16.109.5","PexNum5_HumiditySetPoint","5号空调湿度设定点","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.1.0","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","6.16.109.5","PexNum5_HumidityMeasurement","5号空调湿度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.3.1.3.1","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","6.16.109.5","PexNum5_HumidityDailyHigh","5号空调日最高湿度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.3.1.7.1","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","6.16.109.5","PexNum5_HumidityDailyLow","5号空调日最低湿度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.2.2.3.1.8.1","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","6.16.109.5","PexNum5_StateCooling","5号空调制冷状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.2.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","8","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","6.16.109.5","PexNum5_StateDehumidify","5号空调除湿状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.5.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","6.16.109.5","PexNum5_StateFan","5号空调风机状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.7.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","6.16.109.5","PexNum5_StateHotWater","5号空调热水器状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.22.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","6.16.109.5","PexNum5_StateSystem","5号空调系统状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.1.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","2,","报警,"]
["31","6.16.109.5","PexNum5_StateElectricHeater","5号空调电加热器状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.21.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","6.16.109.5","PexNum5_StateHumidify","5号空调加湿器状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.476.1.42.3.4.3.4.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109","ON","OFF","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","6.16.109.5","PexNum5_Communications","5号空调通讯状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","109",null,null,"0","8","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]