{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["变量dat文件","CSpreadSheetBackup"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":31,"n_cols":76,"rows_kept":31,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","9.4.183.1","DIRIS_AP_1_phase_current_A","配电柜A相电流","4","2","1","3","1792",null,null,"0","30","60","1",null,null,"5","0","250","0","0","0","0","0","0","A","900","0.0010000000","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["2","9.4.183.1","DIRIS_AP_1_phase_current_B","配电柜B相电流","4","2","1","3","1793",null,null,"0","30","60","1",null,null,"5","0","250","0","0","0","0","0","0","A","900","0.0010000000","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["3","9.4.183.1","DIRIS_AP_1_phase_current_C","配电柜C相电流","4","2","1","3","1794",null,null,"0","30","60","1",null,null,"5","0","250","0","0","0","0","0","0","A","900","0.0010000000","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["4","9.4.183.1","DIRIS_AP_1_neutral_current","配电柜中性电流","4","2","1","3","1795",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["5","9.4.183.1","DIRIS_AP_1_line_voltage_AB","配电柜A线电压","4","2","1","3","1796",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["6","9.4.183.1","DIRIS_AP_1_line_voltage_BC","配电柜B线电压","4","2","1","3","1797",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["7","9.4.183.1","DIRIS_AP_1_line_voltage_CA","配电柜C线电压","4","2","1","3","1798",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["8","9.4.183.1","DIRIS_AP_1_phase_voltage_A","配电柜A相电压","4","2","1","3","1799",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["9","9.4.183.1","DIRIS_AP_1_phase_voltage_B","配电柜B相电压","4","2","1","3","1800",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["10","9.4.183.1","DIRIS_AP_1_phase_voltage_C","配电柜C相电压","4","2","1","3","1801",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["11","9.4.183.1","DIRIS_AP_1_Frequency","配电柜频率","4","2","1","3","1802",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["12","9.4.183.1","DIRIS_AP_1_phase_Active_A","配电柜A相有功功率","4","2","1","3","1807",null,null,"0","30","60","1",null,null,"5","0","250","0","0","0","0","0","0","KW","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["13","9.4.183.1","DIRIS_AP_1_phase_Active_B","配电柜B相有功功率","4","2","1","3","1808",null,null,"0","30","60","1",null,null,"5","0","250","0","0","0","0","0","0","KW","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["14","9.4.183.1","DIRIS_AP_1_phase_Active_C","配电柜C相有功功率","4","2","1","3","1809",null,null,"0","30","60","1",null,null,"5","0","250","0","0","0","0","0","0","KW","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["15","9.4.183.1","DIRIS_AP_1","1号配电柜通信","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["16","9.4.183.2","DIRIS_AP_2_phase_current_A","2号配电柜A相电流","4","2","1","3","1792",null,null,"0","30","60","1",null,null,"5","0","250","0","0","0","0","0","0","A","900","0.0010000000","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["17","9.4.183.2","DIRIS_AP_2_phase_current_B","2号配电柜B相电流","4","2","1","3","1793",null,null,"0","30","60","1",null,null,"5","0","250","0","0","0","0","0","0","A","900","0.0010000000","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["18","9.4.183.2","DIRIS_AP_2_phase_current_C","2号配电柜C相电流","4","2","1","3","1794",null,null,"0","30","60","1",null,null,"5","0","250","0","0","0","0","0","0","A","900","0.0010000000","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["19","9.4.183.2","DIRIS_AP_2_neutral_current","2号配电柜中性电流","4","2","1","3","1795",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["20","9.4.183.2","DIRIS_AP_2_line_voltage_AB","2号配电柜A线电压","4","2","1","3","1796",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["21","9.4.183.2","DIRIS_AP_2_line_voltage_BC","2号配电柜B线电压","4","2","1","3","1797",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["22","9.4.183.2","DIRIS_AP_2_line_voltage_CA","2号配电柜C线电压","4","2","1","3","1798",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["23","9.4.183.2","DIRIS_AP_2_phase_voltage_A","2号配电柜A相电压","4","2","1","3","1799",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["24","9.4.183.2","DIRIS_AP_2_phase_voltage_B","2号配电柜B相电压","4","2","1","3","1800",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["25","9.4.183.2","DIRIS_AP_2_phase_voltage_C","2号配电柜C相电压","4","2","1","3","1801",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["26","9.4.183.2","DIRIS_AP_2_Frequency","2号配电柜频率","4","2","1","3","1802",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["27","9.4.183.2","DIRIS_AP_2_phase_Active_A","2号配电柜A相有功功率","4","2","1","3","1807",null,null,"0","30","60","1",null,null,"5","0","250","0","0","0","0","0","0","KW","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["28","9.4.183.2","DIRIS_AP_2_phase_Active_B","2号配电柜B相有功功率","4","2","1","3","1808",null,null,"0","30","60","1",null,null,"5","0","250","0","0","0","0","0","0","KW","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["29","9.4.183.2","DIRIS_AP_2_phase_Active_C","2号配电柜C相有功功率","4","2","1","3","1809",null,null,"0","30","60","1",null,null,"5","0","250","0","0","0","0","0","0","KW","900","0.0099999998","3","0","1","1","0","0","0","0","183",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["30","9.4.183.2","DIRIS_AP_2","2号配电柜通信","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]

{"sheet":"CSpreadSheetBackup","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}