{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":111,"n_cols":77,"rows_kept":111,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述",null,"变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["4","9.1.114.1","FDJ_1_10","Alarm relay status","报警继电器状态","10012","2","1","3",48,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","9.1.114.1","FDJ_1_11","Analog value of the insulation shutdown","模拟值的绝缘关机","10012","2","1","3",49,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","9.1.114.1","FDJ_1_12","Voltage between phase 1 & 2","阶段1和2之间的电压","10012","2","1","3",50,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","9.1.114.1","FDJ_1_13","Voltage between phase 2 & 3","二，三期之间的电压","10012","2","1","3",51,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_14","Voltage between phase 3 &1","阶段3和1之间的电压",null,"2","1","3",52,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_15","Voltage between Neutral & phase 1","中性和相位之间的电压1",null,"2","1","3",53,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_16","Voltage between Neutral & phase 2","中性和相位2之间的电压",null,"2","1","3",54,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_17","Voltage between Neutral & phase 3","中性和第3阶段之间的电压",null,"2","1","3",55,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_18","Current in phase 1","目前在第1阶段",null,"2","1","3",56,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_19","Current in phase 2","目前在第2阶段",null,"2","1","3",57,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_20","Current in phase 3","目前在第3阶段",null,"2","1","3",58,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_21","Current in Neutral In","目前中性的",null,"2","1","3",59,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_22","Frequency","频率",null,"2","1","3",60,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_23","Number of running hours","运行小时数",null,"2","1","3",61,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_24","Lub oil pressure","滑油压力",null,"2","1","3",62,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_25","Water temperature","水温",null,"2","1","3",63,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_26","Fuel oil level","燃油油位",null,"2","1","3",64,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_27","Lub oil temperature","滑油温度",null,"2","1","3",65,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_28","Engine speed","发动机转速",null,"2","1","3",66,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_29","Battery voltage","电池电压",null,"2","1","3",67,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_58","Stop solenoid","停止电磁阀",null,"2","1","3",71,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_59","Starter","起动机",null,"2","1","3",71,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","1","1",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_60","Water coolant heater","水冷却液加热器",null,"2","1","3",71,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","2","2",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_61","Sparking-plug pre-heating","火花插头预热",null,"2","1","3",71,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","3","3",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_62","General shutdown","一般关机",null,"2","1","3",71,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","4","4",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_63","Air shutter","风门",null,"2","1","3",71,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","5","5",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_64","Second starter","第二起动机",null,"2","1","3",71,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","6","6",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_65","Fuel oil pump tripped","燃油泵跳闸",null,"2","1","3",71,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","7","7",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_66","Normal breaker","普通断路器",null,"2","1","3",71,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","8","8",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_67","Emergency breaker","紧急断路器",null,"2","1","3",71,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","9","9",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_68","Louver","百叶窗",null,"2","1","3",71,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","10","10",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_69","Insulation protection relay  ","绝缘保护继电器",null,"2","1","3",71,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","11","11",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_70","Number of start attempts on starter n°1","开始尝试起动N°1",null,"2","1","3",145,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0",{"$nulls":12},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_71","Number of start attempts on starter n°2","N°2起动开始尝试",null,"2","1","3",145,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0",{"$nulls":12},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_72","Alternator low voltage threshold","发电机低电压阈值",null,"2","1","3",146,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0",{"$nulls":12},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_73","Alternator high voltage threshold","发电机高电压阈值",null,"2","1","3",146,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0",{"$nulls":12},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_74","Alternator mini frequency threshold","发电机迷你频率阈值",null,"2","1","3",147,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0",{"$nulls":12},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_75","Alternator maxi frequency threshold","发电机马克西频率阈值",null,"2","1","3",147,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0",{"$nulls":12},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_76","Battery low voltage threshold","电池低电压阈值",null,"2","1","3",148,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0",{"$nulls":12},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_77","Battery high voltage threshold","电池的高电压阈值",null,"2","1","3",148,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0",{"$nulls":12},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_78","Overspeed threshold","超速阈值",null,"2","1","3",149,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0",{"$nulls":12},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_79","Stop cranking threshold on electrical starter","停止起动阈值电起动",null,"2","1","3",149,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0",{"$nulls":12},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_80","Stop cranking threshold on pneumatic starter","气动起动器起动阈值",null,"2","1","3",150,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0",{"$nulls":12},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_81","Alternator overload alarm threshold","发电机过载报警阈值",null,"2","1","3",150,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0",{"$nulls":12},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_82","Emergency stop","紧急停止",null,"2","1","3",195,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_88","Overload or Short circuit","过载或短路",null,"2","1","3",195,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","6","6",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_89","Overspeed","超速",null,"2","1","3",195,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","7","7",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_90","Battery low voltage","电池低电压",null,"2","1","3",195,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","8","8",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_91","Battery high voltage","电池的高电压",null,"2","1","3",195,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","9","9",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_94","Alternator low voltage","发电机低电压",null,"2","1","3",195,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","12","12",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_95","Alternator high voltage","发电机高电压",null,"2","1","3",195,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","13","13",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_98","Module 3 CAN bus fault","模块3个CAN总线故障",null,"2","1","3",196,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_99","Module 4 CAN bus fault","模块4个CAN总线故障",null,"2","1","3",196,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","1","1",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_100","Module 5 CAN bus fault","模块5 CAN总线故障",null,"2","1","3",196,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","2","2",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_101","Module 6 CAN bus fault","模块CAN总线故障",null,"2","1","3",196,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","3","3",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_107","Normal breaker open fault","普通断路器断开故障",null,"2","1","3",196,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","9","9",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_108","Emergency breaker open fault","紧急断路器断开故障",null,"2","1","3",196,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","10","10",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_109","Lub oil temperature failure","滑油温度故障",null,"2","1","3",196,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","11","11",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_110","Lub oil low level fault","滑油低级别的故障",null,"2","1","3",196,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","12","12",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_111","Water coolant heater low temperature fault","水低温冷却液加热器故障",null,"2","1","3",196,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","13","13",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_112","Differential protection relay tripped","差动保护继电器跳闸",null,"2","1","3",196,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","14","14",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_113","Insulation protection relay tripped","绝缘保护继电器跳闸",null,"2","1","3",196,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","15","15",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_114","Differential protection relay badly connected","差动保护继电器，连接错误",null,"2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_115","Insulation protection relay badlly connected","badlly连接的绝缘保护继电器",null,"2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","1","1",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_116","Battery charger fault","电池充电器故障",null,"2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","2","2",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_117","Cooling fan tripped","冷却风扇跳闸",null,"2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","3","3",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_118","Water radiator low level fault","水散热器低级别的故障",null,"2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","4","4",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_119","Fuel oil pump n°1 tripped","燃油泵N°1跳闸",null,"2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","5","5",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_120","Retention tank fault","保留坦克故障",null,"2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","6","6",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_121","Fuel tank low level failure","油箱水平低故障",null,"2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","7","7",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_122","Raw water flow fault","原水流量故障",null,"2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","8","8",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_123","Fire detection fault","消防检测故障",null,"2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","9","9",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_124","Lub oil leakage fault","滑油泄漏故障",null,"2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","10","10",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_125","Fuel oil leakage fault","燃油泄漏故障",null,"2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","11","11",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_126","Door of the cooling fan open","门的冷却风扇打开",null,"2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","12","12",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_127","Door of the generating set breaker open","门的发电机组断路器开",null,"2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","13","13",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_128","Generating set circuit breaker open","发电机组断路器开",null,"2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","14","14",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_129","Overload alarm","过载报警",null,"2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","15","15",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_130","MTU lub oil pressure fault","MTU滑油压力故障",null,"2","1","3",198,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_131","MTU water high temperature fault","MTU水高温故障",null,"2","1","3",198,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","1","1",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_132","MTU overspeed fault","MTU超速故障",null,"2","1","3",198,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","2","2",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_133","MTU general shutdown","MTU一般关机",null,"2","1","3",198,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","3","3",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_134","MTU general alarm","MTU一般报警",null,"2","1","3",198,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","4","4",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_135","QST30 overspeed shutdown","QST30超速关机",null,"2","1","3",198,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","5","5",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_136","General ECM shutdown","一般ECM关闭",null,"2","1","3",198,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","6","6",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_137","General ECM alarm","一般ECM报警",null,"2","1","3",198,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","7","7",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_138","Lub oil high level alarm","滑油高位报警",null,"2","1","3",198,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","8","8",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_139","Lub oil high level shutdown","滑油高层次关机",null,"2","1","3",198,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","9","9",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_140","Starting battery low voltage alarm","启动电池低电压报警",null,"2","1","3",198,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","10","10",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_141","Starting battery charger alarm","启动电池充电器报警",null,"2","1","3",198,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","11","11",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_142","Shunt release coil shutdown (MX)","分励脱扣器线圈关机（MX）",null,"2","1","3",198,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","12","12",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_143","Air shutter shutdown","风门关闭",null,"2","1","3",198,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","13","13",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_144","Starter air pressure alarm","起动空气压力报警",null,"2","1","3",198,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","14","14",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_145","Thermo-magnetic relay alarm","热磁继电器报警",null,"2","1","3",198,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","15","15",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_146","Module 4 lub oil pressure fault","模块4滑油压力故障",null,"2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_147","Module 4 water temperature fault","模块4水温故障",null,"2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","1","1",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_148","Module 4 lub oil temperature fault","模块4滑油温度故障",null,"2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","2","2",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_149","Fuel oil low level fault","燃油低级别的故障",null,"2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","3","3",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_150","Fuel oil high level fault","燃油高级别的故障",null,"2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","4","4",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_151","Fuel oil very low level fault","燃油非常低的水平故障",null,"2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","5","5",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_152","Fuel oil very high level fault","燃油相当高的水平故障",null,"2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","6","6",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_153","Lub oil low level fault","滑油低级别的故障",null,"2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","7","7",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_154","Cylinder head temperature fault","缸头温度故障",null,"2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","8","8",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_155","Water temperature fault (calorstat inlet) ","水温故障（恒温箱进）",null,"2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","9","9",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_156","Lack of water circulation","缺乏水循环",null,"2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","10","10",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_157","Bearing temperature alarm","轴承温度报警",null,"2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","11","11",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_158","Bearing temperature shutdown","轴承温度停机",null,"2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","12","12",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_159","Winding temperature alarm","绕组温度报警",null,"2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","13","13",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_160","Winding temperature shutdown","绕组温度停机",null,"2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","14","14",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[null,"9.1.114.1","FDJ_1_161","Fuel oil pump n°2 tripped","燃油泵N°2跳闸",null,"2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300",null,"3","0","1","1","0","0","0","0","114",null,null,"0","15","15",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]