{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":15,"n_cols":76,"rows_kept":15,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["113","9.35.136.1","Pdu1_A_Phase_Vol","电量仪* A相电压","4","2","1","3","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["114","9.35.136.1","Pdu1_B_Phase_Vol","电量仪* B相电压","4","2","1","3","1",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["115","9.35.136.1","Pdu1_C_Phase_Vol","电量仪* C相电压","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["116","9.35.136.1","Pdu1_A_Line_Vol","电量仪* A线电压","4","2","1","3","4",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["117","9.35.136.1","Pdu1_B_Line_Vol","电量仪* B线电压","4","2","1","3","5",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["118","9.35.136.1","Pdu1_C_Line_Vol","电量仪* C线电压","4","2","1","3","6",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["119","9.35.136.1","Pdu1_A_Line_Current","电量仪* A线电流","4","2","1","3","9",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.0010000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["120","9.35.136.1","Pdu1_B_Line_Current","电量仪* B线电流","4","2","1","3","10",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.0010000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["121","9.35.136.1","Pdu1_C_Line_Current","电量仪* C线电流","4","2","1","3","11",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.0010000000","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["122","9.35.136.1","Pdu1_A_Phase_Pw","电量仪* A相视在功率","5","4","2","3","30",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Kw","300","0.2000000030","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["123","9.35.136.1","Pdu1_B_Phase_Pw","电量仪* B相视在功率","5","4","2","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Kw","300","0.2000000030","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["124","9.35.136.1","Pdu1_C_Phase_Pw","电量仪* C相视在功率","5","4","2","3","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Kw","300","0.2000000030","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["125","9.35.136.1","Pdu1_Sys_Freq","电量仪* 频率","4","2","1","3","42",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.0099999998","3","0","0","0","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.35.136.1","Pdu1_Netstatus","电量仪* 通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]