{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":22,"n_cols":76,"rows_kept":22,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","6.14.104.1","Caross_1_Blower_1_Status","空调* 送风机状态","2","1","1","1","128",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","104","开","关","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","6.14.104.1","Caross_1_Compressor_1_Status","空调* 压缩机1状态","2","1","1","1","129",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","104","开","关","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.14.104.1","Caross_1_Compressor_2_Status","空调* 压缩机2状态","2","1","1","1","130",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","104","开","关","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.14.104.1","Caross_1_ElectricHeater_1_Status","空调* 电加热器1状态","2","1","1","1","131",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","104","开","关","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.14.104.1","Caross_1_ElectricHeater_2_Status","空调* 电加热器2状态","2","1","1","1","132",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","104","开","关","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.14.104.1","Caross_1_DehumidificationStatus","空调* 除湿状态","2","1","1","1","133",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","104","开","关","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.14.104.1","Caross_1_HumidificationStatus","空调* 加湿状态","2","1","1","1","134",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","104","开","关","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.14.104.1","Caross_1_ColdBlower_1_Status","空调* 冷凝风机1状态","2","1","1","1","135",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","104","开","关","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.14.104.1","Caross_1_ColdBlower_2_Status","空调* 冷凝风机2状态","2","1","1","1","136",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","104","开","关","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.14.104.1","Caross_1_InletValueStatus","空调* 进水阀状态","2","1","1","1","137",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","104","开","关","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","6.14.104.1","Caross_1_OutletValueStatus","空调* 排水阀状态","2","1","1","1","138",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","104","开","关","0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","6.14.104.1","Caross_1_BlowerOverload","空调* 送风机过载","2","1","1","1","152",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","104",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","告警,"]
["13","6.14.104.1","Caross_1_FilterFault","空调* 过滤网阻塞","2","1","1","1","153",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","104",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","告警,"]
["14","6.14.104.1","Caross_1_Compressor_1_High","空调* 压缩机1高压","2","1","1","1","154",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","104",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","告警,"]
["15","6.14.104.1","Caross_1_Compressor_1_Low","空调* 压缩机1低压","2","1","1","1","155",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","104",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","告警,"]
["16","6.14.104.1","Caross_1_Compressor_2_High","空调* 压缩机2高压","2","1","1","1","157",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","104",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","告警,"]
["17","6.14.104.1","Caross_1_Compressor_2_Low","空调* 压缩机2低压","2","1","1","1","158",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","104",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","告警,"]
["18","6.14.104.1","Caross_1_Temp","空调* 回风温度","4","2","1","3","704",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","104",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","6.14.104.1","Caross_1_Humidity","空调* 回风湿度","4","2","1","3","705",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1000000015","3","0","1","1","0","0","0","0","104",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","6.14.104.1","Caross_1_Netstatus","空调* 通信状态","1000","0","0","2","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","104",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["1","6.14.104.1","Caross_1_StartORShutSet","空调* 开关机","2","1","1","5","176",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","1","0","0","0","0","0","0","104",null,null,"0","0","0",{"$nulls":10},"1","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]