{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":17,"n_cols":76,"rows_kept":17,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","6.20.180.1","powernet_air1_max_rack_temp","空调* 内机最大机架温度","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.318.1.1.13.3.2.1.1.6.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","6.20.180.1","powernet_air1_min_rack_temp","空调* 内机最小机架温度","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.318.1.1.13.3.2.1.1.8.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.20.180.1","powernet_air1_cooling_setpoint","空调* 内机制冷设定点","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.318.1.1.13.3.2.1.2.2.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.20.180.1","powernet_air1_supply_air_setpoint","空调* 内机送风温度设定点","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.318.1.1.13.3.2.1.2.4.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.20.180.1","powernet_air1_fan_speed_setting","空调* 内机风扇转速","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.318.1.1.13.3.2.1.2.5.0","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.20.180.1","powernet_air1_cooling_operating_mode","空调* 内机制冷运行模式","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.20.180.1","powernet_air1_rack_temp","空调* 内机机架温度","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.7.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.20.180.1","powernet_air1_supply_air_temp","空调* 内机送风温度","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.9.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.20.180.1","powernet_air1_return_air_temp","空调* 内机回风温度","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.11.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.20.180.1","powernet_air1_entering_fluid_temp","空调* 内机进水温度","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.24.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","6.20.180.1","powernet_air1_Leaving_fluid_temp","空调* 内机出水温度","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.26.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","6.20.180.1","powernet_air1_rack_temp_threshold","空调* 内机机架温度阀值","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.2.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","6.20.180.1","powernet_air1_supply_air_temp_threshold","空调* 内机送风温度阀值","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.4.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","6.20.180.1","powernet_air1_return_air_temp_threshold","空调* 内机回风温度阀值","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.6.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","6.20.180.1","powernet_air1_entering_fluid_temp_threshold","空调* 内机进水温度阀值","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.8.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","6.20.180.1","powernet_air1","空调* 通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]