{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":30,"n_cols":76,"rows_kept":30,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","6.8.96.1","Air1_SystemOn","空调* 运行","4","1","1","1","1",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","0,","报警 ,"]
["2","6.8.96.1","Air1_Compressor_1","空调* 压缩机1状态","4","1","1","1","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.8.96.1","Air1_Compressor_2","空调* 压缩机2状态","4","1","1","1","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.8.96.1","Air1_Compressor_3","空调* 压缩机3状态","4","1","1","1","4",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.8.96.1","Air1_Compressor_4","空调* 压缩机4状态","4","1","1","1","5",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.8.96.1","Air1_El_Heater1","空调* 电加热器1状态","4","1","1","1","6",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.8.96.1","Air1_El_Heater2","空调* 电加热器2状态","4","1","1","1","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.8.96.1","Air1_Dehumidification","空调* 除湿器状态","4","1","1","1","10",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.8.96.1","Air1_Humidification","空调* 加湿器状态","4","1","1","1","11",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.8.96.1","Air1_HighRoomTemperatureAlarm","空调* 高温报警","4","1","1","1","21",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警 ,"]
["11","6.8.96.1","Air1_LowRoomTemperatureAlarm","空调* 低温报警","4","1","1","1","22",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警 ,"]
["12","6.8.96.1","Air1_HighRoomHumidityAlarm","空调* 高湿报警","4","1","1","1","23",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警 ,"]
["13","6.8.96.1","Air1_LowRoomHumidityAlarm","空调* 低湿报警","4","1","1","1","24",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警 ,"]
["14","6.8.96.1","Air1_CloggedFilterAlarm","空调* 过滤器堵塞报警","4","1","1","1","26",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警 ,"]
["15","6.8.96.1","Air1_LossofAir lowAlarm","空调* 空气流失报警","4","1","1","1","28",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警 ,"]
["16","6.8.96.1","Air1_HeaterOverheatingAlarm","空调* 加热器过热报警","4","1","1","1","29",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警 ,"]
["17","6.8.96.1","Air1_Circuit1HighPressureAlarm","空调* 电路1高压报警","4","1","1","1","30",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警 ,"]
["18","6.8.96.1","Air1_Circuit2HighPressureAlarm","空调* 电路2高压报警","4","1","1","1","31",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警 ,"]
["19","6.8.96.1","Air1_Circuit1LowPressureAlarm","空调* 电路1低压报警","4","1","1","1","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警 ,"]
["20","6.8.96.1","Air1_Circuit2LowPressureAlarm","空调* 电路2低压报警","4","1","1","1","33",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警 ,"]
["21","6.8.96.1","Air1_Humidifier_WaterLossAlarm","空调* 加湿器:水丢失报警","4","1","1","1","41",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警 ,"]
["22","6.8.96.1","Air1_HumidifierGeneral Alarm","空调* 加湿器一般报警","4","1","1","1","65",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警 ,"]
["23","6.8.96.1","Air1_UnitonAlarm","空调* 单元报警","4","1","1","1","66",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警 ,"]
["24","6.8.96.1","Air1_UnitSwitch","空调* 单元开关","4","1","1","1","75",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","单元关,"]
["25","6.8.96.1","Air1_RoomTemperature","空调* 室温","4","2","1","3","1",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["26","6.8.96.1","Air1_OutdoorTemperature","空调* 室外温度","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["27","6.8.96.1","Air1_RoomRelativeHumidity","空调* 房间相对湿度","4","2","1","3","6",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["28","6.8.96.1","Air1_OutletChilledWaterTemperature","空调* 冷却水温度","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["1","6.8.96.1","Air1_Communications","空调* 通信状态","1000","0","0","1","0","","","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断开,"]