{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":16,"n_cols":76,"rows_kept":16,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","6.4.83.1","Hiro_1_TempSetPoint","空调* 温度设定点","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","83",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0"]
["2","6.4.83.1","Hiro_1_HumiditySetPoint","空调* 湿度设定点","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","83",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.4.83.1","Hiro_1_Temperature","空调* 温度","4","4","1","4","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","83",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.4.83.1","Hiro_1_Humidity","空调* 湿度","4","4","1","4","9",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","83",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.4.83.1","Hiro_1_CompressorStatus","空调* 压缩机状态","4","1","1","1","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","83",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.4.83.1","Hiro_1_pumpdownStatus","空调* 抽气机状态","4","1","1","1","35",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","83",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.4.83.1","Hiro_1_ElectricalHeaterStatus1","空调* 电加热状态1","4","1","1","1","36",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","83",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.4.83.1","Hiro_1_humidifierFeedStatus","空调* 加湿器状态","4","1","1","1","36",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","83",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.4.83.1","Hiro_1_dehumidificationStatus","空调* 除湿器状态","4","1","1","1","40",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","83",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.4.83.1","Hiro_1_ElectricalHeaterStatus2","空调* 电加热状态2","4","1","1","1","41",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","83",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","6.4.83.1","Hiro_1_HighTempWaring","空调* 高温","4","1","1","3","10",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","83",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["12","6.4.83.1","Hiro_1_LowTempWaring","空调* 低温","4","1","1","3","11",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","83",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","告警,"]
["13","6.4.83.1","Hiro_1_HighHumidityWaring","空调* 高湿","4","1","1","3","10",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","83",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","告警,"]
["14","6.4.83.1","Hiro_1_LowHumidityWaring","空调* 低湿","4","1","1","3","10",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","83",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","告警,"]
["15","6.4.83.1","Hiro_1_ComStatus","空调* 通信状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","83",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线告警,"]