{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":22,"n_cols":76,"rows_kept":22,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","5.4.63.1","C2000_1_DI1_Leak","C2000* 机房漏水","3","2","1","3","9",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","6","0",{"$nulls":10},"1","0","255","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","0,","报警,"]
["2","5.4.63.1","C2000_1_DI2_LineBreak","C2000* 机房EPS运行状态","3","2","1","3","10",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","1","0","0","0","63",null,null,"0","6","40",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","未运行,"]
["3","5.4.63.1","C2000_1_DI3_Smoke","C2000* 机房烟感1","3","2","1","3","11",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","6","0",{"$nulls":10},"1","0","255","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","0,","报警,"]
["4","5.4.63.1","C2000_1_DI4_Smoke","C2000* 机房烟感2","3","2","1","3","12",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","6","0",{"$nulls":10},"1","0","255","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","0,","报警,"]
["5","5.4.63.1","C2000_1_DI5_Lamp_panel_monitor","C2000* 机房灯盘监测","3","2","1","3","13",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","6","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","5.4.63.1","C2000_1_DI7_Flow_valve","C2000* 机房流量阀","3","2","1","3","15",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","1","0","0","0","63",null,null,"0","6","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["7","5.4.63.1","C2000_1_DI6_Magnetic","C2000* 机房门磁","3","2","1","3","14",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","6","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","门开启,"]
["8","5.4.63.1","C2000_1_DI8_Tank_liquid_temp","C2000* 机房水箱液温","3","2","1","3","16",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","6","0",{"$nulls":10},"1","0","255","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","0,","报警,"]
["9","5.4.63.1","C2000_1_DO1_Lamp_panelControl","C2000* 机房灯盘状态","3","2","1","3","17",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","6","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","5.4.63.1","C2000_1_DO2_PumpControl","C2000* 机房水泵状态","3","2","1","3","18",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","6","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","5.4.63.1","C2000_1_DO3_SoundLight","C2000* 机房控制声光报警输出","3","2","1","3","19",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","6","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","5.4.63.1","C2000_1_DO4_EPS","C2000* 机房控制EPS无源启动","3","2","1","3","20",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","6","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","5.4.63.1","C2000_1_DO5_Alarm_Mute","C2000* 机房报警消音状态","3","2","1","3","21",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","6","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","5.4.63.1","C2000_1_DO6","C2000* 机房主从泵切换状态","3","2","1","3","22",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","6","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","5.4.63.1","C2000_1_DO1_Lamp_panelControl_set","C2000* 机房控制灯盘","3","2","1","16","17",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","1","1","1","0","0","0","0","63",null,null,"0","6","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","5.4.63.1","C2000_1_DO2_PumpControl_set","C2000* 机房控制水泵","3","2","1","16","18",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","1","1","1","0","0","0","0","63",null,null,"0","6","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","5.4.63.1","C2000_1_DO3_SoundLight_set","C2000* 机房控制声光报警输出","3","2","1","16","19",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","1","1","1","0","0","0","0","63",null,null,"0","6","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","5.4.63.1","C2000_1_DO4_EPS_set","C2000* 机房控制常闭EPS无源启动","3","2","1","16","20",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","1","1","1","0","0","0","0","63",null,null,"0","6","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","5.4.63.1","C2000_1_DO5_Alarm_Mute_set","C2000* 机房控制报警消音启动","3","2","1","16","21",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","1","1","1","0","0","0","0","63",null,null,"0","6","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","5.4.63.1","C2000_1_DO6_set","C2000* 机房控制主从泵切换","3","2","1","16","22",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","1","1","1","0","0","0","0","63",null,null,"0","6","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","5.4.63.1","C2000_1_LinkStatus","C2000* 机房智能采集设备通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]