{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":15,"n_cols":76,"rows_kept":15,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","4.24.48.1","UPS1_BatteryStatus","UPS* 电池电量","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.935.1.1.1.2.1.1.0","public","0","0","0","0","0","0","2","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"2","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","3,","低报警,"]
["2","4.24.48.1","UPS1_BatteryCapacity","UPS* 电池容量","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.935.1.1.1.2.2.1.0","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","4.24.48.1","UPS1_BatteryVoltage","UPS* 电池电压","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.935.1.1.1.2.2.6.0","public","0","0","0","0","0","0","0","0","0","V","300","0.1000000015","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","4.24.48.1","UPS1_BatteryTemperature","UPS* 电池温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.935.1.1.1.2.2.3.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","4.24.48.1","UPS1_BatteryRunTimeRemaining","UPS* 电池供电时间","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.935.1.1.1.2.2.4.0","public","0","0","0","0","0","0","0","0","0","Min","300","1.0000000000","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","10000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","4.24.48.1","UPS1_BatteryCurrent","UPS* 电池电流","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.935.1.1.1.2.2.7.0","public","0","0","0","0","0","0","0","0","0","A","300","0.1000000015","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","150","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","4.24.48.1","UPS1_InputLineVoltage","UPS* 输入线电压","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.935.1.1.1.3.2.1.0","public","0","0","0","0","0","0","0","0","0","V","300","0.1000000015","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","4.24.48.1","UPS1_InputFrequency","UPS* 输入频率","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.935.1.1.1.3.2.4.0","public","0","0","0","0","0","0","0","0","0","Hz","300","0.1000000015","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","4.24.48.1","UPS1_OutputStatus","UPS* 输出状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.935.1.1.1.4.1.1.0","public","0","0","0","0","0","0","2","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"2","0","100","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","6,","报警,"]
["10","4.24.48.1","UPS1_OutputVoltage","UPS* 输出电压","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.935.1.1.1.4.2.1.0","public","0","0","0","0","0","0","0","0","0","V","300","0.1000000015","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","4.24.48.1","UPS1_OutputFrequency","UPS* 输出频率","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.935.1.1.1.4.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","300","0.1000000015","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","4.24.48.1","UPS1_OutputLoad","UPS* 输出负载","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.935.1.1.1.4.2.3.0","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","4.24.48.1","UPS1_InputLineFailCause","UPS* 输入状态","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.935.1.1.1.3.2.5.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0",null,"10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","3,","报警,"]
["14","4.24.48.1","UPS1_Communication","UPS* 通信状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","136",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]