{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":31,"n_cols":76,"rows_kept":31,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","4.3.3.1","APC1_upsBasicBatteryStatus","UPS* 电池状态","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","3,","电池低,"]
["2","4.3.3.1","APC1_upsAdvBatteryTemperature","UPS* 电池温度","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.2.2.2.0","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","4.3.3.1","APC1_upsAdvBatteryRunTimeRemaining","UPS* 电池时间","10","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.2.2.3.0","public","0","0","0","0","0","0","0","0","0","Day","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","10000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","4.3.3.1","APC1_upsAdvBatteryReplaceIndicator","UPS* 电池是否需要替换","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.2.2.4.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","4.3.3.1","APC1_upsAdvBatteryNumOfBattPacks","UPS* 电池节数","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.2.2.5.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","4.3.3.1","APC1_upsAdvBatteryNumOfBadBattPacks","UPS* 坏电池节数","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.2.2.6.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","4.3.3.1","APC1_upsBasicInputPhase","UPS* 输入相数","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.3.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","4.3.3.1","APC1_upsAdvInputLineVoltage","UPS* 输入线电压","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.3.2.1.0","public","0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","4.3.3.1","APC1_upsAdvInputMaxLineVoltage","UPS* 输入最大线电压","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.3.2.2.0","public","0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","4.3.3.1","APC1_upsAdvInputMinLineVoltage","UPS* 输入最小线电压","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.3.2.3.0","public","0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","4.3.3.1","APC1_upsAdvInputFrequency","UPS* 输入频率","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.3.2.4.0","public","0","0","0","0","0","0","0","0","0","Hz","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","4.3.3.1","APC1_upsBasicOutputPhase","UPS* 输出线数","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.4.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","4.3.3.1","APC1_upsBasicOutputStatus","UPS* 基本输出状态","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.4.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","4","3,6,7,10,","输入故障,软件旁路,UPS不在线,硬件旁路失败,"]
["14","4.3.3.1","APC1_upsAdvOutputVoltage","UPS* 输出电压","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.4.2.1.0","public","0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","4.3.3.1","APC1_upsAdvOutputFrequency","UPS* 输出频率","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.4.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","4.3.3.1","APC1_upsAdvOutputLoad","UPS* 输出负载","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.4.2.3.0","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","4.3.3.1","APC1_upsAdvOutputCurrent","UPS* 输出电流","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.4.2.4.0","public","0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","4.3.3.1","APC1_upsPhaseInputVoltage_A","UPS* A相输入电压","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.9.2.3.1.3.1.1.1","public","0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","4.3.3.1","APC1_upsPhaseInputVoltage_B","UPS* B相输入电压","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.9.2.3.1.3.1.1.2","public","0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","4.3.3.1","APC1_upsPhaseInputVoltage_C","UPS* C相输入电压","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.9.2.3.1.3.1.1.3","public","0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","4.3.3.1","APC1_upsPhaseInputCurrent_A","UPS* A相输入电流","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.9.2.3.1.6.1.1.1","public","0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","4.3.3.1","APC1_upsPhaseInputCurrent_B","UPS* B相输入电流","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.9.2.3.1.6.1.1.2","public","0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","4.3.3.1","APC1_upsPhaseInputCurrent_C","UPS* C相输入电流","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.9.2.3.1.6.1.1.3","public","0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","4.3.3.1","APC1_upsPhaseOutputVoltage_A","UPS* A相输出电压","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.9.3.3.1.3.1.1.1","public","0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","4.3.3.1","APC1_upsPhaseOutputVoltage_B","UPS* B相输出电压","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.9.3.3.1.3.1.1.2","public","0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","4.3.3.1","APC1_upsPhaseOutputVoltage_C","UPS* C相输出电压","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.9.3.3.1.3.1.1.3","public","0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","4.3.3.1","APC1_upsPhaseOutputCurrent_A","UPS* A相输出电流","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.9.3.3.1.4.1.1.1","public","0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","4.3.3.1","APC1_upsPhaseOutputCurrent_B","UPS* B相输出电流","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.9.3.3.1.4.1.1.2","public","0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","4.3.3.1","APC1_upsPhaseOutputCurrent_C","UPS* C相输出电流","4","0","1","3","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.1.9.3.3.1.4.1.1.3","public","0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","4.3.3.1","APC1_NetStatus","UPS* 通讯状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","3",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]