{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":78,"n_cols":76,"rows_kept":78,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","4.12.21.1","Gly5000_Loadprotected","UPS* 负载保护","4","2","1","3","64",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","1","21","是","否","0","0","0",{"$nulls":10},"1","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","4.12.21.1","Gly5000_UPScoupled","UPS* 耦合","4","2","1","3","64",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","2","21","是","否","0","0","0",{"$nulls":10},"1","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","4.12.21.1","Gly5000_UPSonline","UPS* 在线模式","4","2","1","3","65",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","3","21","是","否","0","1","1",{"$nulls":10},"1","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","4.12.21.1","Gly5000_UPSeco","UPS* 生态模式","4","2","1","3","65",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","4","21","是","否","0","2","2",{"$nulls":10},"1","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","4.12.21.1","Gly5000_Manualbypassswitch","UPS* 手动旁路开关","4","2","1","3","65",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","5","21","开","关","0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","4.12.21.1","Gly5000_BatteryCircuitbreaker","UPS* 电池断路器","4","2","1","3","66",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","6","21","开","关","0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","4.12.21.1","Gly5000_RectifierNormalSwitch","UPS* 整流器正常开关","4","2","1","3","68",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","7","21","关","开","0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","4.12.21.1","Gly5000_Mains1inputswitch","UPS* 主路输入开关","4","2","1","3","68",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","8","21","关","开","0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","4.12.21.1","Gly5000_Outputswitch","UPS* 输出开关","4","2","1","3","71",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","9","21","关","开","0","11","11",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","4.12.21.1","Gly5000_Batterychargedstate","UPS* 电池充电状态","4","2","1","3","73",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","10","21","未充电","充电中","0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","4.12.21.1","Gly5000_Unitgeneralalarm","UPS* 单元一般状态","4","2","1","3","64",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","11","21",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["12","4.12.21.1","Gly5000_Batterylowwarning","UPS* 电池低","4","2","1","3","64",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","12","21",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["13","4.12.21.1","Gly5000_Emergencystop","UPS* 紧急停止","4","2","1","3","64",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","13","21",null,null,"0","11","11",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["14","4.12.21.1","Gly5000_Batteryendoflife","UPS* 电池寿命结束","4","2","1","3","66",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","14","21",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["15","4.12.21.1","Gly5000_BatteryTemperatureOver","UPS* 电池温度超标","4","2","1","3","66",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","15","21",null,null,"0","10","10",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["16","4.12.21.1","Gly5000_Mains1voltageOver","UPS* 主路电压超标","4","2","1","3","68",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","16","21",null,null,"0","8","8",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["17","4.12.21.1","Gly5000_Mains1frequencyOver","UPS* 主路频率超标","4","2","1","3","68",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","17","21",null,null,"0","11","11",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["18","4.12.21.1","Gly5000_Rectifierthermaloverload","UPS* 整流器热过载","4","2","1","3","68",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","18","21",null,null,"0","12","12",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["19","4.12.21.1","Gly5000_Mains2overload","UPS* 旁路过载","4","2","1","3","70",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","19","21",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["20","4.12.21.1","Gly5000_Mains2thermalOver","UPS* 旁路热过载","4","2","1","3","70",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","20","21",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","4.12.21.1","Gly5000_Mains2frequencyOver","UPS* 旁路频率超标","4","2","1","3","70",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","21","21",null,null,"0","9","9",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["22","4.12.21.1","Gly5000_Mains2voltageOver","UPS* 旁路电压超标","4","2","1","3","70",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","22","21",null,null,"0","10","10",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["23","4.12.21.1","Gly5000_Chargergeneralfault","UPS* 充电器一般故障","4","2","1","3","73",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","23","21",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["24","4.12.21.1","Gly5000_MajorUPSfault","UPS* 主故障","4","2","1","3","76",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","24","21",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["25","4.12.21.1","Gly5000_Inverteroverload","UPS* 逆变器过载","4","2","1","3","76",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","25","21",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["26","4.12.21.1","Gly5000_Inverterthermaloverload","UPS* 逆变器热过载","4","2","1","3","76",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","26","21",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["27","4.12.21.1","Gly5000_Inverterlimitation","UPS* 逆变器受限","4","2","1","3","76",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","27","21",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["28","4.12.21.1","Gly5000_Outputthermaloverload","UPS* 输出热过载","4","2","1","3","76",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","28","21",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["29","4.12.21.1","Gly5000_Outputoverload","UPS* 输出过载","4","2","1","3","77",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","29","21",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["30","4.12.21.1","Gly5000_Inverterfusefault","UPS* 逆变器保险丝故障","4","2","1","3","79",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","30","21",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["31","4.12.21.1","Gly5000_Outputinshortcircuit","UPS* 输出短路","4","2","1","3","79",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","31","21",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["32","4.12.21.1","Gly5000_Mains1I1","UPS* 主路A相电流","4","2","1","3","256",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","4.12.21.1","Gly5000_Mains1I2","UPS* 主路B相电流","4","2","1","3","257",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","4.12.21.1","Gly5000_Mains1I3","UPS* 主路C相电流","4","2","1","3","258",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","4.12.21.1","Gly5000_Mains2I1","UPS* 旁路A相电流","4","2","1","3","262",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["36","4.12.21.1","Gly5000_Mains2I2","UPS* 旁路B相电流","4","2","1","3","263",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["37","4.12.21.1","Gly5000_Mains2I3","UPS* 旁路C相电流","4","2","1","3","264",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["38","4.12.21.1","Gly5000_OutputI1","UPS* A相输出电流","4","2","1","3","265",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["39","4.12.21.1","Gly5000_OutputI2","UPS* B相输出电流","4","2","1","3","266",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["40","4.12.21.1","Gly5000_OutputI3","UPS* C相输出电流","4","2","1","3","267",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["41","4.12.21.1","Gly5000_BatteryI","UPS* 电池电流","4","2","1","3","270",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["42","4.12.21.1","Gly5000_DeviceNominalActivePower","UPS* 额定有功功率","4","2","1","3","273",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","10000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["43","4.12.21.1","Gly5000_Mains1U12","UPS* 主路AB相电压","4","2","1","3","277",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["44","4.12.21.1","Gly5000_Mains1U23","UPS* 主路BC相电压","4","2","1","3","278",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["45","4.12.21.1","Gly5000_Mains1U31","UPS* 主路CA相电压","4","2","1","3","279",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["46","4.12.21.1","Gly5000_InverterU1N","UPS* 逆变器A相电压","4","2","1","3","280",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["47","4.12.21.1","Gly5000_InverterU2N","UPS* 逆变器B相电压","4","2","1","3","281",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["48","4.12.21.1","Gly5000_InverterU3N","UPS* 逆变器C相电压","4","2","1","3","282",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["49","4.12.21.1","Gly5000_Mains2U12","UPS* 旁路AB相电压","4","2","1","3","289",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["50","4.12.21.1","Gly5000_Mains2U23","UPS* 旁路BC相电压","4","2","1","3","290",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["51","4.12.21.1","Gly5000_Mains2U31","UPS* 旁路CA相电压","4","2","1","3","291",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["52","4.12.21.1","Gly5000_OutputU1N","UPS* A相输出电压","4","2","1","3","292",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["53","4.12.21.1","Gly5000_OutputU2N","UPS* B相输出电压","4","2","1","3","293",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["54","4.12.21.1","Gly5000_OutputU3N","UPS* C相输出电压","4","2","1","3","294",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["55","4.12.21.1","Gly5000_OutputU12","UPS* AB相输出电压","4","2","1","3","295",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["56","4.12.21.1","Gly5000_OutputU23","UPS* BC相输出电压","4","2","1","3","296",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["57","4.12.21.1","Gly5000_OutputU31","UPS* CA相输出电压","4","2","1","3","297",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["58","4.12.21.1","Gly5000_BatteryU","UPS* 电池电压","4","2","1","3","301",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["59","4.12.21.1","Gly5000_Outputactivepower1","UPS* A相输出有功功率","4","2","1","3","304",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","10000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["60","4.12.21.1","Gly5000_Outputactivepower2","UPS* B相输出有功功率","4","2","1","3","305",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","10000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["61","4.12.21.1","Gly5000_Outputactivepower3","UPS* C相输出有功功率","4","2","1","3","306",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","10000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["62","4.12.21.1","Gly5000_Outputapparentpower1","UPS* A相输出视在功率","4","2","1","3","307",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","10000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["63","4.12.21.1","Gly5000_Outputapparentpower2","UPS* B相输出视在功率","4","2","1","3","308",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","10000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["64","4.12.21.1","Gly5000_Outputapparentpower3","UPS* C相输出视在功率","4","2","1","3","309",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","10000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["65","4.12.21.1","Gly5000_OutputTotalActivepower","UPS* 输出总有功功率","4","2","1","3","310",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","10000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["66","4.12.21.1","Gly5000_OutputTotalApparentpower","UPS* 输出总视在功率","4","2","1","3","311",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","10000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["67","4.12.21.1","Gly5000_OutputloadLevel","UPS* 输出负载水平","4","2","1","3","313",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["68","4.12.21.1","Gly5000_Mains1frequency","UPS* 主路频率","4","2","1","3","318",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["69","4.12.21.1","Gly5000_Inverterfrequency","UPS* 逆变器频率","4","2","1","3","319",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["70","4.12.21.1","Gly5000_Mains2frequency","UPS* 旁路频率","4","2","1","3","320",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["71","4.12.21.1","Gly5000_Outputfrequency","UPS* 输出频率","4","2","1","3","321",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["72","4.12.21.1","Gly5000_Batterybackuptime","UPS* 电池备份时间","4","2","1","3","329",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","min","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","10000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["73","4.12.21.1","Gly5000_BatteryTemp","UPS* 电池温度","4","2","1","3","330",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["74","4.12.21.1","Gly5000_BatterychargingLevel","UPS* 电池充电量","4","2","1","3","331",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["75","4.12.21.1","Gly5000_BatteryrechargeDuration","UPS* 电池充电时间","4","2","1","3","335",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","min","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["76","4.12.21.1","Gly5000_UPSRatedpower","UPS* 额定功率","4","2","1","3","521",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","10000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["77","4.12.21.1","Gly5000_LinkStatus","UPS* 通信状态","1000","1","1","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","21",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]