{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":39,"n_cols":76,"rows_kept":39,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","4.12.191.1","UPS_1_1_BatteryRemainingTime","UPS* 电池剩余时间","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.5.1.0","public","0","0","0","0","0","0","0","0","0","Min","300","1.0000000000","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","1000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","4.12.191.1","UPS_1_1_BatteryLevel","UPS* 电池容量","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.5.2.0","public","0","0","0","0","0","0","0","0","0","Min","300","1.0000000000","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","1000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","4.12.191.1","UPS_1_1_BatteryVoltage","UPS* 电池电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.5.5.0","public","0","0","0","0","0","0","0","0","0","V","300","0.1000000015","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","4.12.191.1","UPS_1_1_BatteryCurrent","UPS* 电池电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.5.6.0","public","0","0","0","0","0","0","0","0","0","A","300","0.0099999998","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","4.12.191.1","UPS_1_1_BatteryTemperature","UPS* 电池温度","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.5.7.0","public","0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","4.12.191.1","UPS_1_1_BatteryFaultBattery","UPS* 电池故障","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.5.9.0","public","0","0","0","0","0","0","2","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"2","0","5","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["7","4.12.191.1","UPS_1_1_BatteryNoBattery","UPS* 蓄电池状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.5.10.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","5","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","4.12.191.1","UPS_1_1_BatteryUnavailableBattery","UPS* 电池是否可用","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.5.12.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","5","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","4.12.191.1","UPS_1_1_BatteryLowBattery","UPS* 电池电量低","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.5.14.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"2","0","5","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["10","4.12.191.1","UPS_1_1_BatteryChargerFault","UPS* 电池充电状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.5.15.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","5","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","4.12.191.1","UPS_1_1_InputFrequency_A","UPS* A相输入频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.6.2.1.3.1","public","0","0","0","0","0","0","0","0","0","Hz","300","0.1000000015","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","4.12.191.1","UPS_1_1_InputFrequency_B","UPS* B相输入频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.6.2.1.3.2","public","0","0","0","0","0","0","0","0","0","Hz","300","0.1000000015","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","4.12.191.1","UPS_1_1_InputFrequency_C","UPS* C相输入频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.6.2.1.3.3","public","0","0","0","0","0","0","0","0","0","Hz","300","0.1000000015","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","4.12.191.1","UPS_1_1_InputVoltage_A","UPS* A相输入电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.6.2.1.2.1","public","0","0","0","0","0","0","0","0","0","V","300","0.1000000015","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","4.12.191.1","UPS_1_1_InputVoltage_B","UPS* B相输入电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.6.2.1.2.2","public","0","0","0","0","0","0","0","0","0","V","300","0.1000000015","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","4.12.191.1","UPS_1_1_InputVoltage_C","UPS* C相输入电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.6.2.1.2.3","public","0","0","0","0","0","0","0","0","0","V","300","0.1000000015","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","4.12.191.1","UPS_1_1_InputCurrent_A","UPS* A相输入电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.6.2.1.6.1","public","0","0","0","0","0","0","0","0","0","A","300","0.0099999998","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","4.12.191.1","UPS_1_1_InputCurrent_B","UPS* B相输入电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.6.2.1.6.2","public","0","0","0","0","0","0","0","0","0","A","300","0.0099999998","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","4.12.191.1","UPS_1_1_InputCurrent_C","UPS* C相输入电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.6.2.1.6.3","public","0","0","0","0","0","0","0","0","0","A","300","0.0099999998","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","4.12.191.1","UPS_1_1_InputBadStatus","UPS* 输入电压或频率故障","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.6.3.0","public","0","0","0","0","0","0","2","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","5","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","4.12.191.1","UPS_1_1_InputLineFailCause","UPS* 市电故障","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.6.4.0","public","0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","5","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","3","2,3,4,","超压,超出频率,无电压,"]
["22","4.12.191.1","UPS_1_1_OutputVoltage_A","UPS* A相输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.7.2.1.2.1","public","0","0","0","0","0","0","0","0","0","V","300","0.1000000015","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","4.12.191.1","UPS_1_1_OutputVoltage_B","UPS* B相输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.7.2.1.2.2","public","0","0","0","0","0","0","0","0","0","V","300","0.1000000015","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","4.12.191.1","UPS_1_1_OutputVoltage_C","UPS* C相输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.7.2.1.2.3","public","0","0","0","0","0","0","0","0","0","V","300","0.1000000015","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","4.12.191.1","UPS_1_1_OutputCurrent_A","UPS* A相输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.7.2.1.5.1","public","0","0","0","0","0","0","0","0","0","A","300","0.0099999998","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","4.12.191.1","UPS_1_1_OutputCurrent_B","UPS* B相输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.7.2.1.5.2","public","0","0","0","0","0","0","0","0","0","A","300","0.0099999998","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","4.12.191.1","UPS_1_1_OutputCurrent_C","UPS* C相输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.7.2.1.5.3","public","0","0","0","0","0","0","0","0","0","A","300","0.0099999998","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","4.12.191.1","UPS_1_1_OutputLoad_A","UPS* A相输出负载百分比","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.7.2.1.4.1","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["29","4.12.191.1","UPS_1_1_OutputLoad_B","UPS* B相输出负载百分比","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.7.2.1.4.2","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","4.12.191.1","UPS_1_1_OutputLoad_C","UPS* C相输出负载百分比","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.7.2.1.4.3","public","0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","4.12.191.1","UPS_1_1_OutputFrequency_A","UPS* A相输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.7.2.1.3.1","public","0","0","0","0","0","0","0","0","0","Hz","300","0.1000000015","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","4.12.191.1","UPS_1_1_OutputFrequency_B","UPS* B相输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.7.2.1.3.2","public","0","0","0","0","0","0","0","0","0","Hz","300","0.1000000015","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","4.12.191.1","UPS_1_1_OutputFrequency_C","UPS* C相输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.7.2.1.3.3","public","0","0","0","0","0","0","0","0","0","Hz","300","0.1000000015","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","4.12.191.1","UPS_1_1_OutputOnBattery","UPS* 电池供电","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.7.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","5","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","4.12.191.1","UPS_1_1_OutputOnByPass","UPS* 旁路","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.7.4.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","5","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["36","4.12.191.1","UPS_1_1_OutputOverLoad","UPS* 输出过载","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.7.10.0","public","0","0","0","0","0","0","2","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","5","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0"]
["37","4.12.191.1","UPS_1_1_OutputOverTemp","UPS* 输出过温","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.705.1.7.11.0","public","0","0","0","0","0","0","2","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","5","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0"]
["38","4.12.191.1","UPS_1_1_Netstatus","UPS* 通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","191",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]