{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":43,"n_cols":76,"rows_kept":43,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","4.14.25.1","UPS_1_1_BatteryVoltage","UPS* 电池电压","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.2.2","public","0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","4.14.25.1","UPS_1_1_BatteryCurrent","UPS* 电池电流","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.2.3","public","0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","4.14.25.1","UPS_1_1_BatteryChargePercent","UPS* 电池充电量","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.2.4","public","0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","4.14.25.1","UPS_1_1_BatteryStatus","UPS* 电池状态","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.2.5","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","4.14.25.1","UPS_1_1_InputFrequency","UPS* 输入频率","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.3.1","public","0","0","0","0","0","0","0","0","0","Hz","900","0.1000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","4.14.25.1","UPS_1_1_InputVoltage_A","UPS* A相输入电压","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.3.4.1.2.1","public","0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","4.14.25.1","UPS_1_1_InputVoltage_B","UPS* B相输入电压","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.3.4.1.2.2","public","0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","4.14.25.1","UPS_1_1_InputVoltage_C","UPS* C相输入电压","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.3.4.1.2.3","public","0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","4.14.25.1","UPS_1_1_InputCurrent_A","UPS* A相输入电流","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.3.4.1.3.1","public","0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","4.14.25.1","UPS_1_1_InputCurrent_B","UPS* B相输入电流","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.3.4.1.3.2","public","0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","4.14.25.1","UPS_1_1_InputCurrent_C","UPS* C相输入电流","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.3.4.1.3.3","public","0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","4.14.25.1","UPS_1_1_OutputVoltage_A","UPS* A相输出电压","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.4.4.1.2.1","public","0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","4.14.25.1","UPS_1_1_OutputVoltage_B","UPS* B相输出电压","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.4.4.1.2.2","public","0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","4.14.25.1","UPS_1_1_OutputVoltage_C","UPS* C相输出电压","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.4.4.1.2.3","public","0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","4.14.25.1","UPS_1_1_OutputCurrent_A","UPS* A相输出电流","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.4.4.1.3.1","public","0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","4.14.25.1","UPS_1_1_OutputCurrent_B","UPS* B相输出电流","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.4.4.1.3.2","public","0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","4.14.25.1","UPS_1_1_OutputCurrent_C","UPS* C相输出电流","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.4.4.1.3.3","public","0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","4.14.25.1","UPS_1_1_OutputLoad_A","UPS* A相输出负载百分比","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.4.1.1","public","0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["19","4.14.25.1","UPS_1_1_OutputLoad_B","UPS* B相输出负载百分比","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.4.1.2","public","0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","4.14.25.1","UPS_1_1_OutputLoad_C","UPS* C相输出负载百分比","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.4.1.3","public","0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","4.14.25.1","UPS_1_1_OutputFrequency","UPS* 输出频率","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.4.2","public","0","0","0","0","0","0","0","0","0","Hz","900","0.1000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","4.14.25.1","UPS_1_1_BypassVoltage_A","UPS* A相旁路电压","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.5.3.1.2.1","public","0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","4.14.25.1","UPS_1_1_BypassVoltage_B","UPS* B相旁路电压","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.5.3.1.2.2","public","0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","4.14.25.1","UPS_1_1_BypassVoltage_C","UPS* C相旁路电压","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.5.3.1.2.3","public","0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","4.14.25.1","UPS_1_1_BypassFrequency","UPS* 旁路频率","1","0","0","1","0",null,null,"0","60","720","0","1.3.6.1.4.1.534.1.5.1","public","0","0","0","0","0","0","0","0","0","Hz","900","0.1000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","4.14.25.1","UPS_1_1_InternalTemp","UPS* 温度","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.534.1.6.5","public","0","0","0","0","0","0","0","0","0","℃","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","4.14.25.1","UPS_1_1_InternalHumidity","UPS* 湿度","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.534.1.6.6","public","0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","4.14.25.1","UPS_1_1_InternalTempLow","UPS* 温度低","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.534.1.6.9","public","0","0","0","0","0","0","0","0","0","℃","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","4.14.25.1","UPS_1_1_InternalTempHigh","UPS* 温度高","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.534.1.6.10","public","0","0","0","0","0","0","0","0","0","℃","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","4.14.25.1","UPS_1_1_InternalHumidityLow","UPS* 湿度低","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.534.1.6.11","public","0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","4.14.25.1","UPS_1_1_InternalHumidityHigh","UPS* 湿度高","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.534.1.6.12","public","0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","4.14.25.1","UPS_1_1_BatteryPowerLow","UPS* 电池电量低","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.534.1.7.4","public","0","0","0","0","0","0","0","0","0","Kw","900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["33","4.14.25.1","UPS_1_1_OutputOverLoad","UPS* 输出过载","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.534.1.7.7","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["34","4.14.25.1","UPS_1_1_InternalFailure","UPS* 机内故障","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.534.1.7.8","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["35","4.14.25.1","UPS_1_1_InverterFailure","UPS* 逆变器故障","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.534.1.7.10","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["36","4.14.25.1","UPS_1_1_OutputOff","UPS* 输出中断","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.534.1.7.13","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["37","4.14.25.1","UPS_1_1_InputFailure","UPS* 输入故障","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.534.1.7.14","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["38","4.14.25.1","UPS_1_1_BatteryBad","UPS* 电池损坏","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.534.1.7.23","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["39","4.14.25.1","UPS_1_1_ChargerFailed","UPS* 充电器故障","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.534.1.7.32","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["40","4.14.25.1","UPS_1_1_FanFailure","UPS* 风机故障","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.534.1.7.33","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["41","4.14.25.1","UPS_1_1_FuseFailure","UPS* 熔丝故障","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.534.1.7.34","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["42","4.14.25.1","UPS_1_1_LinkStatus","UPS* 通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","25",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]