{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["StoneU"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"StoneU","index":0,"n_rows":87,"n_cols":18,"rows_kept":87,"flags":["formulas_cached_only"]}
["主类","次类","设备品牌","设备型号","设备UID","变量文件名称","界面文件名称","通信方式","通信协议","驱动名称","配置文件","波特率","数据位","停止位","校验位","设备IP","通讯端口","说明"]
["采集模块"]
[null,"干接点","泓格","I_7052","5.1.54.1","采集模块_泓格_I_7052变量.xls","采集模块_泓格_I_7052.stoneu","串口","RS232","icpdas.dll","icpdas.ini",9600,8,1,"NO",null,null,"应用于宏格模块"]
[{"$nulls":3},"I_7053","5.1.54.1","采集模块_泓格_I_7053变量.xls","采集模块_泓格_I_7053.stoneu","串口","RS232","icpdas.dll","icpdas.ini",9600,8,1,"NO",null,null,"应用于宏格模块"]
[{"$nulls":3},"I_7055","5.1.54.1","采集模块_泓格_I_7055变量.xls","采集模块_泓格_I_7055.stoneu","串口","RS232","icpdas.dll","icpdas.ini",9600,8,1,"NO",null,null,"应用于宏格模块"]
[{"$nulls":3},"I_7063","5.1.54.1","采集模块_泓格_I_7063变量.xls","采集模块_泓格_I_7063.stoneu","串口","RS232","icpdas.dll","icpdas.ini",9600,8,1,"NO",null,null,"应用于宏格模块"]
[{"$nulls":3},"I_7065","5.1.54.1","采集模块_泓格_I_7065变量.xls","采集模块_泓格_I_7065.stoneu","串口","RS232","icpdas.dll","icpdas.ini",9600,8,1,"NO",null,null,"应用于宏格模块"]
[null,null,"Akcp","X60",{"$nulls":3},"网络","Snmp","snmp.dll",{"$nulls":6},161]
[null,null,"康耐德","C2000","5.4.63.1","采集模块_康耐德_C2000变量.xls",null,"网络","Modbus Tcp","modbustcp.dll",{"$nulls":6},502]
[null,null,"Sensaphone","IMS1000","5.34.134.1","采集模块_Sensaphone_IMS1000变量.xls"]
[{"$nulls":3},"IMS4000","5.34.135.1","采集模块_Sensaphone_IMS4000变量.xls"]
["环境系统"]
[null,"温湿度"]
[null,null,"万慧通","TH485","5.32.131.1","温湿度_万慧通_TH485变量.xls","温湿度_万慧通_TH485.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,null,"百特瑞","TH802","5.32.131.1","温湿度_百特瑞_TH802变量.xls","温湿度_百特瑞_TH802.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,"空调"]
[null,null,"艾默生","DME3000","6.35.143.1","空调_艾默生_DME3000变量.xls","空调_艾默生_DME3000.stoneu","串口","RS232","MostDevice.dll","DME3000.ini",19200,8,1,"NO"]
[null,null,"艾默生力博特","PEX(Libert新黑色机)、OC485卡","6.16.107.1","空调_艾默生_PEX_OC485变量.xls","空调_艾默生_PEX_OC485.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,null,"艾默生力博特","LibertCM+","6.35.140.1","空调_艾默生_LibertCM+变量.xls","空调_艾默生_LibertCM+.stoneu","串口","RS232","MostDevice.dll","Emerson_CM.ini",9600,8,1,"NO"]
[null,null,"艾默生力博特","PEX","6.16.109.1","空调_艾默生_PEX变量.xls","空调_艾默生_PEX.stoneu","网络","Snmp","snmp.dll",{"$nulls":6},161]
[null,null,"海洛斯","Hirsoll","6.4.83.1","空调_海洛斯_Hirsoll变量.XLS","空调_海洛斯_Hirsoll.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,null,"海瑞氟","Hiref_uACCarel(可能是pCO1,pCO2卡)","6.15.105.1","空调_海瑞氟_uACCarel变量.xls","空调_海瑞氟_uACCarel.stoneu","串口","RS232","Carel.dll","Carel.ini",9600,8,1,"NO"]
[null,null,"思太登高","CAREL(pCO3卡)","6.15.105.1","空调_思太登高_CAREL变量.xls","空调_思太登高_CAREL.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,null,"依米康","EDA2","6.18.111.1","空调_依米康_EDA2变量.xls","空调_依米康_EDA2.stoneu","串口","RS232","MostDevice.dll","Sda_ii.ini",9600,8,1,"NO"]
[null,null,"大金","DAIKIN大金","6.12.102.1","空调_大金_DAIKIN变量.xls","空调_大金_DAIKIN.stoneu","串口","RS232","MostDevice.dll","DaiKin.ini",9600,8,1,"NO"]
[null,null,"施耐德","UG40","6.8.96.1","空调_施耐德_UG40变量.xls","空调_施耐德_UG40.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,null,"菲利克斯","菲利克斯","6.14.104.1","空调_菲利克斯变量.xls","空调_菲利克斯.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,null,"格力","格力TS01","6.30.129.1","空调_格力_格力TS01变量.xls","空调_格力_格力TS01.stoneu","串口","RS232","Carel.dll","Carel.ini",9600,8,1,"NO"]
[null,null,"斯图斯","斯图斯"]
[null,null,"APC","AP9622","4.3.5.1","空调_APC_AP9622变量.xls","空调_APC_AP9622.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,null,"阿尔西","阿尔西","6.14.104.1","空调_阿尔西变量.xls","空调_阿尔西.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,null,"卡洛斯","卡洛斯","6.14.104.1","空调_卡洛斯变量.xls","空调_卡洛斯.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,null,"国祥","国祥","6.1.65.1","空调_国祥变量.xls","空调_国祥.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,"空调外机"]
[null,null,"麦克维尔","Mcquary(MC510, MC501B)","6.54.179.1","空调_麦克维尔_Mcquary变量.xls","空调_麦克维尔_Mcquary.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,"空调内机"]
[null,null,"施耐德","InRow RC","6.20.180.1","空调_施耐德_InRow RC变量.xls","空调_施耐德_InRow RC.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,"漏水检测"]
[null,null,"SToneU","LS6301","7.1.112.1","漏水_SToneU_ls6301变量.xls","漏水_SToneU_ls6301变量.stoneu","串口","Modbus Ascii","modbusasc.dll",null,9600,8,1,"NO"]
[{"$nulls":3},"LDS","7.1.112.1","漏水_LDS变量.xls",null,"串口","Modbus Ascii","modbusasc.dll",null,9600,8,1,"NO"]
[null,null,"法国TTK","FG-SYS","7.33.153.1","漏水_法国TTK_FG-SYS变量.xls","漏水_法国TTK_FG-SYS变量.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[{"$nulls":3},"FG-ALS","7.33.154.1","漏水_法国TTK_FG-ALS变量.xls","漏水_法国TTK_FG-ALS变量.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,null,"美国瑞侃","TTSIM-1","7.33.132.1","漏水_瑞侃TTSIM-1变量.xls","漏水_瑞侃TTSIM-1.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
["动力系统"]
[null,"UPS"]
[null,null,"APC","AP96XX卡","4.3.3.1","UPS_APC_AP96XX卡变量.xls","UPS_APC_AP96XX卡.stoneu","网络","Snmp","snmp.dll",{"$nulls":6},161]
[null,null,"MGE","66061卡","4.12.21.1","UPS_MGE_66061卡变量.xls","UPS_MGE_66061卡.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[{"$nulls":3},"66074卡","4.12.191.1","UPS_MGE_66074卡变量.xls","UPS_MGE_66074卡.stoneu","网络","Snmp","snmp.dll",{"$nulls":6},161]
[null,null,"艾默生","Hipuls_u 1","4.19.36.1","UPS_艾默生_Hipuls_u变量.xls","UPS_艾默生_Hipuls_u.stoneu","网络","Snmp","snmp.dll",{"$nulls":6},161]
[{"$nulls":3},"Hipuls_u 2",{"$nulls":3},"网络","Snmp","snmp.dll",{"$nulls":6},161]
[{"$nulls":3},"Hipulse","4.19.36.1","UPS_艾默生_Hipulse变量.xls","UPS_艾默生_Hipulse.stoneu","串口","RS232","MostDevice.dll","Hipulse_U.ini",9600,8,1,"NO"]
[{"$nulls":3},"NXL","4.19.38.1","UPS_艾默生_NXL变量.xls","UPS_艾默生_NXL.stoneu","网络","Snmp","snmp.dll",{"$nulls":6},161]
[{"$nulls":3},"NXR","4.19.38.1","UPS_艾默生_NXR变量.xls","UPS_艾默生_NXR.stoneu","网络","Snmp","snmp.dll",{"$nulls":6},161]
[{"$nulls":3},"UH11","4.19.43.1","UPS_艾默生_UH11变量.xls","UPS_艾默生_UH11.stoneu","串口","RS232","MostDevice.dll","UpsUH11.ini",9600,8,1,"NO"]
[{"$nulls":3},"UL33","4.19.40.1","UPS_艾默生_UL33变量.xls","UPS_艾默生_UL33.stoneu","串口","RS232","MostDevice.dll","UL33.ini",9600,8,1,"NO"]
[{"$nulls":3},"UH31","4.19.136.1","UPS_艾默生_UH31变量.xls","UPS_艾默生_UH31.stoneu","串口","RS232","MostDevice.dll","UpsUH31.ini",9600,8,1,"NO"]
[{"$nulls":3},"UH31(2台并机)","4.19.40.1","UPS_艾默生_UH312台并机变量.xls","UPS_艾默生_UH312台并机.stoneu","串口","RS232","MostDevice.dll","twouh31.ini",9600,8,1,"NO"]
[null,null,"Santak","发送:RS RD","4.15.31.1","UPS_Santak_发送RS RD变量.xls","UPS_Santak_发送RS RD.stoneu","串口","RS232","MostDevice.dll","ScanTak_3C.ini",2400,8,1,"NO"]
[{"$nulls":3},"发送：Q1 Q4","4.15.30.1","UPS_Santak_发送Q1 Q4变量.XLS","UPS_Santak_发送Q1 Q4.stoneu","串口","RS232","MostDevice.dll","Santak.ini",2400,8,1,"NO"]
[{"$nulls":3},"发送:Q1，地址","4.15.30.1","UPS_Santak_发送Q1，地址变量.xls","UPS_Santak_发送Q1，地址.stoneu","串口","RS232","MostDevice.dll","Santak_ShiWei.ini",2400,8,1,"NO"]
[{"$nulls":3},"凝智SNMP卡","4.15.30.1","UPS_Santak_凝智SNMP卡变量.xls","UPS_Santak_凝智SNMP卡.stoneu","网络","Snmp","snmp.dll",{"$nulls":6},161]
[null,null,"PowerWare","PowerWare","4.14.25.1","UPS_PowerWare变量.xls","UPS_PowerWare.stoneu","网络","Snmp","snmp.dll",{"$nulls":6},161]
[null,null,"爱维达","发送:RS RD","4.15.30.1","UPS_爱维达_发送RS RD变量.xls","UPS_爱维达_发送RS RD.stoneu","串口","RS232","MostDevice.dll","ScanTak_3C.ini",9600,8,1,"NO"]
[null,null,"台达","Delta","4.26.51.1","UPS_台达_Delta变量.xls","UPS_台达_Delta.stoneu","串口","RS232","MostDevice.dll","Delta.ini",4800,8,1,"NO"]
[null,null,"科华","KeLong","4.24.49.1","UPS_科华_KeLong变量.xls","UPS_科华_KeLong.stoneu","串口","RS232","MostDevice.dll","kehua.ini",9600,8,1,"NO"]
[{"$nulls":3},"凝智SNMP卡","4.24.48.1","UPS_科华_凝智SNMP卡变量.xls","UPS_科华_凝智SNMP卡.stoneu","网络","Snmp","snmp.dll",{"$nulls":6},161]
[null,null,"科士达","HiPower","4.19.40.1","UPS_科士达_HiPower变量.xls",null,"串口","Snmp","MostDevice.dll","hipower.ini",9600,8,1,"NO"]
[null,null,"APC","pw9305","4.53.176.1","UPS_APC_pw9305变量.xls","UPS_APC_pw9305.stoneu","串口","RS232","MostDevice.dll","pw9305.ini",9600,8,1,"NO"]
[null,null,"凝智Netmate","凝智Netmate","4.30.185.1","UPS_凝智Netmate变量.xls","UPS_凝智Netmate.stoneu"]
[null,"直流电源"]
[null,null,"艾默生","EmersonM500","14.1.127.1","直流电源_艾默生_EmersonM500变量.xls","直流电源_艾默生_EmersonM500.stoneu","串口","RS232","MostDevice.dll","M84c5z.ini",9600,8,1,"NO"]
[null,null,"万慧通","ADU1000","14.32.190.1","直流电源_万慧通_ADU1000变量.xls","直流电源_万慧通_ADU1000.stoneu","串口","RS232","MostDevice.dll","BatteryAdu.ini",9600,8,1,"NO"]
[{"$nulls":3},"ADU2000","14.1.127.1","直流电源_万慧通_ADU2000变量.xls","直流电源_万慧通_ADU2000.stoneu","串口","RS232","MostDevice.dll","BatteryAdu2000.ini",9600,8,1,"NO"]
[null,null,"旺文","4组24节电池一组","9.3.119.1","直流电源_旺文_4组24节电池一组变量.xls","直流电源_旺文_4组24节电池一组.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,"电量仪"]
[null,null,"雅达","YD2010","9.1.114.1","电量仪_雅达_YD2010变量.xls","电量仪_雅达_YD2010.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,null,"亚特尔","EM300","9.6.192.1","电量仪_亚特尔_EM300变量.xls","电量仪_亚特尔_EM300.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[{"$nulls":3},"PK6200","9.1.114.1","电量仪_亚特尔_PK6200变量.xls","电量仪_亚特尔_PK6200.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,null,"格锐","GR100","9.35.139.1","电量仪_格锐_GR100变量.xls","电量仪_格锐_GR100.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[{"$nulls":3},"GR100-NEW","9.35.136.1","电量仪_格锐_GR100-NEW变量.xls","电量仪_格锐_GR100-NEW.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,null,"派诺","600B","9.2.116.1","电量仪_派诺_600B变量.xls","电量仪_派诺_600B.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[{"$nulls":3},"派诺900","9.2.118.1","电量仪_派诺_900变量.xls","电量仪_派诺_900.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,null,"索科曼","DIRIS_AP","9.4.183.1","电量仪_索科曼_DIRIS_AP变量.xls","电量仪_索科曼_DIRIS_AP.stoneu","串口","Modbus Rtu","modbusrtu.dll",null,9600,8,1,"NO"]
[null,null,"贝思特实业","YD2020",{"$nulls":3},"串口"]
["消防系统"]
["安保系统"]
["IT系统"]