{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["验收"],"not_rendered":{"external_links":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"验收","index":0,"n_rows":96,"n_cols":6,"rows_kept":96,"merged":[[5,0,7,0],[5,1,7,1],[8,0,9,0],[8,1,9,1],[13,0,14,0],[13,1,14,1],[23,0,24,0],[23,1,24,1],[25,0,26,0],[25,1,26,1],[28,0,29,0],[28,1,29,1],[32,0,34,0],[32,1,34,1],[36,0,37,0],[36,1,37,1],[39,0,42,0],[39,1,42,1],[44,0,45,0],[44,1,45,1],[46,0,47,0],[46,1,47,1],[49,0,52,0],[49,1,52,1],[53,0,54,0],[53,1,54,1],[56,0,57,0],[56,1,57,1],[58,0,59,0],[58,1,59,1],[60,0,61,0],[60,1,61,1],[62,0,64,0],[62,1,64,1],[66,0,70,0],[66,1,70,1],[71,0,74,0],[71,1,74,1],[75,0,76,0],[75,1,76,1],[77,0,78,0],[77,1,78,1],[79,0,81,0],[79,1,81,1],[82,0,83,0],[82,1,83,1],[85,0,86,0],[85,1,86,1],[87,0,88,0],[87,1,88,1]],"flags":["formulas_cached_only"]}
["SToneU isP-CMS 机房监控系统 测试验收报告"]
[]
["序号","项目","验收方法","验收内容","结果","备注"]
["一","主端"]
[1,"Windows OS","若重启3次或不间断运行24小时而不死机，则OK","操作系统稳定性","□"]
[2,"PostgreSQL数据库","若数值显示正常，则OK","数据库配置正确","□"]
[null,null,"若数值显示正常，则OK","数据库服务自启动","□"]
[null,null,"若客户端能够正常连接，则OK","ODBC连接正常","□"]
[3,"TTS服务","若拨打电话时，语音正常，则OK","文字转换为语音","□"]
[null,null,"若拨打电话时，语音正常，则OK","声音清楚","□"]
[4,"IIS服务","若通过Web访问，则OK","右击 我的电脑\\管理\\服务和应用程序\\Internet 信息服务，查看IIS服务启用","□"]
[5,"Web浏览","若通过Web访问，则OK","通过Web浏览器查看状态","□"]
[6,"服务端","若重启3次或不间断运行24小时而不死机，则OK","服务端稳定","□"]
[7,"客户端","若重启3次或不间断运行24小时而不死机，则OK","客户端稳定","□"]
[null,null,"若点击软件每页面的关联按钮而正确切换，则OK","正确切换页面","□"]
[8,"双屏显示系统","若两个显示器都能显示，则OK","连接两个显示器，软件显示在两个显示器上","□"]
["二","报警"]
[1,"电话语音报警","若报警，则OK","触发某报警，该系统自动拨号、报警并播报语音","□"]
[2,"短信报警","若报警，则OK","触发某报警，该系统自动发送报警短息","□"]
[3,"本地多媒体报警","若报警，则OK","触发某报警，该系统自动报警并播报语音","□"]
[4,"本地声光报警","若报警，则OK","触发某报警，该系统自动以声光形式报警","□"]
[4,"Email","若报警，则OK","触发某报警，该系统自动以c形式报警","□"]
["三","采集器"]
[1,"采集器(RS485，泓格，KND等)","若采集到数据，则OK","通信正常","□"]
[null,null,"若数据正确，则OK","采集正常","□"]
[2,"AKCP SP系列","若采集到数据，则OK","通信正常","□"]
[null,null,"若数据正确，则OK","采集正常","□"]
[3,"串口卡(CP114等)","若转发串口正常，则OK","虚拟串口正常","□"]
[4,"串口服务器(I-7188E5-485等)","若采集到数据，则OK","通信正常","□"]
[null,null,"若转发串口正常，则OK","虚拟串口成功","□"]
[5,"串口转换(I-7520)","若转发串口正常，则OK","RS-232转化RS-485成功","□"]
["四","环境"]
[1,"定位漏水检测","若采集到数据，则OK","通信正常"]
[null,null,"若检测到漏水报警，则OK","检查漏水感应线的分布位置，模拟漏水，报警","□"]
[null,null,"若检测到的与实际相符，则OK","位置正确","□"]
[2,"不定位漏水检测","若检测到漏水报警，则OK","测试漏水并报警","□"]
[3,"温湿度RS485","若采集到数据，则OK","通信正常","□"]
[null,null,"若检测到的与实际相符，则OK","检查所采集温湿度与实际相符","□"]
[4,"温湿度(非RS485)","若检测到的与实际相符，则OK","检查所采集温湿度与实际相符","□"]
[5,"精密空调","若采集到数据，则OK","通信正常","□"]
[null,null,"若检测到的与实际相符，则OK","检查所采集的数值量正确","□"]
[null,null,"若检测到的与实际相符，则OK","状态量正确","□"]
[null,null,"若检测到的与实际相符，则OK","报警量正确","□"]
[6,"sAC-2501","若停电后来电，空调开启，则OK","来电开启空调","□"]
[7,"新风机系统DI DO","若检测到的与实际相符，则OK","正确地显示开启或关闭；","□"]
[null,null,"若完成指定动作，则OK","正确地控制开启或关闭；","□"]
[8,"干接点桥","若报警，则OK","精密空调报警","□"]
[null,null,"若报警，则OK","定位漏水报警","□"]
["五","动力"]
[1,"UPS","若采集到数据，则OK","通信正常","□"]
[null,null,"若检测到的与实际相符，则OK","检查所采集的数值量正确","□"]
[null,null,"若检测到的与实际相符，则OK","状态量正确","□"]
[null,null,"若检测到的与实际相符，则OK","报警量正确","□"]
[2,"电量仪","若采集到数据，则OK","通信正常","□"]
[null,null,"若检测到的与实际相符，则OK","检查所采集的数值量正确","□"]
[3,"YDDC3U","若报警，则OK","电压偏高或偏低报警","□"]
[4,"供配电开关DI","若检测到的与实际相符，则OK","合上供配电开关，显示合闸状态","□"]
[null,null,"若检测到的与实际相符，则OK","断开供配电开关，显示跳闸状态。","□"]
[5,"蓄电池系统","若采集到数据，则OK","通信正常","□"]
[null,null,"若检测到的与实际相符，则OK","软件能正确显示数据","□"]
[6,"防雷系统DI","若检测到的与实际相符，则OK","采集模块(例如I-7052)输入端连接12V电压，软件显示防雷器状态为损坏","□"]
[null,null,"若检测到的与实际相符，则OK","采集模块输入端断开12V电压，软件显示防雷器状态为正常","□"]
[7,"干接点桥","若报警，则OK","UPS报警","□"]
[null,null,"若报警，则OK","发电机报警","□"]
[null,null,"若报警，则OK","蓄电池系统报警","□"]
["六","安防"]
[1,"视频系统","若采集到数据，则OK","通信正常","□"]
[null,null,"若清晰，则OK","检查所采集图象清晰","□"]
[null,null,"若完成指定动作，则OK","正常移动","□"]
[null,null,"若完成指定动作，则OK","正常录像","□"]
[null,null,"若完成指定动作，则OK","正常回放","□"]
[2,"门禁","若采集到数据，则OK","通信正常","□"]
[null,null,"若完成指定动作，则OK","刷已授权卡，门禁控制器开门","□"]
[null,null,"若完成指定动作，则OK","刷非授权卡，门禁控制器不开门","□"]
[null,null,"若检测到的与实际相符，则OK","软件显示刷卡事件","□"]
[3,"红外系统DI","若检测到的与实际相符，则OK","探头正常状态时，软件显示正常","□"]
[null,null,"若检测到的与实际相符，则OK","探头不正常状态时，软件显示不正常","□"]
[4,"防盗系统DI","若检测到的与实际相符，则OK","探头正常状态时，软件显示正常","□"]
[null,null,"若检测到的与实际相符，则OK","探头不正常状态时，软件显示不正常","□"]
[5,"门磁及照明监控","若完成指定动作，则OK","门打开时，灯亮","□"]
[null,null,"若检测到的与实际相符，则OK","软件显示报警信息","□"]
[null,null,"若完成指定动作，则OK","并触发录像","□"]
[6,"干接点桥","若报警，则OK","视频系统报警","□"]
[null,null,"若报警，则OK","门禁系统报警","□"]
["七","消防"]
[1,"消防系统DI","若检测到的与实际相符，则OK","探头正常状态时，软件显示正常","□"]
[null,null,"若检测到的与实际相符，则OK","探头不正常状态时，软件显示不正常","□"]
[2,"干接点桥","若报警，则OK","VESDA报警","□"]
[null,null,"若报警，则OK","FM200报警","□"]
["八","网络"]
[1,"Ping","若报警，则OK","Ping 网络设备成功","□"]
[]
[]
[null,"测试人：",null,"验收人："]
[]
[null,"日  期：",null,"日  期："]