{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["变量dat文件","CSpreadSheetBackup"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":54,"n_cols":76,"rows_kept":54,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","9.1.114.2","PMC53X_1_PhaseVoltageUa","市电输出配电 A相电压","10402","4","2","3","40000",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.2","PMC53X_1_PhaseVoltageUb","市电输出配电 B相电压","10402","4","2","3","40002",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.2","PMC53X_1_PhaseVoltageUc","市电输出配电 C相电压","10402","4","2","3","40004",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","9.1.114.2","PMC53X_1_PhaseAverVoltage","市电输出配电 相平均电压","10402","4","2","3","40006",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","9.1.114.2","PMC53X_1_LineVoltageUab","市电输出配电 AB线电压","10402","4","2","3","40008",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","9.1.114.2","PMC53X_1_LineVoltageUbc","市电输出配电 BC线电压","10402","4","2","3","40010",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","9.1.114.2","PMC53X_1_LineVoltageUca","市电输出配电 CA线电压","10402","4","2","3","40012",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","9.1.114.2","PMC53X_1_LineAverVoltage","市电输出配电 线平均电压","10402","4","2","3","40014",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","9.1.114.2","PMC53X_1_PhaseCurrentIa","市电输出配电 A相电流","10402","4","2","3","40016",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","9.1.114.2","PMC53X_1_PhaseCurrentIb","市电输出配电 B相电流","10402","4","2","3","40018",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","9.1.114.2","PMC53X_1_PhaseCurrentIc","市电输出配电 C相电流","10402","4","2","3","40020",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","9.1.114.2","PMC53X_1_PhaseAverCurrent","市电输出配电 相平均电流","10402","4","2","3","40022",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","9.1.114.2","PMC53X_1_PhaseActivePowerPa","市电输出配电 A相有功功率","10401","4","2","3","40024",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.2","PMC53X_1_PhaseActivePowerPb","市电输出配电 B相有功功率","10401","4","2","3","40026",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","9.1.114.2","PMC53X_1_PhaseActivePowerPc","市电输出配电 C相有功功率","10401","4","2","3","40028",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","9.1.114.2","PMC53X_1_PhaseTotalActivePower","市电输出配电 相总有功功率","10401","4","2","3","40030",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","9.1.114.2","PMC53X_1_PhaseReActivePowerPa","市电输出配电 A相无功功率","10401","4","2","3","40032",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KAVR","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","9.1.114.2","PMC53X_1_PhaseReActivePowerPb","市电输出配电 B相无功功率","10401","4","2","3","40034",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KAVR","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","9.1.114.2","PMC53X_1_PhaseReActivePowerPc","市电输出配电 C相无功功率","10401","4","2","3","40036",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KAVR","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","9.1.114.2","PMC53X_1_PhaseTotalReActivePower","市电输出配电 相总无功功率","10401","4","2","3","40038",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KAVR","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","9.1.114.2","PMC53X_1_Frequency","市电输出配电 频率","4","2","1","3","40052",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.2","PMC53X_1_InPut_PositivePV","市电输出配电 输入有功电能","10402","4","2","3","40100",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Kwh","300","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.2","PMC53X_1_OutPut_PositivePV","市电输出配电 输出有功电能","10402","4","2","3","40102",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Kwh","300","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.2","PMC53X_1_InPut_NegativePV","市电输出配电 输入无功电能","10402","4","2","3","40106",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Kwh","300","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.2","PMC53X_1_OutPut_NegativePV","市电输出配电 输出无功电能","10402","4","2","3","40108",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.2","PMC53X_1_Communications","市电输出配电 通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
[]
["1","9.1.114.3","PMC53X_2_PhaseVoltageUa","新UPS输出配电 A相电压","10402","4","2","3","40000",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.3","PMC53X_2_PhaseVoltageUb","新UPS输出配电 B相电压","10402","4","2","3","40002",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.3","PMC53X_2_PhaseVoltageUc","新UPS输出配电 C相电压","10402","4","2","3","40004",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","9.1.114.3","PMC53X_2_PhaseAverVoltage","新UPS输出配电 相平均电压","10402","4","2","3","40006",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","9.1.114.3","PMC53X_2_LineVoltageUab","新UPS输出配电 AB线电压","10402","4","2","3","40008",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","9.1.114.3","PMC53X_2_LineVoltageUbc","新UPS输出配电 BC线电压","10402","4","2","3","40010",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","9.1.114.3","PMC53X_2_LineVoltageUca","新UPS输出配电 CA线电压","10402","4","2","3","40012",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","9.1.114.3","PMC53X_2_LineAverVoltage","新UPS输出配电 线平均电压","10402","4","2","3","40014",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","9.1.114.3","PMC53X_2_PhaseCurrentIa","新UPS输出配电 A相电流","10402","4","2","3","40016",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","9.1.114.3","PMC53X_2_PhaseCurrentIb","新UPS输出配电 B相电流","10402","4","2","3","40018",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","9.1.114.3","PMC53X_2_PhaseCurrentIc","新UPS输出配电 C相电流","10402","4","2","3","40020",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","9.1.114.3","PMC53X_2_PhaseAverCurrent","新UPS输出配电 相平均电流","10402","4","2","3","40022",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","9.1.114.3","PMC53X_2_PhaseActivePowerPa","新UPS输出配电 A相有功功率","10401","4","2","3","40024",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.3","PMC53X_2_PhaseActivePowerPb","新UPS输出配电 B相有功功率","10401","4","2","3","40026",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","9.1.114.3","PMC53X_2_PhaseActivePowerPc","新UPS输出配电 C相有功功率","10401","4","2","3","40028",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","9.1.114.3","PMC53X_2_PhaseTotalActivePower","新UPS输出配电 相总有功功率","10401","4","2","3","40030",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","9.1.114.3","PMC53X_2_PhaseReActivePowerPa","新UPS输出配电 A相无功功率","10401","4","2","3","40032",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KAVR","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","9.1.114.3","PMC53X_2_PhaseReActivePowerPb","新UPS输出配电 B相无功功率","10401","4","2","3","40034",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KAVR","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","9.1.114.3","PMC53X_2_PhaseReActivePowerPc","新UPS输出配电 C相无功功率","10401","4","2","3","40036",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KAVR","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","9.1.114.3","PMC53X_2_PhaseTotalReActivePower","新UPS输出配电 相总无功功率","10401","4","2","3","40038",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KAVR","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","9.1.114.3","PMC53X_2_Frequency","新UPS输出配电 频率","4","2","1","3","40052",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.3","PMC53X_2_InPut_PositivePV","新UPS输出配电 输入有功电能","10402","4","2","3","40100",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Kwh","300","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.3","PMC53X_2_OutPut_PositivePV","新UPS输出配电 输出有功电能","10402","4","2","3","40102",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Kwh","300","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.3","PMC53X_2_InPut_NegativePV","新UPS输出配电 输入无功电能","10402","4","2","3","40106",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Kwh","300","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.3","PMC53X_2_OutPut_NegativePV","新UPS输出配电 输出无功电能","10402","4","2","3","40108",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.3","PMC53X_2_Communications","新UPS输出配电 通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]

{"sheet":"CSpreadSheetBackup","index":1,"n_rows":27,"n_cols":76,"rows_kept":27,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","9.1.114.1","PMC53X_1_PhaseVoltageUa","1号电量仪 A相电压","4","2","1","3","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","PMC53X_1_PhaseVoltageUb","1号电量仪 B相电压","4","2","1","3","2",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","PMC53X_1_PhaseVoltageUc","1号电量仪 C相电压","4","2","1","3","4",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","9.1.114.1","PMC53X_1_PhaseAverVoltage","1号电量仪 相平均电压","4","2","1","3","6",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","9.1.114.1","PMC53X_1_LineVoltageUca","1号电量仪 A线电压","4","2","1","3","8",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","9.1.114.1","PMC53X_1_LineVoltageUab","1号电量仪 B线电压","4","2","1","3","10",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","9.1.114.1","PMC53X_1_LineVoltageUbc","1号电量仪 C线电压","4","2","1","3","12",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","9.1.114.1","PMC53X_1_LineAverVoltage","1号电量仪 线平均电压","4","2","1","3","14",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","9.1.114.1","PMC53X_1_PhaseCurrentIa","1号电量仪 A相电流","4","2","1","3","16",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","9.1.114.1","PMC53X_1_PhaseCurrentIb","1号电量仪 B相电流","4","2","1","3","18",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","9.1.114.1","PMC53X_1_PhaseCurrentIc","1号电量仪 C相电流","4","2","1","3","20",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","9.1.114.1","PMC53X_1_PhaseAverCurrent","1号电量仪 相平均电流","4","2","1","3","22",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","9.1.114.1","PMC53X_1_PhaseActivePowerPa","1号电量仪 A相有功功率","3","2","1","3","24",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.1","PMC53X_1_PhaseActivePowerPb","1号电量仪 B相有功功率","3","2","1","3","26",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","9.1.114.1","PMC53X_1_PhaseActivePowerPc","1号电量仪 C相有功功率","3","2","1","3","28",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","9.1.114.1","PMC53X_1_PhaseTotalActivePower","1号电量仪 相总有功功率","3","2","1","3","30",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","9.1.114.1","PMC53X_1_PhaseReActivePowerPa","1号电量仪 A相无功功率","3","2","1","3","32",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KAVR","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","9.1.114.1","PMC53X_1_PhaseReActivePowerPb","1号电量仪 B相无功功率","3","2","1","3","34",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KAVR","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","9.1.114.1","PMC53X_1_PhaseReActivePowerPc","1号电量仪 C相无功功率","3","2","1","3","36",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KAVR","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","9.1.114.1","PMC53X_1_PhaseTotalReActivePower","1号电量仪 相总无功功率","3","2","1","3","38",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","KAVR","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","9.1.114.1","PMC53X_1_Frequency","1号电量仪 频率","4","2","1","3","52",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.1","PMC53X_1_InPut_PositivePV","1号电量仪 输入有功电能","4","2","1","3","100",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Kwh","300","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.1","PMC53X_1_OutPut_PositivePV","1号电量仪 输出有功电能","4","2","1","3","102",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Kwh","300","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.1","PMC53X_1_InPut_NegativePV","1号电量仪 输入无功电能","4","2","1","3","106",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Kwh","300","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.1","PMC53X_1_OutPut_NegativePV","1号电量仪 输出无功电能","4","2","1","3","108",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.1","PMC53X_1_Communications","1号电量仪 通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]