{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["变量dat文件","CSpreadSheetBackup"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":80,"n_cols":76,"rows_kept":80,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","7.1.112.1","Leak_Alarm","主机房漏水","10007","6","3","4","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","112",null,null,"0","0","0",{"$nulls":10},"0","0","5","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","3","1,2,4,","断线,漏水,硬件故障,"]
["2","7.1.112.1","Leak_Comstatus","漏水设备通信状态","1000","0","3","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","112",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线告警,"]
["3","5.29.128.1","AKCP_Temp1","配电间温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.16.1.3.0","public","0","0","0","0","15","35","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"20","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","5.29.128.1","AKCP_Humidity1","配电间湿度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.17.1.3.0","public","0","0","0","0","20","90","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"60","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","5.29.128.1","AKCP_Leak","漏水","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.18.1.3.8","public","0","0","0","0","0","0","2","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"2","0","5","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","4,","报警,"]
["6","5.29.128.1","AKCP_Comstatus","网络采集设备通信状态","1000","0","3","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线告警,"]
["7","6.30.129.1","THR10_1_Temp","主机房温度","10004","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","5","35","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","129",null,null,"0","0","0",{"$nulls":10},"20","0","100","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.30.129.1","THR10_1_Humidity","主机房湿度","10005","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","5","85","0","0","0","%","300","0.1000000000","3","0","1","1","0","0","0","0","129",null,null,"0","0","0",{"$nulls":10},"60","0","100","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.30.129.1","THR10_1_Model1","开机","4","65280","2","5","0",null,null,"0","30","60","0",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","1","0","0","0","0","0","0","129",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.30.129.1","THR10_1_Model2","关机","4","65280","2","5","1",null,null,"0","30","60","0",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","1","0","0","0","0","0","0","129",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","6.30.129.1","THR10_1_LinkStatus","通信状态","1000","0","0","2","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","129",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["12","9.1.114.1","YD2010_1_PhaseVoltageUa","电量仪A相电压","4","2","1","3","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","9.1.114.1","YD2010_1_LineVoltageUca","电量仪A线电压","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.1","YD2010_1_PhaseCurrentIa","电量仪A相电流","4","2","1","3","4",null,null,"0","30","60","1",null,null,"5","0","100","0","0","0","0","0","0","A","300","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","9.1.114.1","YD2010_1_PhaseActivePowerPa","电量仪A相有功功率","3","2","1","3","8",null,null,"0","30","60","1",null,null,"5","0","100","0","0","0","0","0","0","KW","300","0.0004000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","9.1.114.1","YD2010_1_PhaseVoltageUb","电量仪B相电压","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","9.1.114.1","YD2010_1_LineVoltageUab","电量仪B线电压","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","9.1.114.1","YD2010_1_PhaseCurrentIb","电量仪B相电流","4","2","1","3","20",null,null,"0","30","60","1",null,null,"5","0","100","0","0","0","0","0","0","A","300","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","9.1.114.1","YD2010_1_PhaseActivePowerPb","电量仪B相有功功率","3","2","1","3","24",null,null,"0","30","60","1",null,null,"5","0","100","0","0","0","0","0","0","KW","300","0.0004000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","9.1.114.1","YD2010_1_PhaseVoltageUc","电量仪C相电压","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","9.1.114.1","YD2010_1_LineVoltageUbc","电量仪C线电压","4","2","1","3","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.1","YD2010_1_PhaseCurrentIc","电量仪C相电流","4","2","1","3","36",null,null,"0","30","60","1",null,null,"5","0","100","0","0","0","0","0","0","A","300","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.1","YD2010_1_PhaseActivePowerPc","电量仪C相有功功率","3","2","1","3","40",null,null,"0","30","60","1",null,null,"5","0","100","0","0","0","0","0","0","KW","300","0.0004000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.1","YD2010_1_Frequency","电量仪频率","4","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.1","YD2010_1_Netstatus","电量仪通信","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["26","4.14.26.1","XCP_1_OutputLineVoltageAB","输出线电压AB","1","0","0","1","0","cmd-15","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","v","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["27","4.14.26.1","XCP_1_OutputLineVoltageBC","输出线电压BC","1","0","0","1","0","cmd-16","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","v","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["28","4.14.26.1","XCP_1_OutputLineVoltageAC","输出线电压AC","1","0","0","1","0","cmd-17","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","v","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["29","4.14.26.1","XCP_1_InputLineVoltageAB","输入线电压AB","1","0","0","1","0","cmd-18","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","v","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["30","4.14.26.1","XCP_1_InputLineVoltageBC","输入线电压BC","1","0","0","1","0","cmd-19","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","v","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["31","4.14.26.1","XCP_1_InputLineVoltageAC","输入线电压AC","1","0","0","1","0","cmd-20","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","v","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["32","4.14.26.1","XCP_1_BypassLineInputVoltageAB","旁路输入线电压AB","1","0","0","1","0","cmd-21","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","v","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["33","4.14.26.1","XCP_1_BypassLineInputVoltageBC","旁路输入线电压BC","1","0","0","1","0","cmd-22","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","v","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["34","4.14.26.1","XCP_1_BypassLineInputVoltageCA","旁路输入线电压CA","1","0","0","1","0","cmd-23","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","v","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["35","4.14.26.1","XCP_1_InputCurrentA","输入电流A相","1","0","0","1","0","cmd-24","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["36","4.14.26.1","XCP_1_InputCurrentB","输入电流B相","1","0","0","1","0","cmd-25","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["37","4.14.26.1","XCP_1_InputCurrentC","输入电流C相","1","0","0","1","0","cmd-26","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["38","4.14.26.1","XCP_1_OutputPower","输出功率（W）","1","0","0","1","0","cmd-27","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["39","4.14.26.1","XCP_1_OutputApparentPower","输出视在功率（VA）","1","0","0","1","0","cmd-29","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","va","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["40","4.14.26.1","XCP_1_OutputFrequency","输出频率","1","0","0","1","0","cmd-33","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["41","4.14.26.1","XCP_1_InputFrequency","输入频率","1","0","0","1","0","cmd-34","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["42","4.14.26.1","XCP_1_InverterFrequency","逆变器频率","1","0","0","1","0","cmd-35","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["43","4.14.26.1","XCP_1_BypassFrequency","旁路频率","1","0","0","1","0","cmd-36","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["44","4.14.26.1","XCP_1_BatteryElectricCurrent","电池电流","1","0","0","1","0","cmd-37","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","-100","100","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["45","4.14.26.1","XCP_1_BatteryVoltage","电池电压","1","0","0","1","0","cmd-38","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["46","4.14.26.1","XCP_1_BatteryRemainingPercentage","电池剩余百分比","1","0","0","1","0","cmd-39","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["47","4.14.26.1","XCP_1_BatteryRemainingTime","电池剩余时间","1","0","0","1","0","cmd-40","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","S","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","99999999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["48","4.14.26.1","XCP_1_APhaseLoadCurrent","A相负载电流","1","0","0","1","0","cmd-44","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["49","4.14.26.1","XCP_1_BPhaseLoadCurrent","B相负载电流","1","0","0","1","0","cmd-45","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["50","4.14.26.1","XCP_1_CPhaseLoadCurrent","C相负载电流","1","0","0","1","0","cmd-46","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["51","4.14.26.1","XCP_1_InverterVoltagePressure","逆变器电压过压","1","0","0","1","0","cmd-54","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["52","4.14.26.1","XCP_1_InverterVoltageOwePressure","逆变器电压欠压","1","0","0","1","0","cmd-55","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["53","4.14.26.1","XCP_1_MoreLimitedFrequencyInverter","逆变器频率越限","1","0","0","1","0","cmd-56","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["54","4.14.26.1","XCP_1_BypassVoltageOver","旁路电压过压","1","0","0","1","0","cmd-57","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["55","4.14.26.1","XCP_1_BypassVoltageOwePressur","旁路电压欠压","1","0","0","1","0","cmd-58","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["56","4.14.26.1","XCP_1_BypassMoreLimitedFrequency","旁路频率越限","1","0","0","1","0","cmd-59","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["57","4.14.26.1","XCP_1_InputVoltageOver","输入电压过压","1","0","0","1","0","cmd-60","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["58","4.14.26.1","XCP_1_InputVoltageOwePressure","输入电压欠压","1","0","0","1","0","cmd-61","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["59","4.14.26.1","XCP_1_InputFrequencyMoreLimited","输入频率越限","1","0","0","1","0","cmd-62","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["60","4.14.26.1","XCP_1_OutputVoltageOver","输出电压过压","1","0","0","1","0","cmd-63","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["61","4.14.26.1","XCP_1_OutputVoltageOwePressure","输出电压欠压","1","0","0","1","0","cmd-64","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["62","4.14.26.1","XCP_1_OutputFrequencyMoreLimited","输出频率越限","1","0","0","1","0","cmd-65","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["63","4.14.26.1","XCP_1_OutputOverload","输出过载","1","0","0","1","0","cmd-66","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["64","4.14.26.1","XCP_1_RectifierFault","整流器故障","1","0","0","1","0","cmd-69","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["65","4.14.26.1","XCP_1_InverterFault","逆变器故障","1","0","0","1","0","cmd-70","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["66","4.14.26.1","XCP_1_BatteryConnectionFailure","电池连接故障","1","0","0","1","0","cmd-71","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["67","4.14.26.1","XCP_1_BypassSwitchFault","旁路开关故障","1","0","0","1","0","cmd-72","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["68","4.14.26.1","XCP_1_BatteryCurrentLimit","电池电流越限","1","0","0","1","0","cmd-76","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["69","4.14.26.1","XCP_1_Shutdown","关机","1","0","0","1","0","cmd-78","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["70","4.14.26.1","XCP_1_BatteryVoltage","电池欠压","1","0","0","1","0","cmd-79","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["71","4.14.26.1","XCP_1_PowerSupplyFault","供电故障","1","0","0","1","0","cmd-81","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["72","4.14.26.1","XCP_1_RadiatorOverTemperature","散热器超温","1","0","0","1","0","cmd-82","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["73","4.14.26.1","XCP_1_TheRadiatorTemperatureFeelingFault","散热器温感故障","1","0","0","1","0","cmd-83","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["74","4.14.26.1","XCP_1_EmergencyShutdown","紧急关机","1","0","0","1","0","cmd-86","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["75","4.14.26.1","XCP_1_BatteryPowerSupply","由电池供电","1","0","0","1","0","cmd-92","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["76","4.14.26.1","XCP_1_TurnBypassWork","转旁路工作","1","0","0","1","0","cmd-93","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["77","4.14.26.1","XCP_1_BatteriesNeedToReplace","电池需替换","1","0","0","1","0","cmd-94","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["78","4.14.26.1","XCP_1_FanFault","风扇故障","1","0","0","1","0","cmd-95","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["79","4.14.26.1","XCP_1_Communications","通信状态","1000","0","0","1","0",null,null,"0","60","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]

{"sheet":"CSpreadSheetBackup","index":1,"n_rows":80,"n_cols":76,"rows_kept":80,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","7.1.112.1","Leak_Alarm","主机房漏水","10007","6","3","4","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","112",null,null,"0","0","0",{"$nulls":10},"0","0","5","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","3","1,2,4,","断线,漏水,硬件故障,"]
["2","7.1.112.1","Leak_Comstatus","漏水设备通信状态","1000","0","3","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","112",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线告警,"]
["3","5.29.128.1","AKCP_Temp1","配电间温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.16.1.3.0","public","0","0","0","0","15","35","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"20","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","5.29.128.1","AKCP_Humidity1","配电间湿度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.17.1.3.0","public","0","0","0","0","20","90","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"60","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","5.29.128.1","AKCP_Leak","漏水","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.18.1.3.8","public","0","0","0","0","0","0","2","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"2","0","5","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","4,","报警,"]
["6","5.29.128.1","AKCP_Comstatus","网络采集设备通信状态","1000","0","3","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线告警,"]
["7","6.30.129.1","THR10_1_Temp","主机房温度","10004","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","5","35","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","129",null,null,"0","0","0",{"$nulls":10},"20","0","100","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.30.129.1","THR10_1_Humidity","主机房湿度","10005","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","5","85","0","0","0","%","300","0.1000000000","3","0","1","1","0","0","0","0","129",null,null,"0","0","0",{"$nulls":10},"60","0","100","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.30.129.1","THR10_1_Model1","开机","4","65280","2","5","0",null,null,"0","30","60","0",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","1","0","0","0","0","0","0","129",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.30.129.1","THR10_1_Model2","关机","4","65280","2","5","1",null,null,"0","30","60","0",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","1","0","0","0","0","0","0","129",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","6.30.129.1","THR10_1_LinkStatus","通信状态","1000","0","0","2","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","129",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["12","9.1.114.1","YD2010_1_PhaseVoltageUa","电量仪A相电压","4","2","1","3","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","9.1.114.1","YD2010_1_LineVoltageUca","电量仪A线电压","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.1","YD2010_1_PhaseCurrentIa","电量仪A相电流","4","2","1","3","4",null,null,"0","30","60","1",null,null,"5","0","100","0","0","0","0","0","0","A","300","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","9.1.114.1","YD2010_1_PhaseActivePowerPa","电量仪A相有功功率","3","2","1","3","8",null,null,"0","30","60","1",null,null,"5","0","100","0","0","0","0","0","0","KW","300","0.0004000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","9.1.114.1","YD2010_1_PhaseVoltageUb","电量仪B相电压","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","9.1.114.1","YD2010_1_LineVoltageUab","电量仪B线电压","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","9.1.114.1","YD2010_1_PhaseCurrentIb","电量仪B相电流","4","2","1","3","20",null,null,"0","30","60","1",null,null,"5","0","100","0","0","0","0","0","0","A","300","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","9.1.114.1","YD2010_1_PhaseActivePowerPb","电量仪B相有功功率","3","2","1","3","24",null,null,"0","30","60","1",null,null,"5","0","100","0","0","0","0","0","0","KW","300","0.0004000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","9.1.114.1","YD2010_1_PhaseVoltageUc","电量仪C相电压","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","9.1.114.1","YD2010_1_LineVoltageUbc","电量仪C线电压","4","2","1","3","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.1","YD2010_1_PhaseCurrentIc","电量仪C相电流","4","2","1","3","36",null,null,"0","30","60","1",null,null,"5","0","100","0","0","0","0","0","0","A","300","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.1","YD2010_1_PhaseActivePowerPc","电量仪C相有功功率","3","2","1","3","40",null,null,"0","30","60","1",null,null,"5","0","100","0","0","0","0","0","0","KW","300","0.0004000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.1","YD2010_1_Frequency","电量仪频率","4","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.1","YD2010_1_Netstatus","电量仪通信","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["26","4.14.26.1","XCP_1_OutputLineVoltageAB","输出线电压AB","1","0","0","1","0","cmd-15","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","v","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["27","4.14.26.1","XCP_1_OutputLineVoltageBC","输出线电压BC","1","0","0","1","0","cmd-16","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","v","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["28","4.14.26.1","XCP_1_OutputLineVoltageAC","输出线电压AC","1","0","0","1","0","cmd-17","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","v","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["29","4.14.26.1","XCP_1_InputLineVoltageAB","输入线电压AB","1","0","0","1","0","cmd-18","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","v","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["30","4.14.26.1","XCP_1_InputLineVoltageBC","输入线电压BC","1","0","0","1","0","cmd-19","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","v","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["31","4.14.26.1","XCP_1_InputLineVoltageAC","输入线电压AC","1","0","0","1","0","cmd-20","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","v","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["32","4.14.26.1","XCP_1_BypassLineInputVoltageAB","旁路输入线电压AB","1","0","0","1","0","cmd-21","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","v","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["33","4.14.26.1","XCP_1_BypassLineInputVoltageBC","旁路输入线电压BC","1","0","0","1","0","cmd-22","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","v","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["34","4.14.26.1","XCP_1_BypassLineInputVoltageCA","旁路输入线电压CA","1","0","0","1","0","cmd-23","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","v","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["35","4.14.26.1","XCP_1_InputCurrentA","输入电流A相","1","0","0","1","0","cmd-24","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["36","4.14.26.1","XCP_1_InputCurrentB","输入电流B相","1","0","0","1","0","cmd-25","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["37","4.14.26.1","XCP_1_InputCurrentC","输入电流C相","1","0","0","1","0","cmd-26","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["38","4.14.26.1","XCP_1_OutputPower","输出功率（W）","1","0","0","1","0","cmd-27","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["39","4.14.26.1","XCP_1_OutputApparentPower","输出视在功率（VA）","1","0","0","1","0","cmd-29","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","va","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["40","4.14.26.1","XCP_1_OutputFrequency","输出频率","1","0","0","1","0","cmd-33","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["41","4.14.26.1","XCP_1_InputFrequency","输入频率","1","0","0","1","0","cmd-34","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["42","4.14.26.1","XCP_1_InverterFrequency","逆变器频率","1","0","0","1","0","cmd-35","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["43","4.14.26.1","XCP_1_BypassFrequency","旁路频率","1","0","0","1","0","cmd-36","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["44","4.14.26.1","XCP_1_BatteryElectricCurrent","电池电流","1","0","0","1","0","cmd-37","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","-100","100","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["45","4.14.26.1","XCP_1_BatteryVoltage","电池电压","1","0","0","1","0","cmd-38","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["46","4.14.26.1","XCP_1_BatteryRemainingPercentage","电池剩余百分比","1","0","0","1","0","cmd-39","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["47","4.14.26.1","XCP_1_BatteryRemainingTime","电池剩余时间","1","0","0","1","0","cmd-40","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","S","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","99999999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["48","4.14.26.1","XCP_1_APhaseLoadCurrent","A相负载电流","1","0","0","1","0","cmd-44","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["49","4.14.26.1","XCP_1_BPhaseLoadCurrent","B相负载电流","1","0","0","1","0","cmd-45","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["50","4.14.26.1","XCP_1_CPhaseLoadCurrent","C相负载电流","1","0","0","1","0","cmd-46","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0"]
["51","4.14.26.1","XCP_1_InverterVoltagePressure","逆变器电压过压","1","0","0","1","0","cmd-54","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["52","4.14.26.1","XCP_1_InverterVoltageOwePressure","逆变器电压欠压","1","0","0","1","0","cmd-55","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["53","4.14.26.1","XCP_1_MoreLimitedFrequencyInverter","逆变器频率越限","1","0","0","1","0","cmd-56","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["54","4.14.26.1","XCP_1_BypassVoltageOver","旁路电压过压","1","0","0","1","0","cmd-57","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["55","4.14.26.1","XCP_1_BypassVoltageOwePressur","旁路电压欠压","1","0","0","1","0","cmd-58","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["56","4.14.26.1","XCP_1_BypassMoreLimitedFrequency","旁路频率越限","1","0","0","1","0","cmd-59","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["57","4.14.26.1","XCP_1_InputVoltageOver","输入电压过压","1","0","0","1","0","cmd-60","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["58","4.14.26.1","XCP_1_InputVoltageOwePressure","输入电压欠压","1","0","0","1","0","cmd-61","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["59","4.14.26.1","XCP_1_InputFrequencyMoreLimited","输入频率越限","1","0","0","1","0","cmd-62","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["60","4.14.26.1","XCP_1_OutputVoltageOver","输出电压过压","1","0","0","1","0","cmd-63","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["61","4.14.26.1","XCP_1_OutputVoltageOwePressure","输出电压欠压","1","0","0","1","0","cmd-64","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["62","4.14.26.1","XCP_1_OutputFrequencyMoreLimited","输出频率越限","1","0","0","1","0","cmd-65","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["63","4.14.26.1","XCP_1_OutputOverload","输出过载","1","0","0","1","0","cmd-66","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["64","4.14.26.1","XCP_1_RectifierFault","整流器故障","1","0","0","1","0","cmd-69","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["65","4.14.26.1","XCP_1_InverterFault","逆变器故障","1","0","0","1","0","cmd-70","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["66","4.14.26.1","XCP_1_BatteryConnectionFailure","电池连接故障","1","0","0","1","0","cmd-71","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["67","4.14.26.1","XCP_1_BypassSwitchFault","旁路开关故障","1","0","0","1","0","cmd-72","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["68","4.14.26.1","XCP_1_BatteryCurrentLimit","电池电流越限","1","0","0","1","0","cmd-76","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["69","4.14.26.1","XCP_1_Shutdown","关机","1","0","0","1","0","cmd-78","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["70","4.14.26.1","XCP_1_BatteryVoltage","电池欠压","1","0","0","1","0","cmd-79","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["71","4.14.26.1","XCP_1_PowerSupplyFault","供电故障","1","0","0","1","0","cmd-81","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["72","4.14.26.1","XCP_1_RadiatorOverTemperature","散热器超温","1","0","0","1","0","cmd-82","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["73","4.14.26.1","XCP_1_TheRadiatorTemperatureFeelingFault","散热器温感故障","1","0","0","1","0","cmd-83","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["74","4.14.26.1","XCP_1_EmergencyShutdown","紧急关机","1","0","0","1","0","cmd-86","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["75","4.14.26.1","XCP_1_BatteryPowerSupply","由电池供电","1","0","0","1","0","cmd-92","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["76","4.14.26.1","XCP_1_TurnBypassWork","转旁路工作","1","0","0","1","0","cmd-93","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["77","4.14.26.1","XCP_1_BatteriesNeedToReplace","电池需替换","1","0","0","1","0","cmd-94","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["78","4.14.26.1","XCP_1_FanFault","风扇故障","1","0","0","1","0","cmd-95","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","1","1,","报警,"]
["79","4.14.26.1","XCP_1_Communications","通信状态","1000","0","0","1","0",null,null,"0","60","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","26",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]