{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":347,"n_cols":76,"rows_kept":347,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["70","4.19.137.1","Spm1_Src1_APhaseVol","1号SPM源1_A相电压","3","2","1","3","7000",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["71","4.19.137.1","Spm1_Src1_BPhaseVol","1号SPM源1_B相电压","3","2","1","3","7001",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["72","4.19.137.1","Spm1_Src1_CPhaseVol","1号SPM源1_C相电压","3","2","1","3","7002",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["73","4.19.137.1","Spm1_Src1_APhaseCurr","1号SPM源1_A相电流","3","2","1","3","7003",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["74","4.19.137.1","Spm1_Src1_BPhaseCurr","1号SPM源1_B相电流","3","2","1","3","7004",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["75","4.19.137.1","Spm1_Src1_CPhaseCurr","1号SPM源1_C相电流","3","2","1","3","7005",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["76","4.19.137.1","Spm1_Src1_Freq","1号SPM源1_频率","3","2","1","3","7006",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["77","4.19.137.1","Spm1_Slip1_Curr","1号SPM支路1_电流","3","2","1","3","7010",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["78","4.19.137.1","Spm1_Slip1_Status","1号SPM支路1_开关状态","3","2","1","3","7138",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["79","4.19.137.1","Spm1_Slip2_Curr","1号SPM支路2_电流","3","2","1","3","7011",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["80","4.19.137.1","Spm1_Slip2_Status","1号SPM支路2_开关状态","3","2","1","3","7139",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["81","4.19.137.1","Spm1_Slip3_Curr","1号SPM支路3_电流","3","2","1","3","7012",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["82","4.19.137.1","Spm1_Slip3_Status","1号SPM支路3_开关状态","3","2","1","3","7140",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["83","4.19.137.1","Spm1_Slip4_Curr","1号SPM支路4_电流","3","2","1","3","7013",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["84","4.19.137.1","Spm1_Slip4_Status","1号SPM支路4_开关状态","3","2","1","3","7141",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["85","4.19.137.1","Spm1_Slip5_Curr","1号SPM支路5_电流","3","2","1","3","7014",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["86","4.19.137.1","Spm1_Slip5_Status","1号SPM支路5_开关状态","3","2","1","3","7142",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["87","4.19.137.1","Spm1_Slip6_Curr","1号SPM支路6_电流","3","2","1","3","7015",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["88","4.19.137.1","Spm1_Slip6_Status","1号SPM支路6_开关状态","3","2","1","3","7143",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["89","4.19.137.1","Spm1_Slip7_Curr","1号SPM支路7_电流","3","2","1","3","7016",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["90","4.19.137.1","Spm1_Slip7_Status","1号SPM支路7_开关状态","3","2","1","3","7144",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["91","4.19.137.1","Spm1_Slip8_Curr","1号SPM支路8_电流","3","2","1","3","7017",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["92","4.19.137.1","Spm1_Slip8_Status","1号SPM支路8_开关状态","3","2","1","3","7145",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["93","4.19.137.1","Spm1_Slip9_Curr","1号SPM支路9_电流","3","2","1","3","7018",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["94","4.19.137.1","Spm1_Slip9_Status","1号SPM支路9_开关状态","3","2","1","3","7146",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["95","4.19.137.1","Spm1_Slip10_Curr","1号SPM支路10_电流","3","2","1","3","7019",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["96","4.19.137.1","Spm1_Slip10_Status","1号SPM支路10_开关状态","3","2","1","3","7147",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["97","4.19.137.1","Spm1_Slip11_Curr","1号SPM支路11_电流","3","2","1","3","7020",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["98","4.19.137.1","Spm1_Slip11_Status","1号SPM支路11_开关状态","3","2","1","3","7148",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["99","4.19.137.1","Spm1_Slip12_Curr","1号SPM支路12_电流","3","2","1","3","7021",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["100","4.19.137.1","Spm1_Slip12_Status","1号SPM支路12_开关状态","3","2","1","3","7149",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["101","4.19.137.1","Spm1_Slip13_Curr","1号SPM支路13_电流","3","2","1","3","7022",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["102","4.19.137.1","Spm1_Slip13_Status","1号SPM支路13_开关状态","3","2","1","3","7150",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["103","4.19.137.1","Spm1_Slip14_Curr","1号SPM支路14_电流","3","2","1","3","7023",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["104","4.19.137.1","Spm1_Slip14_Status","1号SPM支路14_开关状态","3","2","1","3","7151",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["105","4.19.137.1","Spm1_Slip15_Curr","1号SPM支路15_电流","3","2","1","3","7024",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["106","4.19.137.1","Spm1_Slip15_Status","1号SPM支路15_开关状态","3","2","1","3","7152",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["107","4.19.137.1","Spm1_Slip16_Curr","1号SPM支路16_电流","3","2","1","3","7025",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["108","4.19.137.1","Spm1_Slip16_Status","1号SPM支路16_开关状态","3","2","1","3","7153",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["109","4.19.137.1","Spm1_Slip17_Curr","1号SPM支路17_电流","3","2","1","3","7026",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["110","4.19.137.1","Spm1_Slip17_Status","1号SPM支路17_开关状态","3","2","1","3","7154",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["111","4.19.137.1","Spm1_Slip18_Curr","1号SPM支路18_电流","3","2","1","3","7027",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["112","4.19.137.1","Spm1_Slip18_Status","1号SPM支路18_开关状态","3","2","1","3","7155",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["113","4.19.137.1","Spm1_Slip19_Curr","1号SPM支路19_电流","3","2","1","3","7028",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["114","4.19.137.1","Spm1_Slip19_Status","1号SPM支路19_开关状态","3","2","1","3","7156",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["115","4.19.137.1","Spm1_Slip20_Curr","1号SPM支路20_电流","3","2","1","3","7029",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["116","4.19.137.1","Spm1_Slip20_Status","1号SPM支路20_开关状态","3","2","1","3","7157",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["117","4.19.137.1","Spm1_Slip21_Curr","1号SPM支路21_电流","3","2","1","3","7030",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["118","4.19.137.1","Spm1_Slip21_Status","1号SPM支路21_开关状态","3","2","1","3","7158",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["119","4.19.137.1","Spm1_Slip22_Curr","1号SPM支路22_电流","3","2","1","3","7031",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["120","4.19.137.1","Spm1_Slip22_Status","1号SPM支路22_开关状态","3","2","1","3","7159",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["121","4.19.137.1","Spm1_Slip23_Curr","1号SPM支路23_电流","3","2","1","3","7032",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["122","4.19.137.1","Spm1_Slip23_Status","1号SPM支路23_开关状态","3","2","1","3","7160",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["123","4.19.137.1","Spm1_Slip24_Curr","1号SPM支路24_电流","3","2","1","3","7033",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["124","4.19.137.1","Spm1_Slip24_Status","1号SPM支路24_开关状态","3","2","1","3","7161",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["125","4.19.137.1","Spm1_Slip25_Curr","1号SPM支路25_电流","3","2","1","3","7034",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["126","4.19.137.1","Spm1_Slip25_Status","1号SPM支路25_开关状态","3","2","1","3","7162",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["127","4.19.137.1","Spm1_Slip26_Curr","1号SPM支路26_电流","3","2","1","3","7035",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["128","4.19.137.1","Spm1_Slip26_Status","1号SPM支路26_开关状态","3","2","1","3","7163",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["129","4.19.137.1","Spm1_Slip27_Curr","1号SPM支路27_电流","3","2","1","3","7036",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["130","4.19.137.1","Spm1_Slip27_Status","1号SPM支路27_开关状态","3","2","1","3","7164",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["131","4.19.137.1","Spm1_Slip28_Curr","1号SPM支路28_电流","3","2","1","3","7037",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["132","4.19.137.1","Spm1_Slip28_Status","1号SPM支路28_开关状态","3","2","1","3","7165",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["133","4.19.137.1","Spm1_Slip29_Curr","1号SPM支路29_电流","3","2","1","3","7038",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["134","4.19.137.1","Spm1_Slip29_Status","1号SPM支路29_开关状态","3","2","1","3","7166",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["135","4.19.137.1","Spm1_Slip30_Curr","1号SPM支路30_电流","3","2","1","3","7039",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["136","4.19.137.1","Spm1_Slip30_Status","1号SPM支路30_开关状态","3","2","1","3","7167",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["137","4.19.137.1","Spm1_Slip31_Curr","1号SPM支路31_电流","3","2","1","3","7040",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["138","4.19.137.1","Spm1_Slip31_Status","1号SPM支路31_开关状态","3","2","1","3","7168",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["139","4.19.137.1","Spm1_Slip32_Curr","1号SPM支路32_电流","3","2","1","3","7041",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["140","4.19.137.1","Spm1_Slip32_Status","1号SPM支路32_开关状态","3","2","1","3","7169",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["141","4.19.137.1","Spm1_Slip33_Curr","1号SPM支路33_电流","3","2","1","3","7042",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["142","4.19.137.1","Spm1_Slip33_Status","1号SPM支路33_开关状态","3","2","1","3","7170",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["143","4.19.137.1","Spm1_Slip34_Curr","1号SPM支路34_电流","3","2","1","3","7043",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["144","4.19.137.1","Spm1_Slip34_Status","1号SPM支路34_开关状态","3","2","1","3","7171",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["145","4.19.137.1","Spm1_Slip35_Curr","1号SPM支路35_电流","3","2","1","3","7044",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["146","4.19.137.1","Spm1_Slip35_Status","1号SPM支路35_开关状态","3","2","1","3","7172",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["147","4.19.137.1","Spm1_Slip36_Curr","1号SPM支路36_电流","3","2","1","3","7045",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["148","4.19.137.1","Spm1_Slip36_Status","1号SPM支路36_开关状态","3","2","1","3","7173",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["149","4.19.137.1","Spm1_Slip37_Curr","1号SPM支路37_电流","3","2","1","3","7046",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["150","4.19.137.1","Spm1_Slip37_Status","1号SPM支路37_开关状态","3","2","1","3","7174",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["151","4.19.137.1","Spm1_Slip38_Curr","1号SPM支路38_电流","3","2","1","3","7047",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["152","4.19.137.1","Spm1_Slip38_Status","1号SPM支路38_开关状态","3","2","1","3","7175",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["153","4.19.137.1","Spm1_Slip39_Curr","1号SPM支路39_电流","3","2","1","3","7048",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["154","4.19.137.1","Spm1_Slip39_Status","1号SPM支路39_开关状态","3","2","1","3","7176",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["155","4.19.137.1","Spm1_Slip40_Curr","1号SPM支路40_电流","3","2","1","3","7049",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["156","4.19.137.1","Spm1_Slip40_Status","1号SPM支路40_开关状态","3","2","1","3","7177",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["157","4.19.137.1","Spm1_Slip41_Curr","1号SPM支路41_电流","3","2","1","3","7050",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["158","4.19.137.1","Spm1_Slip41_Status","1号SPM支路41_开关状态","3","2","1","3","7178",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["159","4.19.137.1","Spm1_Slip42_Curr","1号SPM支路42_电流","3","2","1","3","7051",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["160","4.19.137.1","Spm1_Slip42_Status","1号SPM支路42_开关状态","3","2","1","3","7179",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["161","4.19.137.1","Spm1_Slip43_Curr","1号SPM支路43_电流","3","2","1","3","7052",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["162","4.19.137.1","Spm1_Slip43_Status","1号SPM支路43_开关状态","3","2","1","3","7180",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["163","4.19.137.1","Spm1_Slip44_Curr","1号SPM支路44_电流","3","2","1","3","7053",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["164","4.19.137.1","Spm1_Slip44_Status","1号SPM支路44_开关状态","3","2","1","3","7181",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["165","4.19.137.1","Spm1_Slip45_Curr","1号SPM支路45_电流","3","2","1","3","7054",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["166","4.19.137.1","Spm1_Slip45_Status","1号SPM支路45_开关状态","3","2","1","3","7182",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["167","4.19.137.1","Spm1_Slip46_Curr","1号SPM支路46_电流","3","2","1","3","7055",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["168","4.19.137.1","Spm1_Slip46_Status","1号SPM支路46_开关状态","3","2","1","3","7183",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["169","4.19.137.1","Spm1_Slip47_Curr","1号SPM支路47_电流","3","2","1","3","7056",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["170","4.19.137.1","Spm1_Slip47_Status","1号SPM支路47_开关状态","3","2","1","3","7184",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["171","4.19.137.1","Spm1_Slip48_Curr","1号SPM支路48_电流","3","2","1","3","7057",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["172","4.19.137.1","Spm1_Slip48_Status","1号SPM支路48_开关状态","3","2","1","3","7185",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["173","4.19.137.1","Spm1_Slip49_Curr","1号SPM支路49_电流","3","2","1","3","7058",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["174","4.19.137.1","Spm1_Slip49_Status","1号SPM支路49_开关状态","3","2","1","3","7186",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["175","4.19.137.1","Spm1_Slip50_Curr","1号SPM支路50_电流","3","2","1","3","7059",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["176","4.19.137.1","Spm1_Slip50_Status","1号SPM支路50_开关状态","3","2","1","3","7187",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["177","4.19.137.1","Spm1_Slip51_Curr","1号SPM支路51_电流","3","2","1","3","7060",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["178","4.19.137.1","Spm1_Slip51_Status","1号SPM支路51_开关状态","3","2","1","3","7188",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["179","4.19.137.1","Spm1_Slip52_Curr","1号SPM支路52_电流","3","2","1","3","7061",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["180","4.19.137.1","Spm1_Slip52_Status","1号SPM支路52_开关状态","3","2","1","3","7189",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["181","4.19.137.1","Spm1_Slip53_Curr","1号SPM支路53_电流","3","2","1","3","7062",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["182","4.19.137.1","Spm1_Slip53_Status","1号SPM支路53_开关状态","3","2","1","3","7190",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["183","4.19.137.1","Spm1_Slip54_Curr","1号SPM支路54_电流","3","2","1","3","7063",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["184","4.19.137.1","Spm1_Slip54_Status","1号SPM支路54_开关状态","3","2","1","3","7191",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["185","4.19.137.1","Spm1_Slip55_Curr","1号SPM支路55_电流","3","2","1","3","7064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["186","4.19.137.1","Spm1_Slip55_Status","1号SPM支路55_开关状态","3","2","1","3","7192",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["187","4.19.137.1","Spm1_Slip56_Curr","1号SPM支路56_电流","3","2","1","3","7065",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["188","4.19.137.1","Spm1_Slip56_Status","1号SPM支路56_开关状态","3","2","1","3","7193",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["189","4.19.137.1","Spm1_Slip57_Curr","1号SPM支路57_电流","3","2","1","3","7066",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["190","4.19.137.1","Spm1_Slip57_Status","1号SPM支路57_开关状态","3","2","1","3","7194",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["191","4.19.137.1","Spm1_Slip58_Curr","1号SPM支路58_电流","3","2","1","3","7067",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["192","4.19.137.1","Spm1_Slip58_Status","1号SPM支路58_开关状态","3","2","1","3","7195",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["193","4.19.137.1","Spm1_Slip59_Curr","1号SPM支路59_电流","3","2","1","3","7068",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["194","4.19.137.1","Spm1_Slip59_Status","1号SPM支路59_开关状态","3","2","1","3","7196",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["195","4.19.137.1","Spm1_Slip60_Curr","1号SPM支路60_电流","3","2","1","3","7069",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","4.19.137.1","Spm1_Slip60_Status","1号SPM支路60_开关状态","3","2","1","3","7197",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["197","4.19.137.1","Spm1_Slip61_Curr","1号SPM支路61_电流","3","2","1","3","7070",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["198","4.19.137.1","Spm1_Slip61_Status","1号SPM支路61_开关状态","3","2","1","3","7198",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["199","4.19.137.1","Spm1_Slip62_Curr","1号SPM支路62_电流","3","2","1","3","7071",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["200","4.19.137.1","Spm1_Slip62_Status","1号SPM支路62_开关状态","3","2","1","3","7199",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["201","4.19.137.1","Spm1_Slip63_Curr","1号SPM支路63_电流","3","2","1","3","7072",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["202","4.19.137.1","Spm1_Slip63_Status","1号SPM支路63_开关状态","3","2","1","3","7200",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["203","4.19.137.1","Spm1_Slip64_Curr","1号SPM支路64_电流","3","2","1","3","7073",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["204","4.19.137.1","Spm1_Slip64_Status","1号SPM支路64_开关状态","3","2","1","3","7201",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["205","4.19.137.1","Spm1_Slip65_Curr","1号SPM支路65_电流","3","2","1","3","7074",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["206","4.19.137.1","Spm1_Slip65_Status","1号SPM支路65_开关状态","3","2","1","3","7202",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["207","4.19.137.1","Spm1_Slip66_Curr","1号SPM支路66_电流","3","2","1","3","7075",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["208","4.19.137.1","Spm1_Slip66_Status","1号SPM支路66_开关状态","3","2","1","3","7203",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["209","4.19.137.1","Spm1_Slip67_Curr","1号SPM支路67_电流","3","2","1","3","7076",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["210","4.19.137.1","Spm1_Slip67_Status","1号SPM支路67_开关状态","3","2","1","3","7204",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["211","4.19.137.1","Spm1_Slip68_Curr","1号SPM支路68_电流","3","2","1","3","7077",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["212","4.19.137.1","Spm1_Slip68_Status","1号SPM支路68_开关状态","3","2","1","3","7205",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["213","4.19.137.1","Spm1_Slip69_Curr","1号SPM支路69_电流","3","2","1","3","7078",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["214","4.19.137.1","Spm1_Slip69_Status","1号SPM支路69_开关状态","3","2","1","3","7206",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["215","4.19.137.1","Spm1_Slip70_Curr","1号SPM支路70_电流","3","2","1","3","7079",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["216","4.19.137.1","Spm1_Slip70_Status","1号SPM支路70_开关状态","3","2","1","3","7207",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["217","4.19.137.1","Spm1_Slip71_Curr","1号SPM支路71_电流","3","2","1","3","7080",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["218","4.19.137.1","Spm1_Slip71_Status","1号SPM支路71_开关状态","3","2","1","3","7208",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["219","4.19.137.1","Spm1_Slip72_Curr","1号SPM支路72_电流","3","2","1","3","7081",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["220","4.19.137.1","Spm1_Slip72_Status","1号SPM支路72_开关状态","3","2","1","3","7209",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["221","4.19.137.1","Spm1_Slip73_Curr","1号SPM支路73_电流","3","2","1","3","7082",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["222","4.19.137.1","Spm1_Slip73_Status","1号SPM支路73_开关状态","3","2","1","3","7210",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["223","4.19.137.1","Spm1_Slip74_Curr","1号SPM支路74_电流","3","2","1","3","7083",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["224","4.19.137.1","Spm1_Slip74_Status","1号SPM支路74_开关状态","3","2","1","3","7211",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["225","4.19.137.1","Spm1_Slip75_Curr","1号SPM支路75_电流","3","2","1","3","7084",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["226","4.19.137.1","Spm1_Slip75_Status","1号SPM支路75_开关状态","3","2","1","3","7212",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["227","4.19.137.1","Spm1_Slip76_Curr","1号SPM支路76_电流","3","2","1","3","7085",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["228","4.19.137.1","Spm1_Slip76_Status","1号SPM支路76_开关状态","3","2","1","3","7213",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["229","4.19.137.1","Spm1_Slip77_Curr","1号SPM支路77_电流","3","2","1","3","7086",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["230","4.19.137.1","Spm1_Slip77_Status","1号SPM支路77_开关状态","3","2","1","3","7214",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["231","4.19.137.1","Spm1_Slip78_Curr","1号SPM支路78_电流","3","2","1","3","7087",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["232","4.19.137.1","Spm1_Slip78_Status","1号SPM支路78_开关状态","3","2","1","3","7215",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["233","4.19.137.1","Spm1_Slip79_Curr","1号SPM支路79_电流","3","2","1","3","7088",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["234","4.19.137.1","Spm1_Slip79_Status","1号SPM支路79_开关状态","3","2","1","3","7216",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["235","4.19.137.1","Spm1_Slip80_Curr","1号SPM支路80_电流","3","2","1","3","7089",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["236","4.19.137.1","Spm1_Slip80_Status","1号SPM支路80_开关状态","3","2","1","3","7217",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["237","4.19.137.1","Spm1_Src1_OverVol","1号SPM源1_过压","3","2","1","3","2360",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","16","137",null,null,"0","29","29",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["238","4.19.137.1","Spm1_Src1_UnderVol","1号SPM源1_欠压","3","2","1","3","2360",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","17","137",null,null,"0","30","30",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["239","4.19.137.1","Spm1_Src1_UnderPhase","1号SPM源1_缺相","3","2","1","3","2360",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","18","137",null,null,"0","31","31",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["240","4.19.137.1","Spm1_Src1_PowerDown","1号SPM源1_掉电","3","2","1","3","2360",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","19","137",null,null,"0","32","32",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["241","4.19.137.1","Spm1_Src1_OverCurr","1号SPM源1_过流","3","2","1","3","2360",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","20","137",null,null,"0","33","33",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["242","4.19.137.1","Spm1_Src1_FreqAbnormal","1号SPM源1_频率异常","3","2","1","3","2360",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","24","137",null,null,"0","37","37",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["243","4.19.137.2","Spm2_Src2_APhaseVol","2号SPM源2_A相电压","3","2","1","3","7000",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["244","4.19.137.2","Spm2_Src2_BPhaseVol","2号SPM源2_B相电压","3","2","1","3","7001",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["245","4.19.137.2","Spm2_Src2_CPhaseVol","2号SPM源2_C相电压","3","2","1","3","7002",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["246","4.19.137.2","Spm2_Src2_APhaseCurr","2号SPM源2_A相电流","3","2","1","3","7003",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["247","4.19.137.2","Spm2_Src2_BPhaseCurr","2号SPM源2_B相电流","3","2","1","3","7004",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["248","4.19.137.2","Spm2_Src2_CPhaseCurr","2号SPM源2_C相电流","3","2","1","3","7005",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["249","4.19.137.2","Spm2_Src2_Freq","2号SPM源2_频率","3","2","1","3","7006",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["250","4.19.137.2","Spm2_Slip1_Curr","2号SPM支路1_电流","3","2","1","3","7010",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["251","4.19.137.2","Spm2_Slip1_Status","2号SPM支路1_开关状态","3","2","1","3","7138",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["252","4.19.137.2","Spm2_Slip2_Curr","2号SPM支路2_电流","3","2","1","3","7011",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["253","4.19.137.2","Spm2_Slip2_Status","2号SPM支路2_开关状态","3","2","1","3","7139",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["254","4.19.137.2","Spm2_Slip3_Curr","2号SPM支路3_电流","3","2","1","3","7012",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["255","4.19.137.2","Spm2_Slip3_Status","2号SPM支路3_开关状态","3","2","1","3","7140",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["256","4.19.137.2","Spm2_Slip4_Curr","2号SPM支路4_电流","3","2","1","3","7013",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["257","4.19.137.2","Spm2_Slip4_Status","2号SPM支路4_开关状态","3","2","1","3","7141",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["258","4.19.137.2","Spm2_Slip5_Curr","2号SPM支路5_电流","3","2","1","3","7014",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["259","4.19.137.2","Spm2_Slip5_Status","2号SPM支路5_开关状态","3","2","1","3","7142",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["260","4.19.137.2","Spm2_Slip6_Curr","2号SPM支路6_电流","3","2","1","3","7015",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["261","4.19.137.2","Spm2_Slip6_Status","2号SPM支路6_开关状态","3","2","1","3","7143",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["262","4.19.137.2","Spm2_Slip7_Curr","2号SPM支路7_电流","3","2","1","3","7016",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["263","4.19.137.2","Spm2_Slip7_Status","2号SPM支路7_开关状态","3","2","1","3","7144",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["264","4.19.137.2","Spm2_Slip8_Curr","2号SPM支路8_电流","3","2","1","3","7017",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["265","4.19.137.2","Spm2_Slip8_Status","2号SPM支路8_开关状态","3","2","1","3","7145",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["266","4.19.137.2","Spm2_Slip9_Curr","2号SPM支路9_电流","3","2","1","3","7018",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["267","4.19.137.2","Spm2_Slip9_Status","2号SPM支路9_开关状态","3","2","1","3","7146",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["268","4.19.137.2","Spm2_Slip10_Curr","2号SPM支路10_电流","3","2","1","3","7019",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["269","4.19.137.2","Spm2_Slip10_Status","2号SPM支路10_开关状态","3","2","1","3","7147",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["270","4.19.137.2","Spm2_Slip11_Curr","2号SPM支路11_电流","3","2","1","3","7020",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["271","4.19.137.2","Spm2_Slip11_Status","2号SPM支路11_开关状态","3","2","1","3","7148",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["272","4.19.137.2","Spm2_Slip12_Curr","2号SPM支路12_电流","3","2","1","3","7021",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["273","4.19.137.2","Spm2_Slip12_Status","2号SPM支路12_开关状态","3","2","1","3","7149",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["274","4.19.137.2","Spm2_Slip13_Curr","2号SPM支路13_电流","3","2","1","3","7022",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["275","4.19.137.2","Spm2_Slip13_Status","2号SPM支路13_开关状态","3","2","1","3","7150",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["276","4.19.137.2","Spm2_Slip14_Curr","2号SPM支路14_电流","3","2","1","3","7023",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["277","4.19.137.2","Spm2_Slip14_Status","2号SPM支路14_开关状态","3","2","1","3","7151",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["278","4.19.137.2","Spm2_Slip15_Curr","2号SPM支路15_电流","3","2","1","3","7024",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["279","4.19.137.2","Spm2_Slip15_Status","2号SPM支路15_开关状态","3","2","1","3","7152",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["280","4.19.137.2","Spm2_Slip16_Curr","2号SPM支路16_电流","3","2","1","3","7025",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["281","4.19.137.2","Spm2_Slip16_Status","2号SPM支路16_开关状态","3","2","1","3","7153",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["282","4.19.137.2","Spm2_Slip17_Curr","2号SPM支路17_电流","3","2","1","3","7026",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["283","4.19.137.2","Spm2_Slip17_Status","2号SPM支路17_开关状态","3","2","1","3","7154",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["284","4.19.137.2","Spm2_Slip18_Curr","2号SPM支路18_电流","3","2","1","3","7027",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["285","4.19.137.2","Spm2_Slip18_Status","2号SPM支路18_开关状态","3","2","1","3","7155",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["286","4.19.137.2","Spm2_Slip19_Curr","2号SPM支路19_电流","3","2","1","3","7028",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["287","4.19.137.2","Spm2_Slip19_Status","2号SPM支路19_开关状态","3","2","1","3","7156",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["288","4.19.137.2","Spm2_Slip20_Curr","2号SPM支路20_电流","3","2","1","3","7029",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["289","4.19.137.2","Spm2_Slip20_Status","2号SPM支路20_开关状态","3","2","1","3","7157",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["290","4.19.137.2","Spm2_Slip21_Curr","2号SPM支路21_电流","3","2","1","3","7030",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["291","4.19.137.2","Spm2_Slip21_Status","2号SPM支路21_开关状态","3","2","1","3","7158",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["292","4.19.137.2","Spm2_Slip22_Curr","2号SPM支路22_电流","3","2","1","3","7031",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["293","4.19.137.2","Spm2_Slip22_Status","2号SPM支路22_开关状态","3","2","1","3","7159",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["294","4.19.137.2","Spm2_Slip23_Curr","2号SPM支路23_电流","3","2","1","3","7032",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["295","4.19.137.2","Spm2_Slip23_Status","2号SPM支路23_开关状态","3","2","1","3","7160",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["296","4.19.137.2","Spm2_Slip24_Curr","2号SPM支路24_电流","3","2","1","3","7033",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["297","4.19.137.2","Spm2_Slip24_Status","2号SPM支路24_开关状态","3","2","1","3","7161",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["298","4.19.137.2","Spm2_Slip25_Curr","2号SPM支路25_电流","3","2","1","3","7034",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["299","4.19.137.2","Spm2_Slip25_Status","2号SPM支路25_开关状态","3","2","1","3","7162",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["300","4.19.137.2","Spm2_Slip26_Curr","2号SPM支路26_电流","3","2","1","3","7035",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["301","4.19.137.2","Spm2_Slip26_Status","2号SPM支路26_开关状态","3","2","1","3","7163",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["302","4.19.137.2","Spm2_Slip27_Curr","2号SPM支路27_电流","3","2","1","3","7036",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["303","4.19.137.2","Spm2_Slip27_Status","2号SPM支路27_开关状态","3","2","1","3","7164",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["304","4.19.137.2","Spm2_Slip28_Curr","2号SPM支路28_电流","3","2","1","3","7037",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["305","4.19.137.2","Spm2_Slip28_Status","2号SPM支路28_开关状态","3","2","1","3","7165",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["306","4.19.137.2","Spm2_Slip29_Curr","2号SPM支路29_电流","3","2","1","3","7038",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["307","4.19.137.2","Spm2_Slip29_Status","2号SPM支路29_开关状态","3","2","1","3","7166",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["308","4.19.137.2","Spm2_Slip30_Curr","2号SPM支路30_电流","3","2","1","3","7039",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["309","4.19.137.2","Spm2_Slip30_Status","2号SPM支路30_开关状态","3","2","1","3","7167",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["310","4.19.137.2","Spm2_Slip31_Curr","2号SPM支路31_电流","3","2","1","3","7040",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["311","4.19.137.2","Spm2_Slip31_Status","2号SPM支路31_开关状态","3","2","1","3","7168",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["312","4.19.137.2","Spm2_Slip32_Curr","2号SPM支路32_电流","3","2","1","3","7041",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["313","4.19.137.2","Spm2_Slip32_Status","2号SPM支路32_开关状态","3","2","1","3","7169",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["314","4.19.137.2","Spm2_Slip33_Curr","2号SPM支路33_电流","3","2","1","3","7042",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["315","4.19.137.2","Spm2_Slip33_Status","2号SPM支路33_开关状态","3","2","1","3","7170",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["316","4.19.137.2","Spm2_Slip34_Curr","2号SPM支路34_电流","3","2","1","3","7043",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["317","4.19.137.2","Spm2_Slip34_Status","2号SPM支路34_开关状态","3","2","1","3","7171",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["318","4.19.137.2","Spm2_Slip35_Curr","2号SPM支路35_电流","3","2","1","3","7044",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["319","4.19.137.2","Spm2_Slip35_Status","2号SPM支路35_开关状态","3","2","1","3","7172",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["320","4.19.137.2","Spm2_Slip36_Curr","2号SPM支路36_电流","3","2","1","3","7045",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["321","4.19.137.2","Spm2_Slip36_Status","2号SPM支路36_开关状态","3","2","1","3","7173",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["322","4.19.137.2","Spm2_Slip37_Curr","2号SPM支路37_电流","3","2","1","3","7046",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["323","4.19.137.2","Spm2_Slip37_Status","2号SPM支路37_开关状态","3","2","1","3","7174",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["324","4.19.137.2","Spm2_Slip38_Curr","2号SPM支路38_电流","3","2","1","3","7047",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["325","4.19.137.2","Spm2_Slip38_Status","2号SPM支路38_开关状态","3","2","1","3","7175",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["326","4.19.137.2","Spm2_Slip39_Curr","2号SPM支路39_电流","3","2","1","3","7048",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["327","4.19.137.2","Spm2_Slip39_Status","2号SPM支路39_开关状态","3","2","1","3","7176",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["328","4.19.137.2","Spm2_Slip40_Curr","2号SPM支路40_电流","3","2","1","3","7049",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["329","4.19.137.2","Spm2_Slip40_Status","2号SPM支路40_开关状态","3","2","1","3","7177",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["330","4.19.137.2","Spm2_Slip41_Curr","2号SPM支路41_电流","3","2","1","3","7050",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["331","4.19.137.2","Spm2_Slip41_Status","2号SPM支路41_开关状态","3","2","1","3","7178",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["332","4.19.137.2","Spm2_Slip42_Curr","2号SPM支路42_电流","3","2","1","3","7051",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["333","4.19.137.2","Spm2_Slip42_Status","2号SPM支路42_开关状态","3","2","1","3","7179",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["334","4.19.137.2","Spm2_Slip43_Curr","2号SPM支路43_电流","3","2","1","3","7052",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["335","4.19.137.2","Spm2_Slip43_Status","2号SPM支路43_开关状态","3","2","1","3","7180",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["336","4.19.137.2","Spm2_Slip44_Curr","2号SPM支路44_电流","3","2","1","3","7053",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["337","4.19.137.2","Spm2_Slip44_Status","2号SPM支路44_开关状态","3","2","1","3","7181",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["338","4.19.137.2","Spm2_Slip45_Curr","2号SPM支路45_电流","3","2","1","3","7054",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["339","4.19.137.2","Spm2_Slip45_Status","2号SPM支路45_开关状态","3","2","1","3","7182",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["340","4.19.137.2","Spm2_Slip46_Curr","2号SPM支路46_电流","3","2","1","3","7055",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["341","4.19.137.2","Spm2_Slip46_Status","2号SPM支路46_开关状态","3","2","1","3","7183",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["342","4.19.137.2","Spm2_Slip47_Curr","2号SPM支路47_电流","3","2","1","3","7056",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["343","4.19.137.2","Spm2_Slip47_Status","2号SPM支路47_开关状态","3","2","1","3","7184",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["344","4.19.137.2","Spm2_Slip48_Curr","2号SPM支路48_电流","3","2","1","3","7057",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["345","4.19.137.2","Spm2_Slip48_Status","2号SPM支路48_开关状态","3","2","1","3","7185",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["346","4.19.137.2","Spm2_Slip49_Curr","2号SPM支路49_电流","3","2","1","3","7058",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["347","4.19.137.2","Spm2_Slip49_Status","2号SPM支路49_开关状态","3","2","1","3","7186",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["348","4.19.137.2","Spm2_Slip50_Curr","2号SPM支路50_电流","3","2","1","3","7059",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["349","4.19.137.2","Spm2_Slip50_Status","2号SPM支路50_开关状态","3","2","1","3","7187",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["350","4.19.137.2","Spm2_Slip51_Curr","2号SPM支路51_电流","3","2","1","3","7060",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["351","4.19.137.2","Spm2_Slip51_Status","2号SPM支路51_开关状态","3","2","1","3","7188",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["352","4.19.137.2","Spm2_Slip52_Curr","2号SPM支路52_电流","3","2","1","3","7061",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["353","4.19.137.2","Spm2_Slip52_Status","2号SPM支路52_开关状态","3","2","1","3","7189",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["354","4.19.137.2","Spm2_Slip53_Curr","2号SPM支路53_电流","3","2","1","3","7062",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["355","4.19.137.2","Spm2_Slip53_Status","2号SPM支路53_开关状态","3","2","1","3","7190",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["356","4.19.137.2","Spm2_Slip54_Curr","2号SPM支路54_电流","3","2","1","3","7063",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["357","4.19.137.2","Spm2_Slip54_Status","2号SPM支路54_开关状态","3","2","1","3","7191",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["358","4.19.137.2","Spm2_Slip55_Curr","2号SPM支路55_电流","3","2","1","3","7064",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["359","4.19.137.2","Spm2_Slip55_Status","2号SPM支路55_开关状态","3","2","1","3","7192",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["360","4.19.137.2","Spm2_Slip56_Curr","2号SPM支路56_电流","3","2","1","3","7065",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["361","4.19.137.2","Spm2_Slip56_Status","2号SPM支路56_开关状态","3","2","1","3","7193",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["362","4.19.137.2","Spm2_Slip57_Curr","2号SPM支路57_电流","3","2","1","3","7066",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["363","4.19.137.2","Spm2_Slip57_Status","2号SPM支路57_开关状态","3","2","1","3","7194",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["364","4.19.137.2","Spm2_Slip58_Curr","2号SPM支路58_电流","3","2","1","3","7067",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["365","4.19.137.2","Spm2_Slip58_Status","2号SPM支路58_开关状态","3","2","1","3","7195",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["366","4.19.137.2","Spm2_Slip59_Curr","2号SPM支路59_电流","3","2","1","3","7068",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["367","4.19.137.2","Spm2_Slip59_Status","2号SPM支路59_开关状态","3","2","1","3","7196",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["368","4.19.137.2","Spm2_Slip60_Curr","2号SPM支路60_电流","3","2","1","3","7069",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["369","4.19.137.2","Spm2_Slip60_Status","2号SPM支路60_开关状态","3","2","1","3","7197",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["370","4.19.137.2","Spm2_Slip61_Curr","2号SPM支路61_电流","3","2","1","3","7070",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["371","4.19.137.2","Spm2_Slip61_Status","2号SPM支路61_开关状态","3","2","1","3","7198",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["372","4.19.137.2","Spm2_Slip62_Curr","2号SPM支路62_电流","3","2","1","3","7071",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["373","4.19.137.2","Spm2_Slip62_Status","2号SPM支路62_开关状态","3","2","1","3","7199",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["374","4.19.137.2","Spm2_Slip63_Curr","2号SPM支路63_电流","3","2","1","3","7072",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["375","4.19.137.2","Spm2_Slip63_Status","2号SPM支路63_开关状态","3","2","1","3","7200",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["376","4.19.137.2","Spm2_Slip64_Curr","2号SPM支路64_电流","3","2","1","3","7073",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["377","4.19.137.2","Spm2_Slip64_Status","2号SPM支路64_开关状态","3","2","1","3","7201",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["378","4.19.137.2","Spm2_Slip65_Curr","2号SPM支路65_电流","3","2","1","3","7074",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["379","4.19.137.2","Spm2_Slip65_Status","2号SPM支路65_开关状态","3","2","1","3","7202",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["380","4.19.137.2","Spm2_Slip66_Curr","2号SPM支路66_电流","3","2","1","3","7075",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["381","4.19.137.2","Spm2_Slip66_Status","2号SPM支路66_开关状态","3","2","1","3","7203",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["382","4.19.137.2","Spm2_Slip67_Curr","2号SPM支路67_电流","3","2","1","3","7076",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["383","4.19.137.2","Spm2_Slip67_Status","2号SPM支路67_开关状态","3","2","1","3","7204",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["384","4.19.137.2","Spm2_Slip68_Curr","2号SPM支路68_电流","3","2","1","3","7077",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["385","4.19.137.2","Spm2_Slip68_Status","2号SPM支路68_开关状态","3","2","1","3","7205",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["386","4.19.137.2","Spm2_Slip69_Curr","2号SPM支路69_电流","3","2","1","3","7078",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["387","4.19.137.2","Spm2_Slip69_Status","2号SPM支路69_开关状态","3","2","1","3","7206",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["388","4.19.137.2","Spm2_Slip70_Curr","2号SPM支路70_电流","3","2","1","3","7079",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["389","4.19.137.2","Spm2_Slip70_Status","2号SPM支路70_开关状态","3","2","1","3","7207",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["390","4.19.137.2","Spm2_Slip71_Curr","2号SPM支路71_电流","3","2","1","3","7080",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["391","4.19.137.2","Spm2_Slip71_Status","2号SPM支路71_开关状态","3","2","1","3","7208",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["392","4.19.137.2","Spm2_Slip72_Curr","2号SPM支路72_电流","3","2","1","3","7081",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["393","4.19.137.2","Spm2_Slip72_Status","2号SPM支路72_开关状态","3","2","1","3","7209",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["394","4.19.137.2","Spm2_Slip73_Curr","2号SPM支路73_电流","3","2","1","3","7082",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["395","4.19.137.2","Spm2_Slip73_Status","2号SPM支路73_开关状态","3","2","1","3","7210",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["396","4.19.137.2","Spm2_Slip74_Curr","2号SPM支路74_电流","3","2","1","3","7083",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["397","4.19.137.2","Spm2_Slip74_Status","2号SPM支路74_开关状态","3","2","1","3","7211",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["398","4.19.137.2","Spm2_Slip75_Curr","2号SPM支路75_电流","3","2","1","3","7084",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["399","4.19.137.2","Spm2_Slip75_Status","2号SPM支路75_开关状态","3","2","1","3","7212",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["400","4.19.137.2","Spm2_Slip76_Curr","2号SPM支路76_电流","3","2","1","3","7085",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["401","4.19.137.2","Spm2_Slip76_Status","2号SPM支路76_开关状态","3","2","1","3","7213",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["402","4.19.137.2","Spm2_Slip77_Curr","2号SPM支路77_电流","3","2","1","3","7086",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["403","4.19.137.2","Spm2_Slip77_Status","2号SPM支路77_开关状态","3","2","1","3","7214",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["404","4.19.137.2","Spm2_Slip78_Curr","2号SPM支路78_电流","3","2","1","3","7087",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["405","4.19.137.2","Spm2_Slip78_Status","2号SPM支路78_开关状态","3","2","1","3","7215",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["406","4.19.137.2","Spm2_Slip79_Curr","2号SPM支路79_电流","3","2","1","3","7088",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["407","4.19.137.2","Spm2_Slip79_Status","2号SPM支路79_开关状态","3","2","1","3","7216",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["408","4.19.137.2","Spm2_Slip80_Curr","2号SPM支路80_电流","3","2","1","3","7089",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["409","4.19.137.2","Spm2_Slip80_Status","2号SPM支路80_开关状态","3","2","1","3","7217",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","开关断开,"]
["410","4.19.137.2","Spm2_Src2_OverVol","2号SPM源2_过压","3","2","1","3","2360",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","45","137",null,null,"0","38","38",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["411","4.19.137.2","Spm2_Src2_UnderVol","2号SPM源2_欠压","3","2","1","3","2360",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","46","137",null,null,"0","39","39",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["412","4.19.137.2","Spm2_Src2_UnderPhase","2号SPM源2_缺相","3","2","1","3","2360",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","47","137",null,null,"0","40","40",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["413","4.19.137.2","Spm2_Src2_PowerDown","2号SPM源2_掉电","3","2","1","3","2360",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","48","137",null,null,"0","41","41",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["414","4.19.137.2","Spm2_Src2_OverCurr","2号SPM源2_过流","3","2","1","3","2360",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","49","137",null,null,"0","42","42",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["415","4.19.137.2","Spm2_Src2_FreqAbnormal","2号SPM源2_频率异常","3","2","1","3","2360",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","53","137",null,null,"0","46","46",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]