{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":266,"n_cols":76,"rows_kept":266,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","9.1.114.1","Canatal13_1_Temperature","1号空调 温度","4","2","1","3","248321",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","Canatal13_1_Humidity","1号空调 湿度","4","2","1","3","248322",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","Canatal13_1_BO1","1号空调 积水报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["4","9.1.114.1","Canatal13_1_BO2","1号空调 湿度1高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["5","9.1.114.1","Canatal13_1_BO3","1号空调 湿度2高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["6","9.1.114.1","Canatal13_1_BO4","1号空调 温度1高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["7","9.1.114.1","Canatal13_1_BO5","1号空调 温度2高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["8","9.1.114.1","Canatal13_1_BO6","1号空调 电压高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["9","9.1.114.1","Canatal13_1_BO7","1号空调 湿度1低限报警","3","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["10","9.1.114.1","Canatal13_1_BO8","1号空调 湿度2低限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["11","9.1.114.1","Canatal13_1_BT1","1号空调 温度1低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["12","9.1.114.1","Canatal13_1_BT2","1号空调 温度2低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["13","9.1.114.1","Canatal13_1_BTH1","1号空调 电压低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["14","9.1.114.1","Canatal13_1_BTH2","1号空调 风机报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["15","9.1.114.1","Canatal13_1_BTH3","1号空调 压缩机高压报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["16","9.1.114.1","Canatal13_1_BTH4","1号空调 压缩机低压报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["17","9.1.114.1","Canatal13_1_BTH5","1号空调 加湿器报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["18","9.1.114.1","Canatal13_1_BTH6","1号空调 加热器报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["19","9.1.114.1","Canatal13_1_BTH7","1号空调 隔尘网淤塞报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["20","9.1.114.1","Canatal13_1_BTH8","1号空调 火灾报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","9.1.114.1","Canatal13_1_BF1","1号空调 风机状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.1","Canatal13_1_BF2","1号空调 压缩机状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.1","Canatal13_1_BF3","1号空调 压缩机正启动","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.1","Canatal13_1_BF4","1号空调 能效控制","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.1","Canatal13_1_BF5","1号空调 加湿器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","9.1.114.1","Canatal13_1_BF6","1号空调 加热器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","9.1.114.1","Canatal13_1_BF7","1号空调 除湿器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","9.1.114.1","Canatal13_1_BF8","1号空调 矽控加热器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","9.1.114.1","Canatal13_1_UnitSatus","1号空调 机组状态","4","2","1","3","24961",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","9.1.114.1","Canatal13_1_On","1号空调 开机控制","4","2","1","6","24960",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","1","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","9.1.114.1","Canatal13_1_Off","1号空调 关机控制","4","2","1","6","24960",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","1","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","9.1.114.1","Canatal13_1_Communications","1号空调 通信状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114","关","开","0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","通信中断,"]
[]
["1","9.1.114.1","Canatal13_2_Temperature","2号空调 温度","4","2","1","3","248321",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","Canatal13_2_Humidity","2号空调 湿度","4","2","1","3","248322",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","Canatal13_2_BO1","2号空调 积水报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["4","9.1.114.1","Canatal13_2_BO2","2号空调 湿度1高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["5","9.1.114.1","Canatal13_2_BO3","2号空调 湿度2高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["6","9.1.114.1","Canatal13_2_BO4","2号空调 温度1高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["7","9.1.114.1","Canatal13_2_BO5","2号空调 温度2高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["8","9.1.114.1","Canatal13_2_BO6","2号空调 电压高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["9","9.1.114.1","Canatal13_2_BO7","2号空调 湿度1低限报警","3","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["10","9.1.114.1","Canatal13_2_BO8","2号空调 湿度2低限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["11","9.1.114.1","Canatal13_2_BT1","2号空调 温度1低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["12","9.1.114.1","Canatal13_2_BT2","2号空调 温度2低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["13","9.1.114.1","Canatal13_2_BTH1","2号空调 电压低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["14","9.1.114.1","Canatal13_2_BTH2","2号空调 风机报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["15","9.1.114.1","Canatal13_2_BTH3","2号空调 压缩机高压报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["16","9.1.114.1","Canatal13_2_BTH4","2号空调 压缩机低压报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["17","9.1.114.1","Canatal13_2_BTH5","2号空调 加湿器报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["18","9.1.114.1","Canatal13_2_BTH6","2号空调 加热器报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["19","9.1.114.1","Canatal13_2_BTH7","2号空调 隔尘网淤塞报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["20","9.1.114.1","Canatal13_2_BTH8","2号空调 火灾报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","9.1.114.1","Canatal13_2_BF1","2号空调 风机状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.1","Canatal13_2_BF2","2号空调 压缩机状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.1","Canatal13_2_BF3","2号空调 压缩机正启动","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.1","Canatal13_2_BF4","2号空调 能效控制","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.1","Canatal13_2_BF5","2号空调 加湿器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","9.1.114.1","Canatal13_2_BF6","2号空调 加热器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","9.1.114.1","Canatal13_2_BF7","2号空调 除湿器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","9.1.114.1","Canatal13_2_BF8","2号空调 矽控加热器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","9.1.114.1","Canatal13_2_UnitSatus","2号空调 机组状态","4","2","1","3","24961",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","9.1.114.1","Canatal13_2_On","2号空调 开机控制","4","2","1","6","24960",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","1","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","9.1.114.1","Canatal13_2_Off","2号空调 关机控制","4","2","1","6","24960",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","1","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","9.1.114.1","Canatal13_2_Communications","2号空调 通信状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114","关","开","0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","通信中断,"]
[]
[]
["1","9.1.114.1","Canatal13_3_Temperature","3号空调 温度","4","2","1","3","248321",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","Canatal13_3_Humidity","3号空调 湿度","4","2","1","3","248322",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","Canatal13_3_BO1","3号空调 积水报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["4","9.1.114.1","Canatal13_3_BO2","3号空调 湿度1高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["5","9.1.114.1","Canatal13_3_BO3","3号空调 湿度2高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["6","9.1.114.1","Canatal13_3_BO4","3号空调 温度1高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["7","9.1.114.1","Canatal13_3_BO5","3号空调 温度2高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["8","9.1.114.1","Canatal13_3_BO6","3号空调 电压高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["9","9.1.114.1","Canatal13_3_BO7","3号空调 湿度1低限报警","3","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["10","9.1.114.1","Canatal13_3_BO8","3号空调 湿度2低限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["11","9.1.114.1","Canatal13_3_BT1","3号空调 温度1低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["12","9.1.114.1","Canatal13_3_BT2","3号空调 温度2低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["13","9.1.114.1","Canatal13_3_BTH1","3号空调 电压低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["14","9.1.114.1","Canatal13_3_BTH2","3号空调 风机报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["15","9.1.114.1","Canatal13_3_BTH3","3号空调 压缩机高压报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["16","9.1.114.1","Canatal13_3_BTH4","3号空调 压缩机低压报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["17","9.1.114.1","Canatal13_3_BTH5","3号空调 加湿器报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["18","9.1.114.1","Canatal13_3_BTH6","3号空调 加热器报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["19","9.1.114.1","Canatal13_3_BTH7","3号空调 隔尘网淤塞报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["20","9.1.114.1","Canatal13_3_BTH8","3号空调 火灾报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","9.1.114.1","Canatal13_3_BF1","3号空调 风机状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.1","Canatal13_3_BF2","3号空调 压缩机状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.1","Canatal13_3_BF3","3号空调 压缩机正启动","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.1","Canatal13_3_BF4","3号空调 能效控制","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.1","Canatal13_3_BF5","3号空调 加湿器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","9.1.114.1","Canatal13_3_BF6","3号空调 加热器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","9.1.114.1","Canatal13_3_BF7","3号空调 除湿器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","9.1.114.1","Canatal13_3_BF8","3号空调 矽控加热器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","9.1.114.1","Canatal13_3_UnitSatus","3号空调 机组状态","4","2","1","3","24961",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","9.1.114.1","Canatal13_3_On","3号空调 开机控制","4","2","1","6","24960",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","1","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","9.1.114.1","Canatal13_3_Off","3号空调 关机控制","4","2","1","6","24960",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","1","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","9.1.114.1","Canatal13_3_Communications","3号空调 通信状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114","关","开","0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","通信中断,"]
[]
["1","9.1.114.1","Canatal13_4_Temperature","4号空调 温度","4","2","1","3","248321",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","Canatal13_4_Humidity","4号空调 湿度","4","2","1","3","248322",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","Canatal13_4_BO1","4号空调 积水报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["4","9.1.114.1","Canatal13_4_BO2","4号空调 湿度1高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["5","9.1.114.1","Canatal13_4_BO3","4号空调 湿度2高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["6","9.1.114.1","Canatal13_4_BO4","4号空调 温度1高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["7","9.1.114.1","Canatal13_4_BO5","4号空调 温度2高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["8","9.1.114.1","Canatal13_4_BO6","4号空调 电压高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["9","9.1.114.1","Canatal13_4_BO7","4号空调 湿度1低限报警","3","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["10","9.1.114.1","Canatal13_4_BO8","4号空调 湿度2低限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["11","9.1.114.1","Canatal13_4_BT1","4号空调 温度1低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["12","9.1.114.1","Canatal13_4_BT2","4号空调 温度2低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["13","9.1.114.1","Canatal13_4_BTH1","4号空调 电压低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["14","9.1.114.1","Canatal13_4_BTH2","4号空调 风机报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["15","9.1.114.1","Canatal13_4_BTH3","4号空调 压缩机高压报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["16","9.1.114.1","Canatal13_4_BTH4","4号空调 压缩机低压报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["17","9.1.114.1","Canatal13_4_BTH5","4号空调 加湿器报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["18","9.1.114.1","Canatal13_4_BTH6","4号空调 加热器报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["19","9.1.114.1","Canatal13_4_BTH7","4号空调 隔尘网淤塞报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["20","9.1.114.1","Canatal13_4_BTH8","4号空调 火灾报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","9.1.114.1","Canatal13_4_BF1","4号空调 风机状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.1","Canatal13_4_BF2","4号空调 压缩机状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.1","Canatal13_4_BF3","4号空调 压缩机正启动","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.1","Canatal13_4_BF4","4号空调 能效控制","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.1","Canatal13_4_BF5","4号空调 加湿器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","9.1.114.1","Canatal13_4_BF6","4号空调 加热器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","9.1.114.1","Canatal13_4_BF7","4号空调 除湿器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","9.1.114.1","Canatal13_4_BF8","4号空调 矽控加热器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","9.1.114.1","Canatal13_4_UnitSatus","4号空调 机组状态","4","2","1","3","24961",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","9.1.114.1","Canatal13_4_On","4号空调 开机控制","4","2","1","6","24960",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","1","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","9.1.114.1","Canatal13_4_Off","4号空调 关机控制","4","2","1","6","24960",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","1","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","9.1.114.1","Canatal13_4_Communications","4号空调 通信状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114","关","开","0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","通信中断,"]
[]
[]
["1","9.1.114.1","Canatal13_5_Temperature","5号空调 温度","4","2","1","3","248321",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","Canatal13_5_Humidity","5号空调 湿度","4","2","1","3","248322",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","Canatal13_5_BO1","5号空调 积水报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["4","9.1.114.1","Canatal13_5_BO2","5号空调 湿度1高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["5","9.1.114.1","Canatal13_5_BO3","5号空调 湿度2高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["6","9.1.114.1","Canatal13_5_BO4","5号空调 温度1高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["7","9.1.114.1","Canatal13_5_BO5","5号空调 温度2高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["8","9.1.114.1","Canatal13_5_BO6","5号空调 电压高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["9","9.1.114.1","Canatal13_5_BO7","5号空调 湿度1低限报警","3","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["10","9.1.114.1","Canatal13_5_BO8","5号空调 湿度2低限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["11","9.1.114.1","Canatal13_5_BT1","5号空调 温度1低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["12","9.1.114.1","Canatal13_5_BT2","5号空调 温度2低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["13","9.1.114.1","Canatal13_5_BTH1","5号空调 电压低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["14","9.1.114.1","Canatal13_5_BTH2","5号空调 风机报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["15","9.1.114.1","Canatal13_5_BTH3","5号空调 压缩机高压报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["16","9.1.114.1","Canatal13_5_BTH4","5号空调 压缩机低压报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["17","9.1.114.1","Canatal13_5_BTH5","5号空调 加湿器报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["18","9.1.114.1","Canatal13_5_BTH6","5号空调 加热器报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["19","9.1.114.1","Canatal13_5_BTH7","5号空调 隔尘网淤塞报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["20","9.1.114.1","Canatal13_5_BTH8","5号空调 火灾报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","9.1.114.1","Canatal13_5_BF1","5号空调 风机状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.1","Canatal13_5_BF2","5号空调 压缩机状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.1","Canatal13_5_BF3","5号空调 压缩机正启动","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.1","Canatal13_5_BF4","5号空调 能效控制","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.1","Canatal13_5_BF5","5号空调 加湿器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","9.1.114.1","Canatal13_5_BF6","5号空调 加热器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","9.1.114.1","Canatal13_5_BF7","5号空调 除湿器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","9.1.114.1","Canatal13_5_BF8","5号空调 矽控加热器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","9.1.114.1","Canatal13_5_UnitSatus","5号空调 机组状态","4","2","1","3","24961",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","9.1.114.1","Canatal13_5_On","5号空调 开机控制","4","2","1","6","24960",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","1","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","9.1.114.1","Canatal13_5_Off","5号空调 关机控制","4","2","1","6","24960",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","1","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","9.1.114.1","Canatal13_5_Communications","5号空调 通信状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114","关","开","0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","通信中断,"]
[]
["1","9.1.114.1","Canatal13_6_Temperature","6号空调 温度","4","2","1","3","248321",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","Canatal13_6_Humidity","6号空调 湿度","4","2","1","3","248322",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","Canatal13_6_BO1","6号空调 积水报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["4","9.1.114.1","Canatal13_6_BO2","6号空调 湿度1高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["5","9.1.114.1","Canatal13_6_BO3","6号空调 湿度2高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["6","9.1.114.1","Canatal13_6_BO4","6号空调 温度1高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["7","9.1.114.1","Canatal13_6_BO5","6号空调 温度2高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["8","9.1.114.1","Canatal13_6_BO6","6号空调 电压高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["9","9.1.114.1","Canatal13_6_BO7","6号空调 湿度1低限报警","3","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["10","9.1.114.1","Canatal13_6_BO8","6号空调 湿度2低限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["11","9.1.114.1","Canatal13_6_BT1","6号空调 温度1低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["12","9.1.114.1","Canatal13_6_BT2","6号空调 温度2低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["13","9.1.114.1","Canatal13_6_BTH1","6号空调 电压低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["14","9.1.114.1","Canatal13_6_BTH2","6号空调 风机报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["15","9.1.114.1","Canatal13_6_BTH3","6号空调 压缩机高压报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["16","9.1.114.1","Canatal13_6_BTH4","6号空调 压缩机低压报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["17","9.1.114.1","Canatal13_6_BTH5","6号空调 加湿器报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["18","9.1.114.1","Canatal13_6_BTH6","6号空调 加热器报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["19","9.1.114.1","Canatal13_6_BTH7","6号空调 隔尘网淤塞报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["20","9.1.114.1","Canatal13_6_BTH8","6号空调 火灾报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","9.1.114.1","Canatal13_6_BF1","6号空调 风机状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.1","Canatal13_6_BF2","6号空调 压缩机状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.1","Canatal13_6_BF3","6号空调 压缩机正启动","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.1","Canatal13_6_BF4","6号空调 能效控制","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.1","Canatal13_6_BF5","6号空调 加湿器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","9.1.114.1","Canatal13_6_BF6","6号空调 加热器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","9.1.114.1","Canatal13_6_BF7","6号空调 除湿器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","9.1.114.1","Canatal13_6_BF8","6号空调 矽控加热器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","9.1.114.1","Canatal13_6_UnitSatus","6号空调 机组状态","4","2","1","3","24961",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","9.1.114.1","Canatal13_6_On","6号空调 开机控制","4","2","1","6","24960",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","1","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","9.1.114.1","Canatal13_6_Off","6号空调 关机控制","4","2","1","6","24960",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","1","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","9.1.114.1","Canatal13_6_Communications","6号空调 通信状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114","关","开","0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","通信中断,"]
[]
["1","9.1.114.1","Canatal13_7_Temperature","7号空调 温度","4","2","1","3","248321",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","Canatal13_7_Humidity","7号空调 湿度","4","2","1","3","248322",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","Canatal13_7_BO1","7号空调 积水报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["4","9.1.114.1","Canatal13_7_BO2","7号空调 湿度1高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["5","9.1.114.1","Canatal13_7_BO3","7号空调 湿度2高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["6","9.1.114.1","Canatal13_7_BO4","7号空调 温度1高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["7","9.1.114.1","Canatal13_7_BO5","7号空调 温度2高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["8","9.1.114.1","Canatal13_7_BO6","7号空调 电压高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["9","9.1.114.1","Canatal13_7_BO7","7号空调 湿度1低限报警","3","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["10","9.1.114.1","Canatal13_7_BO8","7号空调 湿度2低限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["11","9.1.114.1","Canatal13_7_BT1","7号空调 温度1低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["12","9.1.114.1","Canatal13_7_BT2","7号空调 温度2低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["13","9.1.114.1","Canatal13_7_BTH1","7号空调 电压低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["14","9.1.114.1","Canatal13_7_BTH2","7号空调 风机报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["15","9.1.114.1","Canatal13_7_BTH3","7号空调 压缩机高压报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["16","9.1.114.1","Canatal13_7_BTH4","7号空调 压缩机低压报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["17","9.1.114.1","Canatal13_7_BTH5","7号空调 加湿器报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["18","9.1.114.1","Canatal13_7_BTH6","7号空调 加热器报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["19","9.1.114.1","Canatal13_7_BTH7","7号空调 隔尘网淤塞报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["20","9.1.114.1","Canatal13_7_BTH8","7号空调 火灾报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","9.1.114.1","Canatal13_7_BF1","7号空调 风机状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.1","Canatal13_7_BF2","7号空调 压缩机状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.1","Canatal13_7_BF3","7号空调 压缩机正启动","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.1","Canatal13_7_BF4","7号空调 能效控制","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.1","Canatal13_7_BF5","7号空调 加湿器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","9.1.114.1","Canatal13_7_BF6","7号空调 加热器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","9.1.114.1","Canatal13_7_BF7","7号空调 除湿器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","9.1.114.1","Canatal13_7_BF8","7号空调 矽控加热器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","9.1.114.1","Canatal13_7_UnitSatus","7号空调 机组状态","4","2","1","3","24961",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","9.1.114.1","Canatal13_7_On","7号空调 开机控制","4","2","1","6","24960",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","1","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","9.1.114.1","Canatal13_7_Off","7号空调 关机控制","4","2","1","6","24960",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","1","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","9.1.114.1","Canatal13_7_Communications","7号空调 通信状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114","关","开","0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","通信中断,"]
[]
["1","9.1.114.1","Canatal13_8_Temperature","8号空调 温度","4","2","1","3","248321",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","Canatal13_8_Humidity","8号空调 湿度","4","2","1","3","248322",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","Canatal13_8_BO1","8号空调 积水报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["4","9.1.114.1","Canatal13_8_BO2","8号空调 湿度1高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["5","9.1.114.1","Canatal13_8_BO3","8号空调 湿度2高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["6","9.1.114.1","Canatal13_8_BO4","8号空调 温度1高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["7","9.1.114.1","Canatal13_8_BO5","8号空调 温度2高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["8","9.1.114.1","Canatal13_8_BO6","8号空调 电压高限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["9","9.1.114.1","Canatal13_8_BO7","8号空调 湿度1低限报警","3","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["10","9.1.114.1","Canatal13_8_BO8","8号空调 湿度2低限报警","4","2","1","3","9318",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["11","9.1.114.1","Canatal13_8_BT1","8号空调 温度1低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["12","9.1.114.1","Canatal13_8_BT2","8号空调 温度2低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["13","9.1.114.1","Canatal13_8_BTH1","8号空调 电压低限报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["14","9.1.114.1","Canatal13_8_BTH2","8号空调 风机报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["15","9.1.114.1","Canatal13_8_BTH3","8号空调 压缩机高压报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["16","9.1.114.1","Canatal13_8_BTH4","8号空调 压缩机低压报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["17","9.1.114.1","Canatal13_8_BTH5","8号空调 加湿器报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["18","9.1.114.1","Canatal13_8_BTH6","8号空调 加热器报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["19","9.1.114.1","Canatal13_8_BTH7","8号空调 隔尘网淤塞报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["20","9.1.114.1","Canatal13_8_BTH8","8号空调 火灾报警","4","2","1","3","9319",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","9.1.114.1","Canatal13_8_BF1","8号空调 风机状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","110","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.1","Canatal13_8_BF2","8号空调 压缩机状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","111","114",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.1","Canatal13_8_BF3","8号空调 压缩机正启动","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","112","114",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.1","Canatal13_8_BF4","8号空调 能效控制","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","113","114",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.1","Canatal13_8_BF5","8号空调 加湿器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","114","114",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","9.1.114.1","Canatal13_8_BF6","8号空调 加热器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","115","114",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","9.1.114.1","Canatal13_8_BF7","8号空调 除湿器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","116","114",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","9.1.114.1","Canatal13_8_BF8","8号空调 矽控加热器状态","4","2","1","3","9320",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","117","114",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","9.1.114.1","Canatal13_8_UnitSatus","8号空调 机组状态","4","2","1","3","24961",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","9.1.114.1","Canatal13_8_On","8号空调 开机控制","4","2","1","6","24960",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","1","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","9.1.114.1","Canatal13_8_Off","8号空调 关机控制","4","2","1","6","24960",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","1","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","9.1.114.1","Canatal13_8_Communications","8号空调 通信状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114","关","开","0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","通信中断,"]