{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":23,"n_cols":76,"rows_kept":23,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","6.18.111.1","K200_Switchmachine","一层机房空调开关机","1","2","1","4","4001",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","111",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","6.18.111.1","K200_SetTemp","一层机房空调设定温度","1","2","1","4","4002",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","111",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.18.111.1","K200_SetHumidity","一层机房空调设定湿度","1","2","1","4","4003",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1000000015","3","0","1","1","0","0","0","0","111",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.18.111.1","K200_AirTemperature","一层机房空调回风温度","1","2","1","3","4005",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","111",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.18.111.1","K200_Airhumidity","一层机房空调回风湿度","1","2","1","3","4006",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1000000015","3","0","1","1","0","0","0","0","111",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.18.111.1","K200_DesiccantState","一层机房空调除湿状态","1","2","1","3","4004",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","17","111","开","关","0","10","10",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.18.111.1","K200_AddWetState","一层机房空调加湿状态","1","2","1","3","4004",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","111","开","关","0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.18.111.1","K200_Refrigeration","一层机房空调制冷状态","1","2","1","3","4004",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","19","111","开","关","0","12","12",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.18.111.1","K200_HeatingCondition","一层机房空调制热状态","1","2","1","3","4004",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","20","111","开","关","0","13","13",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.18.111.1","K200_FanState","一层机房空调风机状态","1","2","1","3","4004",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","21","111","开","关","0","14","14",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","6.18.111.1","K200_SwitchState","一层机房空调开关状态","1","2","1","3","4004",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","22","111","开","关","0","15","15",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","6.18.111.1","K200_High1Pressure","一层机房空调压缩机1高压","1","2","1","3","4007",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","7","111",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["13","6.18.111.1","K200_Compressor1Voltage","一层机房空调压缩机1低压","1","2","1","3","4007",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","8","111",null,null,"0","1","1",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["14","6.18.111.1","K200_LossAir","一层机房空调气流丢失","1","2","1","3","4007",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","9","111",null,null,"0","2","2",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["15","6.18.111.1","K200_FanOverload","一层机房空调风机过载","1","2","1","3","4007",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","10","111",null,null,"0","3","3",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["16","6.18.111.1","K200_AirExtractor","一层机房空调空气过滤网","1","2","1","3","4007",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","12","111",null,null,"0","5","5",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["17","6.18.111.1","K200_HighTemperatureAlarm","一层机房空调高温告警","1","2","1","3","4007",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","13","111",null,null,"0","6","6",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["18","6.18.111.1","K200_LowTemperatureAlarm","一层机房空调低温告警","1","2","1","3","4007",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","14","111",null,null,"0","7","7",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["19","6.18.111.1","K200_HumidityAlarm","一层机房空调高湿告警","1","2","1","3","4007",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","15","111",null,null,"0","8","8",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["20","6.18.111.1","K200_warpAlarm","一层机房空调低湿告警","1","2","1","3","4007",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","16","111",null,null,"0","9","9",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","6.18.111.1","K200_High2Pressure","一层机房空调压缩机2高压","1","2","1","3","4008",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","20","111",null,null,"0","13","13",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["22","6.18.111.1","K200_Compressor2Voltage","一层机房空调压缩机2低压","1","2","1","3","4008",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","21","111",null,null,"0","14","14",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]