{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":39,"n_cols":76,"rows_kept":39,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","6.7.88.1","stulz1ReturnTemp","1号空调回温温度","3","2","0","1","2","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.100000","3","0","1","0","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","6.7.88.1","stulz1ReturnHumidity","1号空调回温湿度","1","2","0","1","6","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","0.100000","3","0","1","0","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.7.88.1","stulz1Reheat1","1号空调模块1加热器1","1","1","0","1","22","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","32","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.7.88.1","stulz1Compressor","1号空调模块1压缩机","1","1","0","1","22","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","33","88",null,null,"0","1","1",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.7.88.1","stulz1Humidification","1号空调模块1加湿器","1","1","0","1","22","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","34","88",null,null,"0","2","2",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.7.88.1","stulz1DeHumidification","1号空调模块1除湿器","1","1","0","1","22","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","35","88",null,null,"0","3","3",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.7.88.1","stulz1Fan","1号空调模块1风机","1","1","0","1","22","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","36","88",null,null,"0","4","4",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.7.88.1","stulz1DryCooler","1号空调模块1干冷机","1","1","0","1","22","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","37","88",null,null,"0","5","5",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.7.88.1","stulz1Reheat3","1号空调模块1热风加热器/加热器3","1","1","0","1","22","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","39","88",null,null,"0","7","7",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.7.88.1","stulz1Reheat2","1号空调模块1加热器2","1","1","0","1","22","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","32","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","6.7.88.1","stulz1PCMonite","1号空调电脑监控","1","1","0","1","223","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","32","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","6.7.88.1","stulz1ReturnAirTempTooHigh","1号空调室内温度太高","1","1","0","1","225","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","32","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["13","6.7.88.1","stulz1ReturnAirHumidityTooHigh","1号空调室内湿度太高","1","1","0","1","225","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","33","88",null,null,"0","1","1",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["14","6.7.88.1","stulz1ReturnAirTempTooLow","1号空调室内温度太低","1","1","0","1","225","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","37","88",null,null,"0","5","5",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["15","6.7.88.1","stulz1ReturnAirHumidityTooLow","1号空调室内湿度太低","1","1","0","1","225","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","38","88",null,null,"0","6","6",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["1","6.7.88.2","stulz3ReturnTemp","3号空调回温温度","3","2","0","1","2","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.100000","3","0","1","0","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","6.7.88.2","stulz3ReturnHumidity","3号空调回温湿度","1","2","0","1","6","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","0.100000","3","0","1","0","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.7.88.2","stulz3Mod1Reheat3","3号空调模块1加热器1","1","1","0","1","22","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","40","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.7.88.2","stulz3Mod1Compressor","3号空调模块1压缩机","1","1","0","1","22","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","41","88",null,null,"0","1","1",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.7.88.2","stulz3Mod1Humidification","3号空调模块1加湿器","1","1","0","1","22","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","42","88",null,null,"0","2","2",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.7.88.2","stulz3Mod1DeHumidification","3号空调模块1除湿器","1","1","0","1","22","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","43","88",null,null,"0","3","3",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.7.88.2","stulz3Mod1Fan","3号空调模块1风机","1","1","0","1","22","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","44","88",null,null,"0","4","4",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.7.88.2","stulz3Mod1DryCooler","3号空调模块1干冷机","1","1","0","1","22","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","45","88",null,null,"0","5","5",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.7.88.2","stulz3Mod1Reheat3","3号空调模块1热风加热器/加热器3","1","1","0","1","22","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","47","88",null,null,"0","7","7",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.7.88.2","stulz3Mod1Reheat2","3号空调模块1加热器2","1","1","0","1","22","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","40","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","6.7.88.2","stulz3Mod2Reheat1","3号空调模块2加热器1","1","1","0","1","24","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","40","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","6.7.88.2","stulz3Mod2Compressor","3号空调模块2压缩机","1","1","0","1","24","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","41","88",null,null,"0","1","1",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","6.7.88.2","stulz3Mod2Humidification","3号空调模块2加湿器","1","1","0","1","24","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","42","88",null,null,"0","2","2",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","6.7.88.2","stulz3Mod2DeHumidification","3号空调模块2除湿器","1","1","0","1","24","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","43","88",null,null,"0","3","3",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","6.7.88.2","stulz3Mod2Fan","3号空调模块2风机","1","1","0","1","24","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","44","88",null,null,"0","4","4",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","6.7.88.2","stulz3Mod2DryCooler","3号空调模块2干冷机","1","1","0","1","24","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","45","88",null,null,"0","5","5",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","6.7.88.2","stulz3Mod2Reheat3","3号空调模块2热风加热器/加热器3","1","1","0","1","24","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","47","88",null,null,"0","7","7",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","6.7.88.2","stulz3Mod2Reheat2","3号空调模块2加热器2","1","1","0","1","24","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","40","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","6.7.88.2","stulz3PCMonite","3号空调电脑监控","1","1","0","1","223","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","40","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","6.7.88.2","stulz3ReturnAirTempTooHigh","3号空调室内温度太高","1","1","0","1","225","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","40","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","6.7.88.2","stulz3ReturnAirHumidityTooHigh","3号空调室内湿度太高","1","1","0","1","225","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","41","88",null,null,"0","1","1",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["22","6.7.88.2","stulz3ReturnAirTempTooLow","3号空调室内温度太低","1","1","0","1","225","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","45","88",null,null,"0","5","5",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["23","6.7.88.2","stulz3ReturnAirHumidityTooLow","3号空调室内湿度太低","1","1","0","1","225","cmd-2","type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","0","0","0","0","46","88",null,null,"0","6","6",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]