{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":31,"n_cols":76,"rows_kept":31,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["17","6.7.88.1","stulz1ReturnTemp","1号空调室内温度","101","4","2","4","2340",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","6.7.88.1","stulz1ReturnHumidity","1号空调室内湿度","101","4","2","4","2342",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","6.7.88.1","stulz1Cooling","1号空调压缩机","1","1","1","1","1754",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","6.7.88.1","stulz1Heating","1号空调加热器","1","1","1","1","1755",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","6.7.88.1","stulz1Humidification","1号空调加湿器","1","1","1","1","1756",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","6.7.88.1","stulz1DeHumidification","1号空调除湿器","1","1","1","1","1757",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","6.7.88.1","stulz1ReturnTempTooHigh","1号空调室内温度太高","1","1","1","1","2216",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["24","6.7.88.1","stulz1ReturnHumidityTooHigh","1号空调室内湿度太高","1","1","1","1","2217",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["25","6.7.88.1","stulz1ReturnTempTooLow","1号空调室内温度太低","1","1","1","1","2221",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["26","6.7.88.1","stulz1ReturnHumidityTooLow","1号空调室内湿度太低","1","1","1","1","2222",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["27","6.7.88.2","stulz2ReturnTemp","2号空调室内温度","101","4","2","4","2340",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","6.7.88.2","stulz2ReturnHumidity","2号空调室内湿度","101","4","2","4","2342",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","6.7.88.2","stulz2Cooling","2号空调压缩机","1","1","1","1","1754",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","6.7.88.2","stulz2Heating","2号空调加热器","1","1","1","1","1755",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","6.7.88.2","stulz2Humidification","2号空调加湿器","1","1","1","1","1756",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","6.7.88.2","stulz2DeHumidification","2号空调除湿器","1","1","1","1","1757",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","6.7.88.2","stulz2ReturnTempTooHigh","2号空调室内温度太高","1","1","1","1","2216",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["34","6.7.88.2","stulz2ReturnHumidityTooHigh","2号空调室内湿度太高","1","1","1","1","2217",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["35","6.7.88.2","stulz2ReturnTempTooLow","2号空调室内温度太低","1","1","1","1","2221",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["36","6.7.88.2","stulz2ReturnHumidityTooLow","2号空调室内湿度太低","1","1","1","1","2222",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["37","6.7.88.3","stulz3ReturnTemp","3号空调室内温度","101","4","2","4","2340",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["38","6.7.88.3","stulz3ReturnHumidity","3号空调室内湿度","101","4","2","4","2342",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["39","6.7.88.3","stulz3Cooling","3号空调压缩机","1","1","1","1","1754",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["40","6.7.88.3","stulz3Heating","3号空调加热器","1","1","1","1","1755",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["41","6.7.88.3","stulz3Humidification","3号空调加湿器","1","1","1","1","1756",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["42","6.7.88.3","stulz3DeHumidification","3号空调除湿器","1","1","1","1","1757",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["43","6.7.88.3","stulz3ReturnTempTooHigh","3号空调室内温度太高","1","1","1","1","2216",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["44","6.7.88.3","stulz3ReturnHumidityTooHigh","3号空调室内湿度太高","1","1","1","1","2217",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["45","6.7.88.3","stulz3ReturnTempTooLow","3号空调室内温度太低","1","1","1","1","2221",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["46","6.7.88.3","stulz3ReturnHumidityTooLow","3号空调室内湿度太低","1","1","1","1","2222",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","88",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]