{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["变量dat文件","CSpreadSheetBackup"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":65,"n_cols":76,"rows_kept":65,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["28","6.20.180.1","powernet_air1_max_rack_temp","空调内机1最大机架温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.1.6.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["29","6.20.180.1","powernet_air1_min_rack_temp","空调内机1最小机架温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.1.8.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["30","6.20.180.1","powernet_air1_cooling_setpoint","空调内机1制冷设定点","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.2.2.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["31","6.20.180.1","powernet_air1_supply_air_setpoint","空调内机1送风温度设定点","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.2.4.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["32","6.20.180.1","powernet_air1_fan_speed_setting","空调内机1风扇转速","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.2.5.0","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","6.20.180.1","powernet_air1_cooling_operating_mode","空调内机1制冷运行模式","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","6.20.180.1","powernet_air1_rack_temp","空调内机1机架温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.7.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["35","6.20.180.1","powernet_air1_supply_air_temp","空调内机1送风温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.9.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["36","6.20.180.1","powernet_air1_return_air_temp","空调内机1回风温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.11.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["37","6.20.180.1","powernet_air1_entering_fluid_temp","空调内机1进水温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.24.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["38","6.20.180.1","powernet_air1_Leaving_fluid_temp","空调内机1出水温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.26.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["39","6.20.180.1","powernet_air1_rack_temp_threshold","空调内机1机架温度阀值","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.2.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["40","6.20.180.1","powernet_air1_supply_air_temp_threshold","空调内机1送风温度阀值","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.4.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["41","6.20.180.1","powernet_air1_return_air_temp_threshold","空调内机1回风温度阀值","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.6.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["42","6.20.180.1","powernet_air1_entering_fluid_temp_threshold","空调内机1进水温度阀值","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.8.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["399","6.20.180.1","powernet_air1","空调1通信","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["43","6.20.180.2","powernet_air2_max_rack_temp","空调内机2最大机架温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.1.6.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["44","6.20.180.2","powernet_air2_min_rack_temp","空调内机2最小机架温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.1.8.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["45","6.20.180.2","powernet_air2_cooling_setpoint","空调内机2制冷设定点","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.2.2.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["46","6.20.180.2","powernet_air2_supply_air_setpoint","空调内机2送风温度设定点","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.2.4.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["47","6.20.180.2","powernet_air2_fan_speed_setting","空调内机2风扇转速","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.2.5.0","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["48","6.20.180.2","powernet_air2_cooling_operating_mode","空调内机2制冷运行模式","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["49","6.20.180.2","powernet_air2_rack_temp","空调内机2机架温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.7.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["50","6.20.180.2","powernet_air2_supply_air_temp","空调内机2送风温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.9.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["51","6.20.180.2","powernet_air2_return_air_temp","空调内机2回风温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.11.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["52","6.20.180.2","powernet_air2_entering_fluid_temp","空调内机2进水温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.24.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["53","6.20.180.2","powernet_air2_Leaving_fluid_temp","空调内机2出水温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.26.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["54","6.20.180.2","powernet_air2_rack_temp_threshold","空调内机2机架温度阀值","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.2.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["55","6.20.180.2","powernet_air2_supply_air_temp_threshold","空调内机2送风温度阀值","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.4.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["56","6.20.180.2","powernet_air2_return_air_ temp_threshold","空调内机2回风温度阀值","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.6.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["57","6.20.180.2","powernet_air2_entering_fluid_temp_threshold","空调内机2进水温度阀值","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.8.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["400","6.20.180.2","powernet_air2","空调2通信","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["58","6.20.180.3","powernet_air3_max_rack_temp","空调内机3最大机架温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.1.6.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["59","6.20.180.3","powernet_air3_min_rack_temp","空调内机3最小机架温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.1.8.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["60","6.20.180.3","powernet_air3_cooling_setpoint","空调内机3制冷设定点","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.2.2.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["61","6.20.180.3","powernet_air3_supply_air_setpoint","空调内机3送风温度设定点","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.2.4.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["62","6.20.180.3","powernet_air3_fan_speed_setting","空调内机3风扇转速","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.2.5.0","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["63","6.20.180.3","powernet_air3_cooling_operating_mode","空调内机3制冷运行模式","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["64","6.20.180.3","powernet_air3_rack_temp","空调内机3机架温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.7.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["65","6.20.180.3","powernet_air3_supply_air_temp","空调内机3送风温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.9.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["66","6.20.180.3","powernet_air3_return_air_temp","空调内机3回风温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.11.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["67","6.20.180.3","powernet_air3_entering_fluid_temp","空调内机3进水温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.24.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["68","6.20.180.3","powernet_air3_Leaving_fluid_temp","空调内机3出水温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.26.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["69","6.20.180.3","powernet_air3_rack_temp_threshold","空调内机3机架温度阀值","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.2.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["70","6.20.180.3","powernet_air3_supply_air_temp_threshold","空调内机3送风温度阀值","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.4.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["71","6.20.180.3","powernet_air3_return_air_temp_threshold","空调内机3回风温度阀值","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.6.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["72","6.20.180.3","powernet_air3_entering_fluid_temp_threshold","空调内机3进水温度阀值","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.8.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["401","6.20.180.3","powernet_air3","空调3通信","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["73","6.20.180.4","powernet_air4_max_rack_temp","空调内机4最大机架温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.1.6.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["74","6.20.180.4","powernet_air4_min_rack_temp","空调内机4最小机架温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.1.8.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["75","6.20.180.4","powernet_air4_cooling_setpoint","空调内机4制冷设定点","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.2.2.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["76","6.20.180.4","powernet_air4_supply_air_setpoint","空调内机4送风温度设定点","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.2.4.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["77","6.20.180.4","powernet_air4_fan_speed_setting","空调内机4风扇转速","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.1.2.5.0","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["78","6.20.180.4","powernet_air4_cooling_operating_mode","空调内机4制冷运行模式","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["79","6.20.180.4","powernet_air4_rack_temp","空调内机4机架温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.7.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["80","6.20.180.4","powernet_air4_supply_air_temp","空调内机4送风温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.9.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["81","6.20.180.4","powernet_air4_return_air_temp","空调内机4回风温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.11.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["82","6.20.180.4","powernet_air4_entering_fluid_temp","空调内机4进水温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.24.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["83","6.20.180.4","powernet_air4_Leaving_fluid_temp","空调内机4出水温度","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.2.26.0","public","0","0","0","0","0","0","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["84","6.20.180.4","powernet_air4_rack_temp_threshold","空调内机4机架温度阀值","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.2.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["85","6.20.180.4","powernet_air4_supply_air_temp_threshold","空调内机4送风温度阀值","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.4.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["86","6.20.180.4","powernet_air4_return_air_temp_threshold","空调内机4回风温度阀值","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.6.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["87","6.20.180.4","powernet_air4_entering_fluid_temp_threshold","空调内机4进水温度阀值","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.318.1.1.13.3.2.2.5.8.0","public","0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["402","6.20.180.4","powernet_air4","空调4通信","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]

{"sheet":"CSpreadSheetBackup","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}