{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["变量dat文件","CSpreadSheetBackup"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":25,"n_cols":76,"rows_kept":25,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","6.54.179.1","Chilled_water_outlet_temp","空调外机主机冷冻水出水温度","3","2","1","4","257",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["2","6.54.179.1","Chilled_water_inlet_temp","空调外机主机冷冻水进水温度","3","2","1","4","258",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["3","6.54.179.1","Host_operating_mode","空调外机主机实际运行模式","4","2","1","4","260",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.54.179.1","Host_compressor1_status","空调外机主机压缩机1状态","4","2","1","4","261",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.54.179.1","Host_compressor2_status","空调外机主机压缩机2状态","4","2","1","4","261",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.000000015","3","0","1","1","0","0","0","0","179",null,null,"0","1","1",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.54.179.1","Host_compressor3_status","空调外机主机压缩机3状态","4","2","1","4","261",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.000000015","3","0","1","1","0","0","0","0","179",null,null,"0","2","2",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.54.179.1","Host_compressor4_status","空调外机主机压缩机4状态","4","2","1","4","261",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.000000015","3","0","1","1","0","0","0","0","179",null,null,"0","3","3",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.54.179.1","Host_system2_exhaust_temp","空调外机主机系统2排气温度","4","2","1","4","262",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["6","6.54.179.1","Host_system1_tray_temp","空调外机主机系统1中盘温度","3","2","1","4","263",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["7","6.54.179.1","Host_system2_plate_temp","空调外机主机系统2中盘温度","3","2","1","4","264",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["8","6.54.179.1","Host_engine_cooling_water_temp","空调外机主机冷却水进水温度","3","2","1","4","265",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["9","6.54.179.1","Host_engine_cooling_water_temp","空调外机主机冷却水出水温度","3","2","1","4","266",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["10","6.54.179.1","Host_ambient_temp","空调外机主机环境温度","3","2","1","4","267",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["11","6.54.179.1","Host_system_1_outlet_temp_heat_exchanger","空调外机主机系统1热交器出口温度","3","2","1","4","268",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["12","6.54.179.1","Host_system_2_heat_exchanger_outlet_temp","空调外机主机系统2热交器出口温度","3","2","1","4","269",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["13","6.54.179.1","Host_back_system2_temp","空调外机主机系统2回气温度","3","2","1","4","270",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["14","6.54.179.1","Host_system_1_low","空调外机主机系统1低压","4","2","1","4","271",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Bar","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["15","6.54.179.1","Host_system_2_Low","空调外机主机系统2低压","4","2","1","4","272",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Bar","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["16","6.54.179.1","Host_system_1_exhaust_temp","空调外机主机系统1排气温度","4","2","1","4","273",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["17","6.54.179.1","Host_Back_system1_temp","空调外机主机系统1回气温度","3","2","1","4","274",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["18","6.54.179.1","Chilled_water_temp","空调外机主机冷冻水总管出水温度","3","2","1","4","275",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["19","6.54.179.1","Cooling_water_temp","空调外机主机冷却水总管出水温度","3","2","1","4","276",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["20","6.54.179.1","Host_water_temp","空调外机主机水箱温度","3","2","1","4","277",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["21","6.54.179.1","AIR_MC_1","空调外机通信","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]

{"sheet":"CSpreadSheetBackup","index":1,"n_rows":25,"n_cols":76,"rows_kept":25,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","6.54.179.1","Chilled_water_outlet_temp","空调外机主机冷冻水出水温度","4","2","1","3","258",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["2","6.54.179.1","Chilled_water_inlet_temp","空调外机主机冷冻水进水温度","4","2","1","3","259",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["3","6.54.179.1","Host_operating_mode","空调外机主机实际运行模式","4","2","1","3","261",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.54.179.1","Host_compressor1_status","空调外机主机压缩机1状态","4","2","1","3","262",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.54.179.1","Host_compressor2_status","空调外机主机压缩机2状态","4","2","1","3","262",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.000000015","3","0","1","1","0","0","0","0","179",null,null,"0","1","1",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.54.179.1","Host_compressor3_status","空调外机主机压缩机3状态","4","2","1","3","262",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.000000015","3","0","1","1","0","0","0","0","179",null,null,"0","2","2",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.54.179.1","Host_compressor4_status","空调外机主机压缩机4状态","4","2","1","3","262",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.000000015","3","0","1","1","0","0","0","0","179",null,null,"0","3","3",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.54.179.1","Host_system2_exhaust_temp","空调外机主机系统2排气温度","4","2","1","3","263",null,null,"0","30","60","1",null,null,"5","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["6","6.54.179.1","Host_system1_tray_temp","空调外机主机系统1中盘温度","4","2","1","3","264",null,null,"0","30","60","1",null,null,"5","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["7","6.54.179.1","Host_system2_plate_temp","空调外机主机系统2中盘温度","4","2","1","3","265",null,null,"0","30","60","1",null,null,"5","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["8","6.54.179.1","Host_engine_cooling_water_temp","空调外机主机冷却水进水温度","4","2","1","3","266",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["9","6.54.179.1","Host_engine_cooling_water_temp","空调外机主机冷却水出水温度","4","2","1","3","267",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["10","6.54.179.1","Host_ambient_temp","空调外机主机环境温度","4","2","1","3","268",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["11","6.54.179.1","Host_system_1_outlet_temp_heat_exchanger","空调外机主机系统1热交器出口温度","4","2","1","3","269",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["12","6.54.179.1","Host_system_2_heat_exchanger_outlet_temp","空调外机主机系统2热交器出口温度","4","2","1","3","270",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["13","6.54.179.1","Host_back_system2_temp","空调外机主机系统2回气温度","4","2","1","3","271",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["14","6.54.179.1","Host_system_1_low","空调外机主机系统1低压","4","2","1","3","272",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Bar","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["15","6.54.179.1","Host_system_2_Low","空调外机主机系统2低压","4","2","1","3","273",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Bar","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["16","6.54.179.1","Host_system_1_exhaust_temp","空调外机主机系统1排气温度","4","2","1","3","274",null,null,"0","30","60","1",null,null,"5","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["17","6.54.179.1","Host_Back_system1_temp","空调外机主机系统1回气温度","4","2","1","3","275",null,null,"0","30","60","1",null,null,"5","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["18","6.54.179.1","Chilled_water_temp","空调外机主机冷冻水总管出水温度","4","2","1","3","276",null,null,"0","30","60","1",null,null,"5","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["19","6.54.179.1","Cooling_water_temp","空调外机主机冷却水总管出水温度","4","2","1","3","277",null,null,"0","30","60","1",null,null,"5","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["20","6.54.179.1","Host_water_temp","空调外机主机水箱温度","4","2","1","3","278",null,null,"0","30","60","1",null,null,"5","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0"]
["21","6.54.179.1","AIR_MC_1","空调外机通信","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","179",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]