{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":381,"n_cols":76,"rows_kept":381,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["169","6.16.107.1","Num1OC485_ReturnAirTemp","1号空调回风温度","4","2","1","4","109",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["170","6.16.107.1","Num1OC485_ReturnAirHumidity","1号空调回风湿度","4","2","1","4","129",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["171","6.16.107.1","Num1OC485_ActualReturnTempSetPoint","1号空调实际回风温度设定点","4","2","1","4","110",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["172","6.16.107.1","Num1OC485_ActualReturnHumSetPoint","1号空调实际回风湿度设定点","4","2","1","4","130",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["173","6.16.107.1","Num1OC485_HighTempAlarmPoints","1号空调高温报警点","4","2","1","4","49",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["174","6.16.107.1","Num1OC485_LowTempAlarmPoints","1号空调低温报警点","4","2","1","4","50",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["175","6.16.107.1","Num1OC485_HightHumAlarmPoints","1号空调高湿报警点","4","2","1","4","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["176","6.16.107.1","Num1OC485_LowHumAlarmPoints","1号空调低湿报警点","4","2","1","4","54",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["177","6.16.107.1","Num1OC485_Fan","1号空调风机状态","2","1","1","2","24",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["178","6.16.107.1","Num1OC485_Refrigeration","1号空调制冷状态","2","1","1","2","25",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["179","6.16.107.1","Num1OC485_NaturalSourceCold","1号空调自然冷源状态","2","1","1","2","26",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["180","6.16.107.1","Num1OC485_StateWaterHeater","1号空调热水器状态","2","1","1","2","27",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["181","6.16.107.1","Num1OC485_ElectricHeater","1号空调电加热器状态","2","1","1","2","28",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["182","6.16.107.1","Num1OC485_Humidifier","1号空调加湿器状态","2","1","1","2","29",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["183","6.16.107.1","Num1OC485_Dehumidifier","1号空调除湿器状态","2","1","1","2","30",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["184","6.16.107.1","Num1OC485_FanOverload","1号空调风机过载","2","1","1","2","33",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["185","6.16.107.1","Num1OC485_AirLoss","1号空调气流丢失","2","1","1","2","34",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["186","6.16.107.1","Num1OC485_WaterLoss","1号空调水流丢失","2","1","1","2","35",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["187","6.16.107.1","Num1OC485_HighPressureCompressor1","1号空调压缩机1高压","2","1","1","2","36",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["188","6.16.107.1","Num1OC485_LowPressureCompressor1","1号空调压缩机1低压","2","1","1","2","37",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["189","6.16.107.1","Num1OC485_Compressor1Overload","1号空调压缩机1过载","2","1","1","2","38",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["190","6.16.107.1","Num1OC485_HightPressureCompressor2","1号空调压缩机2高压","2","1","1","2","40",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["191","6.16.107.1","Num1OC485_LowPressureCompressor2","1号空调压缩机2低压","2","1","1","2","41",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["192","6.16.107.1","Num1OC485_Compressor2Overload","1号空调压缩机2过载","2","1","1","2","42",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["193","6.16.107.1","Num1OC485_Compressor1PumpDownFail","1号空调压缩机1泵下降失败","2","1","1","2","39",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["194","6.16.107.1","Num1OC485_Compressor2PumpDownFail","1号空调压缩机2泵下降失败","2","1","1","2","43",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["195","6.16.107.1","Num1OC485_HumidifierFailure","1号空调加湿器故障","2","1","1","2","48",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["196","6.16.107.1","Num1OC485_CompressorPowerDown","1号空调压缩机掉电","2","1","1","2","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["197","6.16.107.1","Num1OC485_SysHighTemperature","1号空调系统高温","2","1","1","2","59",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["198","6.16.107.1","Num1OC485_SysPowerDown","1号空调系统掉电","2","1","1","2","60",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["199","6.16.107.1","Num1OC485_ChilledWaterTemp","1号空调冷冻水高温","2","1","1","2","64",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["200","6.16.107.1","Num1OC485_RoomHightTemp","1号空调室内高温","2","1","1","2","66",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["201","6.16.107.1","Num1OC485_RoomLowTemp","1号空调室内低温","2","1","1","2","67",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["202","6.16.107.1","Num1OC485_IndoorHightHumidity","1号空调室内高湿","2","1","1","2","68",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["203","6.16.107.1","Num1OC485_IndoorLowHumidity","1号空调室内低湿","2","1","1","2","69",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["204","6.16.107.1","Num1OC485_ChilledWaterFlowLoss","1号空调冷冻水水流丢失","2","1","1","2","74",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["205","6.16.107.1","Num1OC485_FilterBlock","1号空调过滤网堵塞","2","1","1","2","75",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["206","6.16.107.1","Num1OC485_1_status","1号空调通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["207","6.16.107.2","Num2OC485_ReturnAirTemp","2号空调回风温度","4","2","1","4","109",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["208","6.16.107.2","Num2OC485_ReturnAirHumidity","2号空调回风湿度","4","2","1","4","129",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["209","6.16.107.2","Num2OC485_ActualReturnTempSetPoint","2号空调实际回风温度设定点","4","2","1","4","110",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["210","6.16.107.2","Num2OC485_ActualReturnHumSetPoint","2号空调实际回风湿度设定点","4","2","1","4","130",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["211","6.16.107.2","Num2OC485_HighTempAlarmPoints","2号空调高温报警点","4","2","1","4","49",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["212","6.16.107.2","Num2OC485_LowTempAlarmPoints","2号空调低温报警点","4","2","1","4","50",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["213","6.16.107.2","Num2OC485_HightHumAlarmPoints","2号空调高湿报警点","4","2","1","4","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["214","6.16.107.2","Num2OC485_LowHumAlarmPoints","2号空调低湿报警点","4","2","1","4","54",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["215","6.16.107.2","Num2OC485_Fan","2号空调风机状态","2","1","1","2","24",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["216","6.16.107.2","Num2OC485_Refrigeration","2号空调制冷状态","2","1","1","2","25",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["217","6.16.107.2","Num2OC485_NaturalSourceCold","2号空调自然冷源状态","2","1","1","2","26",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["218","6.16.107.2","Num2OC485_StateWaterHeater","2号空调热水器状态","2","1","1","2","27",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["219","6.16.107.2","Num2OC485_ElectricHeater","2号空调电加热器状态","2","1","1","2","28",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["220","6.16.107.2","Num2OC485_Humidifier","2号空调加湿器状态","2","1","1","2","29",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["221","6.16.107.2","Num2OC485_Dehumidifier","2号空调除湿器状态","2","1","1","2","30",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["222","6.16.107.2","Num2OC485_FanOverload","2号空调风机过载","2","1","1","2","33",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["223","6.16.107.2","Num2OC485_AirLoss","2号空调气流丢失","2","1","1","2","34",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["224","6.16.107.2","Num2OC485_WaterLoss","2号空调水流丢失","2","1","1","2","35",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["225","6.16.107.2","Num2OC485_HighPressureCompressor1","2号空调压缩机1高压","2","1","1","2","36",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["226","6.16.107.2","Num2OC485_LowPressureCompressor1","2号空调压缩机1低压","2","1","1","2","37",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["227","6.16.107.2","Num2OC485_Compressor1Overload","2号空调压缩机1过载","2","1","1","2","38",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["228","6.16.107.2","Num2OC485_HightPressureCompressor2","2号空调压缩机2高压","2","1","1","2","40",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["229","6.16.107.2","Num2OC485_LowPressureCompressor2","2号空调压缩机2低压","2","1","1","2","41",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["230","6.16.107.2","Num2OC485_Compressor2Overload","2号空调压缩机2过载","2","1","1","2","42",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["231","6.16.107.2","Num2OC485_Compressor1PumpDownFail","2号空调压缩机1泵下降失败","2","1","1","2","39",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["232","6.16.107.2","Num2OC485_Compressor2PumpDownFail","2号空调压缩机2泵下降失败","2","1","1","2","43",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["233","6.16.107.2","Num2OC485_HumidifierFailure","2号空调加湿器故障","2","1","1","2","48",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["234","6.16.107.2","Num2OC485_CompressorPowerDown","2号空调压缩机掉电","2","1","1","2","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["235","6.16.107.2","Num2OC485_SysHighTemperature","2号空调系统高温","2","1","1","2","59",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["236","6.16.107.2","Num2OC485_SysPowerDown","2号空调系统掉电","2","1","1","2","60",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["237","6.16.107.2","Num2OC485_ChilledWaterTemp","2号空调冷冻水高温","2","1","1","2","64",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["238","6.16.107.2","Num2OC485_RoomHightTemp","2号空调室内高温","2","1","1","2","66",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["239","6.16.107.2","Num2OC485_RoomLowTemp","2号空调室内低温","2","1","1","2","67",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["240","6.16.107.2","Num2OC485_IndoorHightHumidity","2号空调室内高湿","2","1","1","2","68",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["241","6.16.107.2","Num2OC485_IndoorLowHumidity","2号空调室内低湿","2","1","1","2","69",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["242","6.16.107.2","Num2OC485_ChilledWaterFlowLoss","2号空调冷冻水水流丢失","2","1","1","2","74",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["243","6.16.107.2","Num2OC485_FilterBlock","2号空调过滤网堵塞","2","1","1","2","75",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["244","6.16.107.2","Num2OC485_2_status","2号空调通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["245","6.16.107.3","Num3OC485_ReturnAirTemp","3号空调回风温度","4","2","1","4","109",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["246","6.16.107.3","Num3OC485_ReturnAirHumidity","3号空调回风湿度","4","2","1","4","129",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["247","6.16.107.3","Num3OC485_ActualReturnTempSetPoint","3号空调实际回风温度设定点","4","2","1","4","110",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["248","6.16.107.3","Num3OC485_ActualReturnHumSetPoint","3号空调实际回风湿度设定点","4","2","1","4","130",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["249","6.16.107.3","Num3OC485_HighTempAlarmPoints","3号空调高温报警点","4","2","1","4","49",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["250","6.16.107.3","Num3OC485_LowTempAlarmPoints","3号空调低温报警点","4","2","1","4","50",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["251","6.16.107.3","Num3OC485_HightHumAlarmPoints","3号空调高湿报警点","4","2","1","4","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["252","6.16.107.3","Num3OC485_LowHumAlarmPoints","3号空调低湿报警点","4","2","1","4","54",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["253","6.16.107.3","Num3OC485_Fan","3号空调风机状态","2","1","1","2","24",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["254","6.16.107.3","Num3OC485_Refrigeration","3号空调制冷状态","2","1","1","2","25",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["255","6.16.107.3","Num3OC485_NaturalSourceCold","3号空调自然冷源状态","2","1","1","2","26",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["256","6.16.107.3","Num3OC485_StateWaterHeater","3号空调热水器状态","2","1","1","2","27",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["257","6.16.107.3","Num3OC485_ElectricHeater","3号空调电加热器状态","2","1","1","2","28",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["258","6.16.107.3","Num3OC485_Humidifier","3号空调加湿器状态","2","1","1","2","29",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["259","6.16.107.3","Num3OC485_Dehumidifier","3号空调除湿器状态","2","1","1","2","30",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["260","6.16.107.3","Num3OC485_FanOverload","3号空调风机过载","2","1","1","2","33",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["261","6.16.107.3","Num3OC485_AirLoss","3号空调气流丢失","2","1","1","2","34",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["262","6.16.107.3","Num3OC485_WaterLoss","3号空调水流丢失","2","1","1","2","35",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["263","6.16.107.3","Num3OC485_HighPressureCompressor1","3号空调压缩机1高压","2","1","1","2","36",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["264","6.16.107.3","Num3OC485_LowPressureCompressor1","3号空调压缩机1低压","2","1","1","2","37",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["265","6.16.107.3","Num3OC485_Compressor1Overload","3号空调压缩机1过载","2","1","1","2","38",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["266","6.16.107.3","Num3OC485_HightPressureCompressor2","3号空调压缩机2高压","2","1","1","2","40",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["267","6.16.107.3","Num3OC485_LowPressureCompressor2","3号空调压缩机2低压","2","1","1","2","41",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["268","6.16.107.3","Num3OC485_Compressor2Overload","3号空调压缩机2过载","2","1","1","2","42",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["269","6.16.107.3","Num3OC485_Compressor1PumpDownFail","3号空调压缩机1泵下降失败","2","1","1","2","39",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["270","6.16.107.3","Num3OC485_Compressor2PumpDownFail","3号空调压缩机2泵下降失败","2","1","1","2","43",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["271","6.16.107.3","Num3OC485_HumidifierFailure","3号空调加湿器故障","2","1","1","2","48",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["272","6.16.107.3","Num3OC485_CompressorPowerDown","3号空调压缩机掉电","2","1","1","2","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["273","6.16.107.3","Num3OC485_SysHighTemperature","3号空调系统高温","2","1","1","2","59",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["274","6.16.107.3","Num3OC485_SysPowerDown","3号空调系统掉电","2","1","1","2","60",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["275","6.16.107.3","Num3OC485_ChilledWaterTemp","3号空调冷冻水高温","2","1","1","2","64",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["276","6.16.107.3","Num3OC485_RoomHightTemp","3号空调室内高温","2","1","1","2","66",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["277","6.16.107.3","Num3OC485_RoomLowTemp","3号空调室内低温","2","1","1","2","67",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["278","6.16.107.3","Num3OC485_IndoorHightHumidity","3号空调室内高湿","2","1","1","2","68",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["279","6.16.107.3","Num3OC485_IndoorLowHumidity","3号空调室内低湿","2","1","1","2","69",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["280","6.16.107.3","Num3OC485_ChilledWaterFlowLoss","3号空调冷冻水水流丢失","2","1","1","2","74",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["281","6.16.107.3","Num3OC485_FilterBlock","3号空调过滤网堵塞","2","1","1","2","75",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["282","6.16.107.3","Num3OC485_1_status","3号空调通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["283","6.16.107.4","Num4OC485_ReturnAirTemp","4号空调回风温度","4","2","1","4","109",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["284","6.16.107.4","Num4OC485_ReturnAirHumidity","4号空调回风湿度","4","2","1","4","129",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["285","6.16.107.4","Num4OC485_ActualReturnTempSetPoint","4号空调实际回风温度设定点","4","2","1","4","110",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["286","6.16.107.4","Num4OC485_ActualReturnHumSetPoint","4号空调实际回风湿度设定点","4","2","1","4","130",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["287","6.16.107.4","Num4OC485_HighTempAlarmPoints","4号空调高温报警点","4","2","1","4","49",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["288","6.16.107.4","Num4OC485_LowTempAlarmPoints","4号空调低温报警点","4","2","1","4","50",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["289","6.16.107.4","Num4OC485_HightHumAlarmPoints","4号空调高湿报警点","4","2","1","4","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["290","6.16.107.4","Num4OC485_LowHumAlarmPoints","4号空调低湿报警点","4","2","1","4","54",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["291","6.16.107.4","Num4OC485_Fan","4号空调风机状态","2","1","1","2","24",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["292","6.16.107.4","Num4OC485_Refrigeration","4号空调制冷状态","2","1","1","2","25",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["293","6.16.107.4","Num4OC485_NaturalSourceCold","4号空调自然冷源状态","2","1","1","2","26",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["294","6.16.107.4","Num4OC485_StateWaterHeater","4号空调热水器状态","2","1","1","2","27",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["295","6.16.107.4","Num4OC485_ElectricHeater","4号空调电加热器状态","2","1","1","2","28",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["296","6.16.107.4","Num4OC485_Humidifier","4号空调加湿器状态","2","1","1","2","29",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["297","6.16.107.4","Num4OC485_Dehumidifier","4号空调除湿器状态","2","1","1","2","30",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["298","6.16.107.4","Num4OC485_FanOverload","4号空调风机过载","2","1","1","2","33",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["299","6.16.107.4","Num4OC485_AirLoss","4号空调气流丢失","2","1","1","2","34",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["300","6.16.107.4","Num4OC485_WaterLoss","4号空调水流丢失","2","1","1","2","35",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["301","6.16.107.4","Num4OC485_HighPressureCompressor1","4号空调压缩机1高压","2","1","1","2","36",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["302","6.16.107.4","Num4OC485_LowPressureCompressor1","4号空调压缩机1低压","2","1","1","2","37",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["303","6.16.107.4","Num4OC485_Compressor1Overload","4号空调压缩机1过载","2","1","1","2","38",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["304","6.16.107.4","Num4OC485_HightPressureCompressor2","4号空调压缩机2高压","2","1","1","2","40",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["305","6.16.107.4","Num4OC485_LowPressureCompressor2","4号空调压缩机2低压","2","1","1","2","41",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["306","6.16.107.4","Num4OC485_Compressor2Overload","4号空调压缩机2过载","2","1","1","2","42",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["307","6.16.107.4","Num4OC485_Compressor1PumpDownFail","4号空调压缩机1泵下降失败","2","1","1","2","39",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["308","6.16.107.4","Num4OC485_Compressor2PumpDownFail","4号空调压缩机2泵下降失败","2","1","1","2","43",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["309","6.16.107.4","Num4OC485_HumidifierFailure","4号空调加湿器故障","2","1","1","2","48",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["310","6.16.107.4","Num4OC485_CompressorPowerDown","4号空调压缩机掉电","2","1","1","2","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["311","6.16.107.4","Num4OC485_SysHighTemperature","4号空调系统高温","2","1","1","2","59",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["312","6.16.107.4","Num4OC485_SysPowerDown","4号空调系统掉电","2","1","1","2","60",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["313","6.16.107.4","Num4OC485_ChilledWaterTemp","4号空调冷冻水高温","2","1","1","2","64",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["314","6.16.107.4","Num4OC485_RoomHightTemp","4号空调室内高温","2","1","1","2","66",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["315","6.16.107.4","Num4OC485_RoomLowTemp","4号空调室内低温","2","1","1","2","67",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["316","6.16.107.4","Num4OC485_IndoorHightHumidity","4号空调室内高湿","2","1","1","2","68",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["317","6.16.107.4","Num4OC485_IndoorLowHumidity","4号空调室内低湿","2","1","1","2","69",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["318","6.16.107.4","Num4OC485_ChilledWaterFlowLoss","4号空调冷冻水水流丢失","2","1","1","2","74",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["319","6.16.107.4","Num4OC485_FilterBlock","4号空调过滤网堵塞","2","1","1","2","75",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["320","6.16.107.4","Num4OC485_2_status","4号空调通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["321","6.16.107.5","Num5OC485_ReturnAirTemp","5号空调回风温度","4","2","1","4","109",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["322","6.16.107.5","Num5OC485_ReturnAirHumidity","5号空调回风湿度","4","2","1","4","129",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["323","6.16.107.5","Num5OC485_ActualReturnTempSetPoint","5号空调实际回风温度设定点","4","2","1","4","110",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["324","6.16.107.5","Num5OC485_ActualReturnHumSetPoint","5号空调实际回风湿度设定点","4","2","1","4","130",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["325","6.16.107.5","Num5OC485_HighTempAlarmPoints","5号空调高温报警点","4","2","1","4","49",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["326","6.16.107.5","Num5OC485_LowTempAlarmPoints","5号空调低温报警点","4","2","1","4","50",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["327","6.16.107.5","Num5OC485_HightHumAlarmPoints","5号空调高湿报警点","4","2","1","4","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["328","6.16.107.5","Num5OC485_LowHumAlarmPoints","5号空调低湿报警点","4","2","1","4","54",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["329","6.16.107.5","Num5OC485_Fan","5号空调风机状态","2","1","1","2","24",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["330","6.16.107.5","Num5OC485_Refrigeration","5号空调制冷状态","2","1","1","2","25",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["331","6.16.107.5","Num5OC485_NaturalSourceCold","5号空调自然冷源状态","2","1","1","2","26",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["332","6.16.107.5","Num5OC485_StateWaterHeater","5号空调热水器状态","2","1","1","2","27",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["333","6.16.107.5","Num5OC485_ElectricHeater","5号空调电加热器状态","2","1","1","2","28",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["334","6.16.107.5","Num5OC485_Humidifier","5号空调加湿器状态","2","1","1","2","29",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["335","6.16.107.5","Num5OC485_Dehumidifier","5号空调除湿器状态","2","1","1","2","30",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["336","6.16.107.5","Num5OC485_FanOverload","5号空调风机过载","2","1","1","2","33",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["337","6.16.107.5","Num5OC485_AirLoss","5号空调气流丢失","2","1","1","2","34",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["338","6.16.107.5","Num5OC485_WaterLoss","5号空调水流丢失","2","1","1","2","35",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["339","6.16.107.5","Num5OC485_HighPressureCompressor1","5号空调压缩机1高压","2","1","1","2","36",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["340","6.16.107.5","Num5OC485_LowPressureCompressor1","5号空调压缩机1低压","2","1","1","2","37",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["341","6.16.107.5","Num5OC485_Compressor1Overload","5号空调压缩机1过载","2","1","1","2","38",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["342","6.16.107.5","Num5OC485_HightPressureCompressor2","5号空调压缩机2高压","2","1","1","2","40",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["343","6.16.107.5","Num5OC485_LowPressureCompressor2","5号空调压缩机2低压","2","1","1","2","41",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["344","6.16.107.5","Num5OC485_Compressor2Overload","5号空调压缩机2过载","2","1","1","2","42",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["345","6.16.107.5","Num5OC485_Compressor1PumpDownFail","5号空调压缩机1泵下降失败","2","1","1","2","39",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["346","6.16.107.5","Num5OC485_Compressor2PumpDownFail","5号空调压缩机2泵下降失败","2","1","1","2","43",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["347","6.16.107.5","Num5OC485_HumidifierFailure","5号空调加湿器故障","2","1","1","2","48",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["348","6.16.107.5","Num5OC485_CompressorPowerDown","5号空调压缩机掉电","2","1","1","2","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["349","6.16.107.5","Num5OC485_SysHighTemperature","5号空调系统高温","2","1","1","2","59",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["350","6.16.107.5","Num5OC485_SysPowerDown","5号空调系统掉电","2","1","1","2","60",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["351","6.16.107.5","Num5OC485_ChilledWaterTemp","5号空调冷冻水高温","2","1","1","2","64",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["352","6.16.107.5","Num5OC485_RoomHightTemp","5号空调室内高温","2","1","1","2","66",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["353","6.16.107.5","Num5OC485_RoomLowTemp","5号空调室内低温","2","1","1","2","67",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["354","6.16.107.5","Num5OC485_IndoorHightHumidity","5号空调室内高湿","2","1","1","2","68",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["355","6.16.107.5","Num5OC485_IndoorLowHumidity","5号空调室内低湿","2","1","1","2","69",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["356","6.16.107.5","Num5OC485_ChilledWaterFlowLoss","5号空调冷冻水水流丢失","2","1","1","2","74",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["357","6.16.107.5","Num5OC485_FilterBlock","5号空调过滤网堵塞","2","1","1","2","75",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["358","6.16.107.5","Num5OC485_1_status","5号空调通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["359","6.16.107.6","Num6OC485_ReturnAirTemp","6号空调回风温度","4","2","1","4","109",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["360","6.16.107.6","Num6OC485_ReturnAirHumidity","6号空调回风湿度","4","2","1","4","129",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["361","6.16.107.6","Num6OC485_ActualReturnTempSetPoint","6号空调实际回风温度设定点","4","2","1","4","110",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["362","6.16.107.6","Num6OC485_ActualReturnHumSetPoint","6号空调实际回风湿度设定点","4","2","1","4","130",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["363","6.16.107.6","Num6OC485_HighTempAlarmPoints","6号空调高温报警点","4","2","1","4","49",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["364","6.16.107.6","Num6OC485_LowTempAlarmPoints","6号空调低温报警点","4","2","1","4","50",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["365","6.16.107.6","Num6OC485_HightHumAlarmPoints","6号空调高湿报警点","4","2","1","4","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["366","6.16.107.6","Num6OC485_LowHumAlarmPoints","6号空调低湿报警点","4","2","1","4","54",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["367","6.16.107.6","Num6OC485_Fan","6号空调风机状态","2","1","1","2","24",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["368","6.16.107.6","Num6OC485_Refrigeration","6号空调制冷状态","2","1","1","2","25",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["369","6.16.107.6","Num6OC485_NaturalSourceCold","6号空调自然冷源状态","2","1","1","2","26",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["370","6.16.107.6","Num6OC485_StateWaterHeater","6号空调热水器状态","2","1","1","2","27",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["371","6.16.107.6","Num6OC485_ElectricHeater","6号空调电加热器状态","2","1","1","2","28",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["372","6.16.107.6","Num6OC485_Humidifier","6号空调加湿器状态","2","1","1","2","29",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["373","6.16.107.6","Num6OC485_Dehumidifier","6号空调除湿器状态","2","1","1","2","30",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["374","6.16.107.6","Num6OC485_FanOverload","6号空调风机过载","2","1","1","2","33",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["375","6.16.107.6","Num6OC485_AirLoss","6号空调气流丢失","2","1","1","2","34",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["376","6.16.107.6","Num6OC485_WaterLoss","6号空调水流丢失","2","1","1","2","35",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["377","6.16.107.6","Num6OC485_HighPressureCompressor1","6号空调压缩机1高压","2","1","1","2","36",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["378","6.16.107.6","Num6OC485_LowPressureCompressor1","6号空调压缩机1低压","2","1","1","2","37",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["379","6.16.107.6","Num6OC485_Compressor1Overload","6号空调压缩机1过载","2","1","1","2","38",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["380","6.16.107.6","Num6OC485_HightPressureCompressor2","6号空调压缩机2高压","2","1","1","2","40",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["381","6.16.107.6","Num6OC485_LowPressureCompressor2","6号空调压缩机2低压","2","1","1","2","41",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["382","6.16.107.6","Num6OC485_Compressor2Overload","6号空调压缩机2过载","2","1","1","2","42",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["383","6.16.107.6","Num6OC485_Compressor1PumpDownFail","6号空调压缩机1泵下降失败","2","1","1","2","39",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["384","6.16.107.6","Num6OC485_Compressor2PumpDownFail","6号空调压缩机2泵下降失败","2","1","1","2","43",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["385","6.16.107.6","Num6OC485_HumidifierFailure","6号空调加湿器故障","2","1","1","2","48",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["386","6.16.107.6","Num6OC485_CompressorPowerDown","6号空调压缩机掉电","2","1","1","2","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["387","6.16.107.6","Num6OC485_SysHighTemperature","6号空调系统高温","2","1","1","2","59",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["388","6.16.107.6","Num6OC485_SysPowerDown","6号空调系统掉电","2","1","1","2","60",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["389","6.16.107.6","Num6OC485_ChilledWaterTemp","6号空调冷冻水高温","2","1","1","2","64",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["390","6.16.107.6","Num6OC485_RoomHightTemp","6号空调室内高温","2","1","1","2","66",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["391","6.16.107.6","Num6OC485_RoomLowTemp","6号空调室内低温","2","1","1","2","67",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["392","6.16.107.6","Num6OC485_IndoorHightHumidity","6号空调室内高湿","2","1","1","2","68",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["393","6.16.107.6","Num6OC485_IndoorLowHumidity","6号空调室内低湿","2","1","1","2","69",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["394","6.16.107.6","Num6OC485_ChilledWaterFlowLoss","6号空调冷冻水水流丢失","2","1","1","2","74",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["395","6.16.107.6","Num6OC485_FilterBlock","6号空调过滤网堵塞","2","1","1","2","75",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["396","6.16.107.6","Num6OC485_2_status","6号空调通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["397","6.16.107.7","Num7OC485_ReturnAirTemp","7号空调回风温度","4","2","1","4","109",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["398","6.16.107.7","Num7OC485_ReturnAirHumidity","7号空调回风湿度","4","2","1","4","129",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["399","6.16.107.7","Num7OC485_ActualReturnTempSetPoint","7号空调实际回风温度设定点","4","2","1","4","110",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["400","6.16.107.7","Num7OC485_ActualReturnHumSetPoint","7号空调实际回风湿度设定点","4","2","1","4","130",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["401","6.16.107.7","Num7OC485_HighTempAlarmPoints","7号空调高温报警点","4","2","1","4","49",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["402","6.16.107.7","Num7OC485_LowTempAlarmPoints","7号空调低温报警点","4","2","1","4","50",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["403","6.16.107.7","Num7OC485_HightHumAlarmPoints","7号空调高湿报警点","4","2","1","4","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["404","6.16.107.7","Num7OC485_LowHumAlarmPoints","7号空调低湿报警点","4","2","1","4","54",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["405","6.16.107.7","Num7OC485_Fan","7号空调风机状态","2","1","1","2","24",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["406","6.16.107.7","Num7OC485_Refrigeration","7号空调制冷状态","2","1","1","2","25",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["407","6.16.107.7","Num7OC485_NaturalSourceCold","7号空调自然冷源状态","2","1","1","2","26",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["408","6.16.107.7","Num7OC485_StateWaterHeater","7号空调热水器状态","2","1","1","2","27",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["409","6.16.107.7","Num7OC485_ElectricHeater","7号空调电加热器状态","2","1","1","2","28",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["410","6.16.107.7","Num7OC485_Humidifier","7号空调加湿器状态","2","1","1","2","29",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["411","6.16.107.7","Num7OC485_Dehumidifier","7号空调除湿器状态","2","1","1","2","30",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["412","6.16.107.7","Num7OC485_FanOverload","7号空调风机过载","2","1","1","2","33",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["413","6.16.107.7","Num7OC485_AirLoss","7号空调气流丢失","2","1","1","2","34",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["414","6.16.107.7","Num7OC485_WaterLoss","7号空调水流丢失","2","1","1","2","35",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["415","6.16.107.7","Num7OC485_HighPressureCompressor1","7号空调压缩机1高压","2","1","1","2","36",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["416","6.16.107.7","Num7OC485_LowPressureCompressor1","7号空调压缩机1低压","2","1","1","2","37",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["417","6.16.107.7","Num7OC485_Compressor1Overload","7号空调压缩机1过载","2","1","1","2","38",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["418","6.16.107.7","Num7OC485_HightPressureCompressor2","7号空调压缩机2高压","2","1","1","2","40",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["419","6.16.107.7","Num7OC485_LowPressureCompressor2","7号空调压缩机2低压","2","1","1","2","41",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["420","6.16.107.7","Num7OC485_Compressor2Overload","7号空调压缩机2过载","2","1","1","2","42",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["421","6.16.107.7","Num7OC485_Compressor1PumpDownFail","7号空调压缩机1泵下降失败","2","1","1","2","39",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["422","6.16.107.7","Num7OC485_Compressor2PumpDownFail","7号空调压缩机2泵下降失败","2","1","1","2","43",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["423","6.16.107.7","Num7OC485_HumidifierFailure","7号空调加湿器故障","2","1","1","2","48",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["424","6.16.107.7","Num7OC485_CompressorPowerDown","7号空调压缩机掉电","2","1","1","2","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["425","6.16.107.7","Num7OC485_SysHighTemperature","7号空调系统高温","2","1","1","2","59",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["426","6.16.107.7","Num7OC485_SysPowerDown","7号空调系统掉电","2","1","1","2","60",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["427","6.16.107.7","Num7OC485_ChilledWaterTemp","7号空调冷冻水高温","2","1","1","2","64",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["428","6.16.107.7","Num7OC485_RoomHightTemp","7号空调室内高温","2","1","1","2","66",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["429","6.16.107.7","Num7OC485_RoomLowTemp","7号空调室内低温","2","1","1","2","67",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["430","6.16.107.7","Num7OC485_IndoorHightHumidity","7号空调室内高湿","2","1","1","2","68",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["431","6.16.107.7","Num7OC485_IndoorLowHumidity","7号空调室内低湿","2","1","1","2","69",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["432","6.16.107.7","Num7OC485_ChilledWaterFlowLoss","7号空调冷冻水水流丢失","2","1","1","2","74",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["433","6.16.107.7","Num7OC485_FilterBlock","7号空调过滤网堵塞","2","1","1","2","75",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["434","6.16.107.7","Num7OC485_1_status","7号空调通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["435","6.16.107.8","Num8OC485_ReturnAirTemp","8号空调回风温度","4","2","1","4","109",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["436","6.16.107.8","Num8OC485_ReturnAirHumidity","8号空调回风湿度","4","2","1","4","129",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["437","6.16.107.8","Num8OC485_ActualReturnTempSetPoint","8号空调实际回风温度设定点","4","2","1","4","110",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["438","6.16.107.8","Num8OC485_ActualReturnHumSetPoint","8号空调实际回风湿度设定点","4","2","1","4","130",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["439","6.16.107.8","Num8OC485_HighTempAlarmPoints","8号空调高温报警点","4","2","1","4","49",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["440","6.16.107.8","Num8OC485_LowTempAlarmPoints","8号空调低温报警点","4","2","1","4","50",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["441","6.16.107.8","Num8OC485_HightHumAlarmPoints","8号空调高湿报警点","4","2","1","4","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["442","6.16.107.8","Num8OC485_LowHumAlarmPoints","8号空调低湿报警点","4","2","1","4","54",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["443","6.16.107.8","Num8OC485_Fan","8号空调风机状态","2","1","1","2","24",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["444","6.16.107.8","Num8OC485_Refrigeration","8号空调制冷状态","2","1","1","2","25",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["445","6.16.107.8","Num8OC485_NaturalSourceCold","8号空调自然冷源状态","2","1","1","2","26",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["446","6.16.107.8","Num8OC485_StateWaterHeater","8号空调热水器状态","2","1","1","2","27",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["447","6.16.107.8","Num8OC485_ElectricHeater","8号空调电加热器状态","2","1","1","2","28",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["448","6.16.107.8","Num8OC485_Humidifier","8号空调加湿器状态","2","1","1","2","29",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["449","6.16.107.8","Num8OC485_Dehumidifier","8号空调除湿器状态","2","1","1","2","30",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["450","6.16.107.8","Num8OC485_FanOverload","8号空调风机过载","2","1","1","2","33",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["451","6.16.107.8","Num8OC485_AirLoss","8号空调气流丢失","2","1","1","2","34",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["452","6.16.107.8","Num8OC485_WaterLoss","8号空调水流丢失","2","1","1","2","35",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["453","6.16.107.8","Num8OC485_HighPressureCompressor1","8号空调压缩机1高压","2","1","1","2","36",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["454","6.16.107.8","Num8OC485_LowPressureCompressor1","8号空调压缩机1低压","2","1","1","2","37",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["455","6.16.107.8","Num8OC485_Compressor1Overload","8号空调压缩机1过载","2","1","1","2","38",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["456","6.16.107.8","Num8OC485_HightPressureCompressor2","8号空调压缩机2高压","2","1","1","2","40",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["457","6.16.107.8","Num8OC485_LowPressureCompressor2","8号空调压缩机2低压","2","1","1","2","41",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["458","6.16.107.8","Num8OC485_Compressor2Overload","8号空调压缩机2过载","2","1","1","2","42",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["459","6.16.107.8","Num8OC485_Compressor1PumpDownFail","8号空调压缩机1泵下降失败","2","1","1","2","39",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["460","6.16.107.8","Num8OC485_Compressor2PumpDownFail","8号空调压缩机2泵下降失败","2","1","1","2","43",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["461","6.16.107.8","Num8OC485_HumidifierFailure","8号空调加湿器故障","2","1","1","2","48",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["462","6.16.107.8","Num8OC485_CompressorPowerDown","8号空调压缩机掉电","2","1","1","2","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["463","6.16.107.8","Num8OC485_SysHighTemperature","8号空调系统高温","2","1","1","2","59",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["464","6.16.107.8","Num8OC485_SysPowerDown","8号空调系统掉电","2","1","1","2","60",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["465","6.16.107.8","Num8OC485_ChilledWaterTemp","8号空调冷冻水高温","2","1","1","2","64",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["466","6.16.107.8","Num8OC485_RoomHightTemp","8号空调室内高温","2","1","1","2","66",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["467","6.16.107.8","Num8OC485_RoomLowTemp","8号空调室内低温","2","1","1","2","67",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["468","6.16.107.8","Num8OC485_IndoorHightHumidity","8号空调室内高湿","2","1","1","2","68",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["469","6.16.107.8","Num8OC485_IndoorLowHumidity","8号空调室内低湿","2","1","1","2","69",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["470","6.16.107.8","Num8OC485_ChilledWaterFlowLoss","8号空调冷冻水水流丢失","2","1","1","2","74",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["471","6.16.107.8","Num8OC485_FilterBlock","8号空调过滤网堵塞","2","1","1","2","75",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["472","6.16.107.8","Num8OC485_2_status","8号空调通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["473","6.16.107.9","Num9OC485_ReturnAirTemp","9号空调回风温度","4","2","1","4","109",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["474","6.16.107.9","Num9OC485_ReturnAirHumidity","9号空调回风湿度","4","2","1","4","129",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["475","6.16.107.9","Num9OC485_ActualReturnTempSetPoint","9号空调实际回风温度设定点","4","2","1","4","110",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["476","6.16.107.9","Num9OC485_ActualReturnHumSetPoint","9号空调实际回风湿度设定点","4","2","1","4","130",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["477","6.16.107.9","Num9OC485_HighTempAlarmPoints","9号空调高温报警点","4","2","1","4","49",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["478","6.16.107.9","Num9OC485_LowTempAlarmPoints","9号空调低温报警点","4","2","1","4","50",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["479","6.16.107.9","Num9OC485_HightHumAlarmPoints","9号空调高湿报警点","4","2","1","4","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["480","6.16.107.9","Num9OC485_LowHumAlarmPoints","9号空调低湿报警点","4","2","1","4","54",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["481","6.16.107.9","Num9OC485_Fan","9号空调风机状态","2","1","1","2","24",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["482","6.16.107.9","Num9OC485_Refrigeration","9号空调制冷状态","2","1","1","2","25",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["483","6.16.107.9","Num9OC485_NaturalSourceCold","9号空调自然冷源状态","2","1","1","2","26",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["484","6.16.107.9","Num9OC485_StateWaterHeater","9号空调热水器状态","2","1","1","2","27",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["485","6.16.107.9","Num9OC485_ElectricHeater","9号空调电加热器状态","2","1","1","2","28",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["486","6.16.107.9","Num9OC485_Humidifier","9号空调加湿器状态","2","1","1","2","29",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["487","6.16.107.9","Num9OC485_Dehumidifier","9号空调除湿器状态","2","1","1","2","30",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["488","6.16.107.9","Num9OC485_FanOverload","9号空调风机过载","2","1","1","2","33",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["489","6.16.107.9","Num9OC485_AirLoss","9号空调气流丢失","2","1","1","2","34",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["490","6.16.107.9","Num9OC485_WaterLoss","9号空调水流丢失","2","1","1","2","35",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["491","6.16.107.9","Num9OC485_HighPressureCompressor1","9号空调压缩机1高压","2","1","1","2","36",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["492","6.16.107.9","Num9OC485_LowPressureCompressor1","9号空调压缩机1低压","2","1","1","2","37",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["493","6.16.107.9","Num9OC485_Compressor1Overload","9号空调压缩机1过载","2","1","1","2","38",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["494","6.16.107.9","Num9OC485_HightPressureCompressor2","9号空调压缩机2高压","2","1","1","2","40",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["495","6.16.107.9","Num9OC485_LowPressureCompressor2","9号空调压缩机2低压","2","1","1","2","41",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["496","6.16.107.9","Num9OC485_Compressor2Overload","9号空调压缩机2过载","2","1","1","2","42",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["497","6.16.107.9","Num9OC485_Compressor1PumpDownFail","9号空调压缩机1泵下降失败","2","1","1","2","39",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["498","6.16.107.9","Num9OC485_Compressor2PumpDownFail","9号空调压缩机2泵下降失败","2","1","1","2","43",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["499","6.16.107.9","Num9OC485_HumidifierFailure","9号空调加湿器故障","2","1","1","2","48",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["500","6.16.107.9","Num9OC485_CompressorPowerDown","9号空调压缩机掉电","2","1","1","2","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["501","6.16.107.9","Num9OC485_SysHighTemperature","9号空调系统高温","2","1","1","2","59",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["502","6.16.107.9","Num9OC485_SysPowerDown","9号空调系统掉电","2","1","1","2","60",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["503","6.16.107.9","Num9OC485_ChilledWaterTemp","9号空调冷冻水高温","2","1","1","2","64",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["504","6.16.107.9","Num9OC485_RoomHightTemp","9号空调室内高温","2","1","1","2","66",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["505","6.16.107.9","Num9OC485_RoomLowTemp","9号空调室内低温","2","1","1","2","67",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["506","6.16.107.9","Num9OC485_IndoorHightHumidity","9号空调室内高湿","2","1","1","2","68",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["507","6.16.107.9","Num9OC485_IndoorLowHumidity","9号空调室内低湿","2","1","1","2","69",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["508","6.16.107.9","Num9OC485_ChilledWaterFlowLoss","9号空调冷冻水水流丢失","2","1","1","2","74",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["509","6.16.107.9","Num9OC485_FilterBlock","9号空调过滤网堵塞","2","1","1","2","75",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["510","6.16.107.9","Num9OC485_1_status","9号空调通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["511","6.16.107.10","Num10OC485_ReturnAirTemp","10号空调回风温度","4","2","1","4","109",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["512","6.16.107.10","Num10OC485_ReturnAirHumidity","10号空调回风湿度","4","2","1","4","129",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["513","6.16.107.10","Num10OC485_ActualReturnTempSetPoint","10号空调实际回风温度设定点","4","2","1","4","110",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["514","6.16.107.10","Num10OC485_ActualReturnHumSetPoint","10号空调实际回风湿度设定点","4","2","1","4","130",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["515","6.16.107.10","Num10OC485_HighTempAlarmPoints","10号空调高温报警点","4","2","1","4","49",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["516","6.16.107.10","Num10OC485_LowTempAlarmPoints","10号空调低温报警点","4","2","1","4","50",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["517","6.16.107.10","Num10OC485_HightHumAlarmPoints","10号空调高湿报警点","4","2","1","4","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["518","6.16.107.10","Num10OC485_LowHumAlarmPoints","10号空调低湿报警点","4","2","1","4","54",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["519","6.16.107.10","Num10OC485_Fan","10号空调风机状态","2","1","1","2","24",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["520","6.16.107.10","Num10OC485_Refrigeration","10号空调制冷状态","2","1","1","2","25",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["521","6.16.107.10","Num10OC485_NaturalSourceCold","10号空调自然冷源状态","2","1","1","2","26",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["522","6.16.107.10","Num10OC485_StateWaterHeater","10号空调热水器状态","2","1","1","2","27",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["523","6.16.107.10","Num10OC485_ElectricHeater","10号空调电加热器状态","2","1","1","2","28",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["524","6.16.107.10","Num10OC485_Humidifier","10号空调加湿器状态","2","1","1","2","29",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["525","6.16.107.10","Num10OC485_Dehumidifier","10号空调除湿器状态","2","1","1","2","30",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["526","6.16.107.10","Num10OC485_FanOverload","10号空调风机过载","2","1","1","2","33",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["527","6.16.107.10","Num10OC485_AirLoss","10号空调气流丢失","2","1","1","2","34",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["528","6.16.107.10","Num10OC485_WaterLoss","10号空调水流丢失","2","1","1","2","35",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["529","6.16.107.10","Num10OC485_HighPressureCompressor1","10号空调压缩机1高压","2","1","1","2","36",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["530","6.16.107.10","Num10OC485_LowPressureCompressor1","10号空调压缩机1低压","2","1","1","2","37",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["531","6.16.107.10","Num10OC485_Compressor1Overload","10号空调压缩机1过载","2","1","1","2","38",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["532","6.16.107.10","Num10OC485_HightPressureCompressor2","10号空调压缩机2高压","2","1","1","2","40",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["533","6.16.107.10","Num10OC485_LowPressureCompressor2","10号空调压缩机2低压","2","1","1","2","41",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["534","6.16.107.10","Num10OC485_Compressor2Overload","10号空调压缩机2过载","2","1","1","2","42",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["535","6.16.107.10","Num10OC485_Compressor1PumpDownFail","10号空调压缩机1泵下降失败","2","1","1","2","39",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["536","6.16.107.10","Num10OC485_Compressor2PumpDownFail","10号空调压缩机2泵下降失败","2","1","1","2","43",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["537","6.16.107.10","Num10OC485_HumidifierFailure","10号空调加湿器故障","2","1","1","2","48",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["538","6.16.107.10","Num10OC485_CompressorPowerDown","10号空调压缩机掉电","2","1","1","2","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["539","6.16.107.10","Num10OC485_SysHighTemperature","10号空调系统高温","2","1","1","2","59",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["540","6.16.107.10","Num10OC485_SysPowerDown","10号空调系统掉电","2","1","1","2","60",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["541","6.16.107.10","Num10OC485_ChilledWaterTemp","10号空调冷冻水高温","2","1","1","2","64",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["542","6.16.107.10","Num10OC485_RoomHightTemp","10号空调室内高温","2","1","1","2","66",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["543","6.16.107.10","Num10OC485_RoomLowTemp","10号空调室内低温","2","1","1","2","67",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["544","6.16.107.10","Num10OC485_IndoorHightHumidity","10号空调室内高湿","2","1","1","2","68",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["545","6.16.107.10","Num10OC485_IndoorLowHumidity","10号空调室内低湿","2","1","1","2","69",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["546","6.16.107.10","Num10OC485_ChilledWaterFlowLoss","10号空调冷冻水水流丢失","2","1","1","2","74",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["547","6.16.107.10","Num10OC485_FilterBlock","10号空调过滤网堵塞","2","1","1","2","75",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["548","6.16.107.10","Num10OC485_2_status","10号空调通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]