{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["变量dat文件","CSpreadSheetBackup"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":157,"n_cols":76,"rows_kept":157,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","6.16.107.1","Num1OC485_ReturnAirTemp","1号空调回风温度","4","2","1","4","30110",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","6.16.107.1","Num1OC485_SupplyAirTemp","1号空调送风温度","4","2","1","4","30112",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.16.107.1","Num1OC485_ReturnAirHumidity","1号空调回风湿度","4","2","1","4","30130",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.16.107.1","Num1OC485_ActualReturnTempSetPoint","1号空调实际回风温度设定点","4","2","1","4","30111",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.16.107.1","Num1OC485_ActualSupplyTempSetPoint","1号空调实际送风温度设定点","4","2","1","4","30113",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.16.107.1","Num1OC485_ActualReturnHumSetPoint","1号空调实际回风湿度设定点","4","2","1","4","30131",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.16.107.1","Num1OC485_HighTempAlarmPoints","1号空调高温报警点","4","2","1","4","30050",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.16.107.1","Num1OC485_LowTempAlarmPoints","1号空调低温报警点","4","2","1","4","30051",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.16.107.1","Num1OC485_HightHumAlarmPoints","1号空调高湿报警点","4","2","1","4","30054",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.16.107.1","Num1OC485_LowHumAlarmPoints","1号空调低湿报警点","4","2","1","4","30055",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","6.16.107.1","Num1OC485_Fan","1号空调风机状态","4","2","1","2","10025",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","6.16.107.1","Num1OC485_Refrigeration","1号空调制冷状态","4","2","1","2","10026",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","6.16.107.1","Num1OC485_NaturalSourceCold","1号空调自然冷源状态","4","2","1","2","10027",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","6.16.107.1","Num1OC485_StateWaterHeater","1号空调热水器状态","4","2","1","2","10028",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","6.16.107.1","Num1OC485_ElectricHeater","1号空调电加热器状态","4","2","1","2","10029",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","6.16.107.1","Num1OC485_Humidifier","1号空调加湿器状态","4","2","1","2","10030",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","6.16.107.1","Num1OC485_Dehumidifier","1号空调除湿器状态","4","2","1","2","10031",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","6.16.107.1","Num1OC485_FanOverload","1号空调风机过载","4","2","1","2","10034",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["19","6.16.107.1","Num1OC485_AirLoss","1号空调气流丢失","4","2","1","2","10035",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["20","6.16.107.1","Num1OC485_WaterLoss","1号空调水流丢失","4","2","1","2","10036",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","6.16.107.1","Num1OC485_HighPressureCompressor1","1号空调压缩机1高压","4","2","1","2","10037",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["22","6.16.107.1","Num1OC485_LowPressureCompressor1","1号空调压缩机1低压","4","2","1","2","10038",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["23","6.16.107.1","Num1OC485_Compressor1Overload","1号空调压缩机1过载","4","2","1","2","10039",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["24","6.16.107.1","Num1OC485_HightPressureCompressor2","1号空调压缩机2高压","4","2","1","2","10041",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["25","6.16.107.1","Num1OC485_LowPressureCompressor2","1号空调压缩机2低压","4","2","1","2","10042",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["26","6.16.107.1","Num1OC485_Compressor2Overload","1号空调压缩机2过载","4","2","1","2","10043",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["27","6.16.107.1","Num1OC485_Compressor1PumpDownFail","1号空调压缩机1泵下降失败","4","2","1","2","10040",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["28","6.16.107.1","Num1OC485_Compressor2PumpDownFail","1号空调压缩机2泵下降失败","4","2","1","2","10044",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["29","6.16.107.1","Num1OC485_HumidifierFailure","1号空调加湿器故障","4","2","1","2","10049",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["30","6.16.107.1","Num1OC485_CompressorPowerDown","1号空调压缩机掉电","4","2","1","2","10054",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["31","6.16.107.1","Num1OC485_SysHighTemperature","1号空调系统高温","4","2","1","2","10060",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["32","6.16.107.1","Num1OC485_SysPowerDown","1号空调系统掉电","4","2","1","2","10061",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["33","6.16.107.1","Num1OC485_ChilledWaterTemp","1号空调冷冻水高温","4","2","1","2","10065",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["34","6.16.107.1","Num1OC485_RoomHightTemp","1号空调室内高温","4","2","1","2","10067",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["35","6.16.107.1","Num1OC485_RoomLowTemp","1号空调室内低温","4","2","1","2","10068",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["36","6.16.107.1","Num1OC485_IndoorHightHumidity","1号空调室内高湿","4","2","1","2","10069",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["37","6.16.107.1","Num1OC485_IndoorLowHumidity","1号空调室内低湿","4","2","1","2","10070",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["38","6.16.107.1","Num1OC485_ChilledWaterFlowLoss","1号空调冷冻水水流丢失","4","2","1","2","10075",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["39","6.16.107.1","Num1OC485_FilterBlock","1号空调过滤网堵塞","4","2","1","2","10076",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["1","6.16.107.2","Num2OC485_ReturnAirTemp","2号空调回风温度","4","2","1","4","30110",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","6.16.107.2","Num2OC485_SupplyAirTemp","2号空调送风温度","4","2","1","4","30112",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.16.107.2","Num2OC485_ReturnAirHumidity","2号空调回风湿度","4","2","1","4","30130",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.16.107.2","Num2OC485_ActualReturnTempSetPoint","2号空调实际回风温度设定点","4","2","1","4","30111",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.16.107.2","Num2OC485_ActualSupplyTempSetPoint","2号空调实际送风温度设定点","4","2","1","4","30113",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.16.107.2","Num2OC485_ActualReturnHumSetPoint","2号空调实际回风湿度设定点","4","2","1","4","30131",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.16.107.2","Num2OC485_HighTempAlarmPoints","2号空调高温报警点","4","2","1","4","30050",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.16.107.2","Num2OC485_LowTempAlarmPoints","2号空调低温报警点","4","2","1","4","30051",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.16.107.2","Num2OC485_HightHumAlarmPoints","2号空调高湿报警点","4","2","1","4","30054",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.16.107.2","Num2OC485_LowHumAlarmPoints","2号空调低湿报警点","4","2","1","4","30055",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","6.16.107.2","Num2OC485_Fan","2号空调风机状态","4","2","1","2","10025",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","6.16.107.2","Num2OC485_Refrigeration","2号空调制冷状态","4","2","1","2","10026",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","6.16.107.2","Num2OC485_NaturalSourceCold","2号空调自然冷源状态","4","2","1","2","10027",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","6.16.107.2","Num2OC485_StateWaterHeater","2号空调热水器状态","4","2","1","2","10028",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","6.16.107.2","Num2OC485_ElectricHeater","2号空调电加热器状态","4","2","1","2","10029",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","6.16.107.2","Num2OC485_Humidifier","2号空调加湿器状态","4","2","1","2","10030",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","6.16.107.2","Num2OC485_Dehumidifier","2号空调除湿器状态","4","2","1","2","10031",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","6.16.107.2","Num2OC485_FanOverload","2号空调风机过载","4","2","1","2","10034",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["19","6.16.107.2","Num2OC485_AirLoss","2号空调气流丢失","4","2","1","2","10035",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["20","6.16.107.2","Num2OC485_WaterLoss","2号空调水流丢失","4","2","1","2","10036",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","6.16.107.2","Num2OC485_HighPressureCompressor1","2号空调压缩机1高压","4","2","1","2","10037",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["22","6.16.107.2","Num2OC485_LowPressureCompressor1","2号空调压缩机1低压","4","2","1","2","10038",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["23","6.16.107.2","Num2OC485_Compressor1Overload","2号空调压缩机1过载","4","2","1","2","10039",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["24","6.16.107.2","Num2OC485_HightPressureCompressor2","2号空调压缩机2高压","4","2","1","2","10041",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["25","6.16.107.2","Num2OC485_LowPressureCompressor2","2号空调压缩机2低压","4","2","1","2","10042",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["26","6.16.107.2","Num2OC485_Compressor2Overload","2号空调压缩机2过载","4","2","1","2","10043",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["27","6.16.107.2","Num2OC485_Compressor1PumpDownFail","2号空调压缩机1泵下降失败","4","2","1","2","10040",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["28","6.16.107.2","Num2OC485_Compressor2PumpDownFail","2号空调压缩机2泵下降失败","4","2","1","2","10044",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["29","6.16.107.2","Num2OC485_HumidifierFailure","2号空调加湿器故障","4","2","1","2","10049",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["30","6.16.107.2","Num2OC485_CompressorPowerDown","2号空调压缩机掉电","4","2","1","2","10054",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["31","6.16.107.2","Num2OC485_SysHighTemperature","2号空调系统高温","4","2","1","2","10060",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["32","6.16.107.2","Num2OC485_SysPowerDown","2号空调系统掉电","4","2","1","2","10061",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["33","6.16.107.2","Num2OC485_ChilledWaterTemp","2号空调冷冻水高温","4","2","1","2","10065",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["34","6.16.107.2","Num2OC485_RoomHightTemp","2号空调室内高温","4","2","1","2","10067",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["35","6.16.107.2","Num2OC485_RoomLowTemp","2号空调室内低温","4","2","1","2","10068",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["36","6.16.107.2","Num2OC485_IndoorHightHumidity","2号空调室内高湿","4","2","1","2","10069",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["37","6.16.107.2","Num2OC485_IndoorLowHumidity","2号空调室内低湿","4","2","1","2","10070",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["38","6.16.107.2","Num2OC485_ChilledWaterFlowLoss","2号空调冷冻水水流丢失","4","2","1","2","10075",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["39","6.16.107.2","Num2OC485_FilterBlock","2号空调过滤网堵塞","4","2","1","2","10076",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["1","6.16.107.3","Num3OC485_ReturnAirTemp","3号空调回风温度","4","2","1","4","30110",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","6.16.107.3","Num3OC485_SupplyAirTemp","3号空调送风温度","4","2","1","4","30112",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.16.107.3","Num3OC485_ReturnAirHumidity","3号空调回风湿度","4","2","1","4","30130",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.16.107.3","Num3OC485_ActualReturnTempSetPoint","3号空调实际回风温度设定点","4","2","1","4","30111",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.16.107.3","Num3OC485_ActualSupplyTempSetPoint","3号空调实际送风温度设定点","4","2","1","4","30113",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.16.107.3","Num3OC485_ActualReturnHumSetPoint","3号空调实际回风湿度设定点","4","2","1","4","30131",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.16.107.3","Num3OC485_HighTempAlarmPoints","3号空调高温报警点","4","2","1","4","30050",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.16.107.3","Num3OC485_LowTempAlarmPoints","3号空调低温报警点","4","2","1","4","30051",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.16.107.3","Num3OC485_HightHumAlarmPoints","3号空调高湿报警点","4","2","1","4","30054",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.16.107.3","Num3OC485_LowHumAlarmPoints","3号空调低湿报警点","4","2","1","4","30055",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","6.16.107.3","Num3OC485_Fan","3号空调风机状态","4","2","1","2","10025",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","6.16.107.3","Num3OC485_Refrigeration","3号空调制冷状态","4","2","1","2","10026",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","6.16.107.3","Num3OC485_NaturalSourceCold","3号空调自然冷源状态","4","2","1","2","10027",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","6.16.107.3","Num3OC485_StateWaterHeater","3号空调热水器状态","4","2","1","2","10028",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","6.16.107.3","Num3OC485_ElectricHeater","3号空调电加热器状态","4","2","1","2","10029",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","6.16.107.3","Num3OC485_Humidifier","3号空调加湿器状态","4","2","1","2","10030",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","6.16.107.3","Num3OC485_Dehumidifier","3号空调除湿器状态","4","2","1","2","10031",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","6.16.107.3","Num3OC485_FanOverload","3号空调风机过载","4","2","1","2","10034",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["19","6.16.107.3","Num3OC485_AirLoss","3号空调气流丢失","4","2","1","2","10035",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["20","6.16.107.3","Num3OC485_WaterLoss","3号空调水流丢失","4","2","1","2","10036",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","6.16.107.3","Num3OC485_HighPressureCompressor1","3号空调压缩机1高压","4","2","1","2","10037",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["22","6.16.107.3","Num3OC485_LowPressureCompressor1","3号空调压缩机1低压","4","2","1","2","10038",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["23","6.16.107.3","Num3OC485_Compressor1Overload","3号空调压缩机1过载","4","2","1","2","10039",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["24","6.16.107.3","Num3OC485_HightPressureCompressor2","3号空调压缩机2高压","4","2","1","2","10041",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["25","6.16.107.3","Num3OC485_LowPressureCompressor2","3号空调压缩机2低压","4","2","1","2","10042",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["26","6.16.107.3","Num3OC485_Compressor2Overload","3号空调压缩机2过载","4","2","1","2","10043",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["27","6.16.107.3","Num3OC485_Compressor1PumpDownFail","3号空调压缩机1泵下降失败","4","2","1","2","10040",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["28","6.16.107.3","Num3OC485_Compressor2PumpDownFail","3号空调压缩机2泵下降失败","4","2","1","2","10044",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["29","6.16.107.3","Num3OC485_HumidifierFailure","3号空调加湿器故障","4","2","1","2","10049",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["30","6.16.107.3","Num3OC485_CompressorPowerDown","3号空调压缩机掉电","4","2","1","2","10054",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["31","6.16.107.3","Num3OC485_SysHighTemperature","3号空调系统高温","4","2","1","2","10060",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["32","6.16.107.3","Num3OC485_SysPowerDown","3号空调系统掉电","4","2","1","2","10061",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["33","6.16.107.3","Num3OC485_ChilledWaterTemp","3号空调冷冻水高温","4","2","1","2","10065",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["34","6.16.107.3","Num3OC485_RoomHightTemp","3号空调室内高温","4","2","1","2","10067",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["35","6.16.107.3","Num3OC485_RoomLowTemp","3号空调室内低温","4","2","1","2","10068",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["36","6.16.107.3","Num3OC485_IndoorHightHumidity","3号空调室内高湿","4","2","1","2","10069",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["37","6.16.107.3","Num3OC485_IndoorLowHumidity","3号空调室内低湿","4","2","1","2","10070",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["38","6.16.107.3","Num3OC485_ChilledWaterFlowLoss","3号空调冷冻水水流丢失","4","2","1","2","10075",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["39","6.16.107.3","Num3OC485_FilterBlock","3号空调过滤网堵塞","4","2","1","2","10076",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["1","6.16.107.4","Num4OC485_ReturnAirTemp","4号空调回风温度","4","2","1","4","30110",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","6.16.107.4","Num4OC485_SupplyAirTemp","4号空调送风温度","4","2","1","4","30112",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.16.107.4","Num4OC485_ReturnAirHumidity","4号空调回风湿度","4","2","1","4","30130",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.16.107.4","Num4OC485_ActualReturnTempSetPoint","4号空调实际回风温度设定点","4","2","1","4","30111",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.16.107.4","Num4OC485_ActualSupplyTempSetPoint","4号空调实际送风温度设定点","4","2","1","4","30113",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.16.107.4","Num4OC485_ActualReturnHumSetPoint","4号空调实际回风湿度设定点","4","2","1","4","30131",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.16.107.4","Num4OC485_HighTempAlarmPoints","4号空调高温报警点","4","2","1","4","30050",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.16.107.4","Num4OC485_LowTempAlarmPoints","4号空调低温报警点","4","2","1","4","30051",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.16.107.4","Num4OC485_HightHumAlarmPoints","4号空调高湿报警点","4","2","1","4","30054",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.16.107.4","Num4OC485_LowHumAlarmPoints","4号空调低湿报警点","4","2","1","4","30055",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","6.16.107.4","Num4OC485_Fan","4号空调风机状态","4","2","1","2","10025",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","6.16.107.4","Num4OC485_Refrigeration","4号空调制冷状态","4","2","1","2","10026",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","6.16.107.4","Num4OC485_NaturalSourceCold","4号空调自然冷源状态","4","2","1","2","10027",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","6.16.107.4","Num4OC485_StateWaterHeater","4号空调热水器状态","4","2","1","2","10028",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","6.16.107.4","Num4OC485_ElectricHeater","4号空调电加热器状态","4","2","1","2","10029",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","6.16.107.4","Num4OC485_Humidifier","4号空调加湿器状态","4","2","1","2","10030",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","6.16.107.4","Num4OC485_Dehumidifier","4号空调除湿器状态","4","2","1","2","10031",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","6.16.107.4","Num4OC485_FanOverload","4号空调风机过载","4","2","1","2","10034",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["19","6.16.107.4","Num4OC485_AirLoss","4号空调气流丢失","4","2","1","2","10035",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["20","6.16.107.4","Num4OC485_WaterLoss","4号空调水流丢失","4","2","1","2","10036",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","6.16.107.4","Num4OC485_HighPressureCompressor1","4号空调压缩机1高压","4","2","1","2","10037",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["22","6.16.107.4","Num4OC485_LowPressureCompressor1","4号空调压缩机1低压","4","2","1","2","10038",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["23","6.16.107.4","Num4OC485_Compressor1Overload","4号空调压缩机1过载","4","2","1","2","10039",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["24","6.16.107.4","Num4OC485_HightPressureCompressor2","4号空调压缩机2高压","4","2","1","2","10041",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["25","6.16.107.4","Num4OC485_LowPressureCompressor2","4号空调压缩机2低压","4","2","1","2","10042",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["26","6.16.107.4","Num4OC485_Compressor2Overload","4号空调压缩机2过载","4","2","1","2","10043",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["27","6.16.107.4","Num4OC485_Compressor1PumpDownFail","4号空调压缩机1泵下降失败","4","2","1","2","10040",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["28","6.16.107.4","Num4OC485_Compressor2PumpDownFail","4号空调压缩机2泵下降失败","4","2","1","2","10044",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["29","6.16.107.4","Num4OC485_HumidifierFailure","4号空调加湿器故障","4","2","1","2","10049",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["30","6.16.107.4","Num4OC485_CompressorPowerDown","4号空调压缩机掉电","4","2","1","2","10054",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["31","6.16.107.4","Num4OC485_SysHighTemperature","4号空调系统高温","4","2","1","2","10060",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["32","6.16.107.4","Num4OC485_SysPowerDown","4号空调系统掉电","4","2","1","2","10061",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["33","6.16.107.4","Num4OC485_ChilledWaterTemp","4号空调冷冻水高温","4","2","1","2","10065",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["34","6.16.107.4","Num4OC485_RoomHightTemp","4号空调室内高温","4","2","1","2","10067",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["35","6.16.107.4","Num4OC485_RoomLowTemp","4号空调室内低温","4","2","1","2","10068",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["36","6.16.107.4","Num4OC485_IndoorHightHumidity","4号空调室内高湿","4","2","1","2","10069",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["37","6.16.107.4","Num4OC485_IndoorLowHumidity","4号空调室内低湿","4","2","1","2","10070",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["38","6.16.107.4","Num4OC485_ChilledWaterFlowLoss","4号空调冷冻水水流丢失","4","2","1","2","10075",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["39","6.16.107.4","Num4OC485_FilterBlock","4号空调过滤网堵塞","4","2","1","2","10076",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]

{"sheet":"CSpreadSheetBackup","index":1,"n_rows":40,"n_cols":76,"rows_kept":40,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","6.16.107.1","Num1OC485_ReturnAirTemp","回风温度","4","2","1","4","30110",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","6.16.107.1","Num1OC485_SupplyAirTemp","送风温度","4","2","1","4","30112",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.16.107.1","Num1OC485_ReturnAirHumidity","回风湿度","4","2","1","4","30130",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.16.107.1","Num1OC485_ActualReturnTempSetPoint","实际回风温度设定点","4","2","1","4","30111",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.16.107.1","Num1OC485_ActualSupplyTempSetPoint","实际送风温度设定点","4","2","1","4","30113",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.16.107.1","Num1OC485_ActualReturnHumSetPoint","实际回风湿度设定点","4","2","1","4","30131",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.16.107.1","Num1OC485_HighTempAlarmPoints","高温报警点","4","2","1","4","30050",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.16.107.1","Num1OC485_LowTempAlarmPoints","低温报警点","4","2","1","4","30051",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.16.107.1","Num1OC485_HightHumAlarmPoints","高湿报警点","4","2","1","4","30054",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.16.107.1","Num1OC485_LowHumAlarmPoints","低湿报警点","4","2","1","4","30055",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","6.16.107.1","Num1OC485_Fan","风机状态","4","2","1","2","10025",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","6.16.107.1","Num1OC485_Refrigeration","制冷状态","4","2","1","2","10026",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","6.16.107.1","Num1OC485_NaturalSourceCold","自然冷源状态","4","2","1","2","10027",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","6.16.107.1","Num1OC485_StateWaterHeater","热水器状态","4","2","1","2","10028",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","6.16.107.1","Num1OC485_ElectricHeater","电加热器状态","4","2","1","2","10029",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","6.16.107.1","Num1OC485_Humidifier","加湿器状态","4","2","1","2","10030",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","6.16.107.1","Num1OC485_Dehumidifier","除湿器状态","4","2","1","2","10031",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","6.16.107.1","Num1OC485_FanOverload","风机过载","4","2","1","2","10034",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["19","6.16.107.1","Num1OC485_AirLoss","气流丢失","4","2","1","2","10035",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["20","6.16.107.1","Num1OC485_WaterLoss","水流丢失","4","2","1","2","10036",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","6.16.107.1","Num1OC485_HighPressureCompressor1","压缩机1高压","4","2","1","2","10037",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["22","6.16.107.1","Num1OC485_LowPressureCompressor1","压缩机1低压","4","2","1","2","10038",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["23","6.16.107.1","Num1OC485_Compressor1Overload","压缩机1过载","4","2","1","2","10039",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["24","6.16.107.1","Num1OC485_HightPressureCompressor2","压缩机2高压","4","2","1","2","10041",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["25","6.16.107.1","Num1OC485_LowPressureCompressor2","压缩机2低压","4","2","1","2","10042",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["26","6.16.107.1","Num1OC485_Compressor2Overload","压缩机2过载","4","2","1","2","10043",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["27","6.16.107.1","Num1OC485_Compressor1PumpDownFail","压缩机1泵下降失败","4","2","1","2","10040",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["28","6.16.107.1","Num1OC485_Compressor2PumpDownFail","压缩机2泵下降失败","4","2","1","2","10044",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["29","6.16.107.1","Num1OC485_HumidifierFailure","加湿器故障","4","2","1","2","10049",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["30","6.16.107.1","Num1OC485_CompressorPowerDown","压缩机掉电","4","2","1","2","10054",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["31","6.16.107.1","Num1OC485_SysHighTemperature","系统高温","4","2","1","2","10060",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["32","6.16.107.1","Num1OC485_SysPowerDown","系统掉电","4","2","1","2","10061",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["33","6.16.107.1","Num1OC485_ChilledWaterTemp","冷冻水高温","4","2","1","2","10065",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["34","6.16.107.1","Num1OC485_RoomHightTemp","室内高温","4","2","1","2","10067",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["35","6.16.107.1","Num1OC485_RoomLowTemp","室内低温","4","2","1","2","10068",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["36","6.16.107.1","Num1OC485_IndoorHightHumidity","室内高湿","4","2","1","2","10069",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["37","6.16.107.1","Num1OC485_IndoorLowHumidity","室内低湿","4","2","1","2","10070",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["38","6.16.107.1","Num1OC485_ChilledWaterFlowLoss","冷冻水水流丢失","4","2","1","2","10075",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["39","6.16.107.1","Num1OC485_FilterBlock","过滤网堵塞","4","2","1","2","10076",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]