{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":81,"n_cols":76,"rows_kept":81,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["50","6.16.107.1","Num1OC485_ReturnAirTemp","1号空调回风温度","4","2","1","4","109",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["51","6.16.107.1","Num1OC485_SupplyAirTemp","1号空调送风温度","4","2","1","4","111",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["52","6.16.107.1","Num1OC485_ReturnAirHumidity","1号空调回风湿度","4","2","1","4","129",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["53","6.16.107.1","Num1OC485_ActualReturnTempSetPoint","1号空调实际回风温度设定点","4","2","1","4","110",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["54","6.16.107.1","Num1OC485_ActualSupplyTempSetPoint","1号空调实际送风温度设定点","4","2","1","4","112",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["55","6.16.107.1","Num1OC485_ActualReturnHumSetPoint","1号空调实际回风湿度设定点","4","2","1","4","130",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["56","6.16.107.1","Num1OC485_HighTempAlarmPoints","1号空调高温报警点","4","2","1","4","49",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["57","6.16.107.1","Num1OC485_LowTempAlarmPoints","1号空调低温报警点","4","2","1","4","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["58","6.16.107.1","Num1OC485_HightHumAlarmPoints","1号空调高湿报警点","4","2","1","4","53",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["59","6.16.107.1","Num1OC485_LowHumAlarmPoints","1号空调低湿报警点","4","2","1","4","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["60","6.16.107.1","Num1OC485_Fan","1号空调风机状态","2","1","1","2","24",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["61","6.16.107.1","Num1OC485_Refrigeration","1号空调制冷状态","2","1","1","2","25",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["62","6.16.107.1","Num1OC485_NaturalSourceCold","1号空调自然冷源状态","2","1","1","2","26",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["63","6.16.107.1","Num1OC485_StateWaterHeater","1号空调热水器状态","2","1","1","2","27",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["64","6.16.107.1","Num1OC485_ElectricHeater","1号空调电加热器状态","2","1","1","2","28",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["65","6.16.107.1","Num1OC485_Humidifier","1号空调加湿器状态","2","1","1","2","29",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["66","6.16.107.1","Num1OC485_Dehumidifier","1号空调除湿器状态","2","1","1","2","30",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["67","6.16.107.1","Num1OC485_FanOverload","1号空调风机过载","2","1","1","2","33",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["68","6.16.107.1","Num1OC485_AirLoss","1号空调气流丢失","2","1","1","2","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["69","6.16.107.1","Num1OC485_WaterLoss","1号空调水流丢失","2","1","1","2","35",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["70","6.16.107.1","Num1OC485_HighPressureCompressor1","1号空调压缩机1高压","2","1","1","2","36",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["71","6.16.107.1","Num1OC485_LowPressureCompressor1","1号空调压缩机1低压","2","1","1","2","37",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["72","6.16.107.1","Num1OC485_Compressor1Overload","1号空调压缩机1过载","2","1","1","2","38",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["73","6.16.107.1","Num1OC485_HightPressureCompressor2","1号空调压缩机2高压","2","1","1","2","40",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["74","6.16.107.1","Num1OC485_LowPressureCompressor2","1号空调压缩机2低压","2","1","1","2","41",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["75","6.16.107.1","Num1OC485_Compressor2Overload","1号空调压缩机2过载","2","1","1","2","42",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["76","6.16.107.1","Num1OC485_Compressor1PumpDownFail","1号空调压缩机1泵下降失败","2","1","1","2","39",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["77","6.16.107.1","Num1OC485_Compressor2PumpDownFail","1号空调压缩机2泵下降失败","2","1","1","2","43",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["78","6.16.107.1","Num1OC485_HumidifierFailure","1号空调加湿器故障","2","1","1","2","48",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["79","6.16.107.1","Num1OC485_CompressorPowerDown","1号空调压缩机掉电","2","1","1","2","53",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["80","6.16.107.1","Num1OC485_SysHighTemperature","1号空调系统高温","2","1","1","2","59",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["81","6.16.107.1","Num1OC485_SysPowerDown","1号空调系统掉电","2","1","1","2","60",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["82","6.16.107.1","Num1OC485_ChilledWaterTemp","1号空调冷冻水高温","2","1","1","2","64",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["83","6.16.107.1","Num1OC485_RoomHightTemp","1号空调室内高温","2","1","1","2","66",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["84","6.16.107.1","Num1OC485_RoomLowTemp","1号空调室内低温","2","1","1","2","67",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["85","6.16.107.1","Num1OC485_IndoorHightHumidity","1号空调室内高湿","2","1","1","2","68",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["86","6.16.107.1","Num1OC485_IndoorLowHumidity","1号空调室内低湿","2","1","1","2","69",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["87","6.16.107.1","Num1OC485_ChilledWaterFlowLoss","1号空调冷冻水水流丢失","2","1","1","2","74",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["88","6.16.107.1","Num1OC485_FilterBlock","1号空调过滤网堵塞","2","1","1","2","75",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["89","6.16.107.1","Num1OC485_1_status","1号空调通信","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["90","6.16.107.2","Num2OC485_ReturnAirTemp","2号空调回风温度","4","2","1","4","109",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["91","6.16.107.2","Num2OC485_SupplyAirTemp","2号空调送风温度","4","2","1","4","111",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["92","6.16.107.2","Num2OC485_ReturnAirHumidity","2号空调回风湿度","4","2","1","4","129",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["93","6.16.107.2","Num2OC485_ActualReturnTempSetPoint","2号空调实际回风温度设定点","4","2","1","4","110",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["94","6.16.107.2","Num2OC485_ActualSupplyTempSetPoint","2号空调实际送风温度设定点","4","2","1","4","112",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["95","6.16.107.2","Num2OC485_ActualReturnHumSetPoint","2号空调实际回风湿度设定点","4","2","1","4","130",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["96","6.16.107.2","Num2OC485_HighTempAlarmPoints","2号空调高温报警点","4","2","1","4","49",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["97","6.16.107.2","Num2OC485_LowTempAlarmPoints","2号空调低温报警点","4","2","1","4","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["98","6.16.107.2","Num2OC485_HightHumAlarmPoints","2号空调高湿报警点","4","2","1","4","53",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["99","6.16.107.2","Num2OC485_LowHumAlarmPoints","2号空调低湿报警点","4","2","1","4","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["100","6.16.107.2","Num2OC485_Fan","2号空调风机状态","2","1","1","2","24",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["101","6.16.107.2","Num2OC485_Refrigeration","2号空调制冷状态","2","1","1","2","25",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["102","6.16.107.2","Num2OC485_NaturalSourceCold","2号空调自然冷源状态","2","1","1","2","26",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["103","6.16.107.2","Num2OC485_StateWaterHeater","2号空调热水器状态","2","1","1","2","27",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["104","6.16.107.2","Num2OC485_ElectricHeater","2号空调电加热器状态","2","1","1","2","28",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["105","6.16.107.2","Num2OC485_Humidifier","2号空调加湿器状态","2","1","1","2","29",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["106","6.16.107.2","Num2OC485_Dehumidifier","2号空调除湿器状态","2","1","1","2","30",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","255","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["107","6.16.107.2","Num2OC485_FanOverload","2号空调风机过载","2","1","1","2","33",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["108","6.16.107.2","Num2OC485_AirLoss","2号空调气流丢失","2","1","1","2","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["109","6.16.107.2","Num2OC485_WaterLoss","2号空调水流丢失","2","1","1","2","35",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["110","6.16.107.2","Num2OC485_HighPressureCompressor1","2号空调压缩机1高压","2","1","1","2","36",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["111","6.16.107.2","Num2OC485_LowPressureCompressor1","2号空调压缩机1低压","2","1","1","2","37",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["112","6.16.107.2","Num2OC485_Compressor1Overload","2号空调压缩机1过载","2","1","1","2","38",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["113","6.16.107.2","Num2OC485_HightPressureCompressor2","2号空调压缩机2高压","2","1","1","2","40",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["114","6.16.107.2","Num2OC485_LowPressureCompressor2","2号空调压缩机2低压","2","1","1","2","41",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["115","6.16.107.2","Num2OC485_Compressor2Overload","2号空调压缩机2过载","2","1","1","2","42",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["116","6.16.107.2","Num2OC485_Compressor1PumpDownFail","2号空调压缩机1泵下降失败","2","1","1","2","39",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["117","6.16.107.2","Num2OC485_Compressor2PumpDownFail","2号空调压缩机2泵下降失败","2","1","1","2","43",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["118","6.16.107.2","Num2OC485_HumidifierFailure","2号空调加湿器故障","2","1","1","2","48",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["119","6.16.107.2","Num2OC485_CompressorPowerDown","2号空调压缩机掉电","2","1","1","2","53",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["120","6.16.107.2","Num2OC485_SysHighTemperature","2号空调系统高温","2","1","1","2","59",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["121","6.16.107.2","Num2OC485_SysPowerDown","2号空调系统掉电","2","1","1","2","60",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["122","6.16.107.2","Num2OC485_ChilledWaterTemp","2号空调冷冻水高温","2","1","1","2","64",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["123","6.16.107.2","Num2OC485_RoomHightTemp","2号空调室内高温","2","1","1","2","66",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["124","6.16.107.2","Num2OC485_RoomLowTemp","2号空调室内低温","2","1","1","2","67",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["125","6.16.107.2","Num2OC485_IndoorHightHumidity","2号空调室内高湿","2","1","1","2","68",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["126","6.16.107.2","Num2OC485_IndoorLowHumidity","2号空调室内低湿","2","1","1","2","69",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["127","6.16.107.2","Num2OC485_ChilledWaterFlowLoss","2号空调冷冻水水流丢失","2","1","1","2","74",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["128","6.16.107.2","Num2OC485_FilterBlock","2号空调过滤网堵塞","2","1","1","2","75",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["129","6.16.107.2","Num2OC485_2_status","2号空调通信","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]