{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["变量dat文件","CSpreadSheetBackup"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":26,"n_cols":76,"rows_kept":26,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","6.16.107.1","Etronix_1_ReturnAirTemp","1号空调回风温度","4","2","1","3","2",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"25","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","6.16.107.1","Etronix_1_ReturnAirHumidity","1号空调回风湿度","4","2","1","3","1",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"65","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.16.107.1","Etronix_1_Fans","1号空调风机开关","4","16","1","1","1",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","10","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["5","6.16.107.1","Etronix_1_Comp1Status","1号空调压缩机1","4","16","1","1","1",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","21","107",null,null,"0","13","13",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["6","6.16.107.1","Etronix_1_Comp2Status","1号空调压缩机2","4","16","1","1","1",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","22","107",null,null,"0","14","14",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["7","6.16.107.1","Etronix_1_Heater1","1号空调加热器1","2","16","1","1","2",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","10","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["8","6.16.107.1","Etronix_1_Heater2","1号空调加热器2","2","16","1","1","2",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","11","107",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["9","6.16.107.1","Etronix_1_MainFan","1号空调主风扇","2","16","1","1","2",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","13","107",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["1","6.16.107.1","Etronix_1_AirPlug","1号空调气流堵塞","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","10","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["2","6.16.107.1","Etronix_1_FireAlarm","1号空调火灾报警","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","12","107",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["3","6.16.107.1","Etronix_1_FilterPlug","1号空调过滤网堵塞","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","13","107",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["4","6.16.107.1","Etronix_1_RoomTempHigh","1号空调房间温度过高","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","14","107",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["5","6.16.107.1","Etronix_1_RoomTempLow","1号空调房间温度过低","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","15","107",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["6","6.16.107.1","Etronix_1_HighHumidity","1号空调湿度过高","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","16","107",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["7","6.16.107.1","Etronix_1_LowHumidity","1号空调湿度过低","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","17","107",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["8","6.16.107.1","Etronix_1_TemperatureSernsorFault","1号空调房间温度传感器故障","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","22","107",null,null,"0","12","12",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["9","6.16.107.1","Etronix_1_HumiditySensorFault","1号空调房间湿度传感器故障","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","23","107",null,null,"0","13","13",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["10","6.16.107.1","Etronix_1_SendAirTemperatureSensor","1号空调送风温度传感器故障","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","24","107",null,null,"0","14","14",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["11","6.16.107.1","Etronix_1_WaterLeakgeAlarm","1号空调漏水报警","2","16","1","1","4",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","20","107",null,null,"0","10","10",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["12","6.16.107.1","Etronix_1_HighConductivityAlarm","1号空调高传导率报警","2","16","1","1","6",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","25","107",null,null,"0","15","15",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["13","6.16.107.1","Etronix_1_DrainageAlarm","1号空调排水报警","2","16","1","1","7",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","12","107",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["14","6.16.107.1","Etronix_1_CylinderFilledAlarm","1号空调气缸充满报警","2","16","1","1","7",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","13","107",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["15","6.16.107.1","Etronix_1_SendTemperatureHigh","1号空调送风温度过高","2","16","1","1","7",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","22","107",null,null,"0","12","12",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["16","6.16.107.1","Etronix_1_SendTemperatureLow","1号空调送风温度过低","2","16","1","1","7",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","23","107",null,null,"0","13","13",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["34","6.16.107.1","Etronix_1_Communications","1号空调通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]

{"sheet":"CSpreadSheetBackup","index":1,"n_rows":26,"n_cols":76,"rows_kept":26,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","6.16.107.1","Etronix_1_ReturnAirTemp","1号空调回风温度","4","2","1","3","2",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"25","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","6.16.107.1","Etronix_1_ReturnAirHumidity","1号空调回风湿度","4","2","1","3","1",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"65","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.16.107.1","Etronix_1_Fans","1号空调风机开关","4","16","1","1","1",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","10","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["5","6.16.107.1","Etronix_1_Comp1Status","1号空调压缩机1","4","16","1","1","1",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","21","107",null,null,"0","13","13",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["6","6.16.107.1","Etronix_1_Comp2Status","1号空调压缩机2","4","16","1","1","1",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","22","107",null,null,"0","14","14",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["7","6.16.107.1","Etronix_1_Heater1","1号空调加热器1","2","16","1","1","2",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","10","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["8","6.16.107.1","Etronix_1_Heater2","1号空调加热器2","2","16","1","1","2",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","11","107",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["9","6.16.107.1","Etronix_1_MainFan","1号空调主风扇","2","16","1","1","2",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","13","107",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["1","6.16.107.1","Etronix_1_AirPlug","1号空调气流堵塞","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","10","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["2","6.16.107.1","Etronix_1_FireAlarm","1号空调火灾报警","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","12","107",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","报警,"]
["3","6.16.107.1","Etronix_1_FilterPlug","1号空调过滤网堵塞","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","13","107",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["4","6.16.107.1","Etronix_1_RoomTempHigh","1号空调房间温度过高","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","14","107",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["5","6.16.107.1","Etronix_1_RoomTempLow","1号空调房间温度过低","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","15","107",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["6","6.16.107.1","Etronix_1_HighHumidity","1号空调湿度过高","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","16","107",null,null,"0","6","6",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["7","6.16.107.1","Etronix_1_LowHumidity","1号空调湿度过低","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","17","107",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["8","6.16.107.1","Etronix_1_TemperatureSernsorFault","1号空调房间温度传感器故障","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","22","107",null,null,"0","12","12",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["9","6.16.107.1","Etronix_1_HumiditySensorFault","1号空调房间湿度传感器故障","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","23","107",null,null,"0","13","13",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["10","6.16.107.1","Etronix_1_SendAirTemperatureSensor","1号空调送风温度传感器故障","2","16","1","1","3",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","24","107",null,null,"0","14","14",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["11","6.16.107.1","Etronix_1_WaterLeakgeAlarm","1号空调漏水报警","2","16","1","1","4",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","20","107",null,null,"0","10","10",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["12","6.16.107.1","Etronix_1_HighConductivityAlarm","1号空调高传导率报警","2","16","1","1","6",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","25","107",null,null,"0","15","15",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["13","6.16.107.1","Etronix_1_DrainageAlarm","1号空调排水报警","2","16","1","1","7",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","12","107",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["14","6.16.107.1","Etronix_1_CylinderFilledAlarm","1号空调气缸充满报警","2","16","1","1","7",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","13","107",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["15","6.16.107.1","Etronix_1_SendTemperatureHigh","1号空调送风温度过高","2","16","1","1","7",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","22","107",null,null,"0","12","12",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["16","6.16.107.1","Etronix_1_SendTemperatureLow","1号空调送风温度过低","2","16","1","1","7",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","23","107",null,null,"0","13","13",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["34","6.16.107.1","Etronix_1_Communications","1号空调通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]