{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["变量dat文件","CSpreadSheetBackup"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":93,"n_cols":76,"rows_kept":93,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","6.9.97.1","RCgroup_1_UnitSates","1号空调机组状态","4","1","1","2","119",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"1","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","0,","报警,"]
["2","6.9.97.1","RCgroup_1_SetpointTemp","1号空调温度设定点","4","2","1","3","16",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"65","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.9.97.1","RCgroup_1_SetpointHumi","1号空调湿度设定点","4","2","1","3","230",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"25","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.9.97.1","RCgroup_1_ReturnAirTemp","1号空调回风温度","4","2","1","3","2",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"65","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.9.97.1","RCgroup_1_ReturnAirHumidity","1号空调回风湿度","4","2","1","3","129",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"25","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.9.97.1","RCgroup_1_MainFan","1号空调主扇状态","4","1","1","2","5",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.9.97.1","RCgroup_1_Dehumidification","1号空调除湿器状态","4","1","1","2","6",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.9.97.1","RCgroup_1_Humidifier","1号空调加湿器状态","4","1","1","2","7",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.9.97.1","RCgroup_1_Comp1","1号空调压缩机1状态","4","1","1","2","15",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.9.97.1","RCgroup_1_Comp2","1号空调压缩机2状态","4","1","1","2","16",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","6.9.97.1","RCgroup_1_Heater1","1号空调加热器1状态","4","1","1","2","19",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","6.9.97.1","RCgroup_1_Heater2","1号空调加热器2状态","4","1","1","2","20",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","6.9.97.1","RCgroup_1_MainFanOverLoad","1号空调主扇过载","4","1","1","2","31",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["14","6.9.97.1","RCgroup_1_AirFlowSwitchAlarm","1号空调空气流量开关报警","4","1","1","2","32",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["15","6.9.97.1","RCgroup_1_AirFilterAlarm","1号空调空气过滤器报警","4","1","1","2","33",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["16","6.9.97.1","RCgroup_1_Comp1Overload","1号空调压缩机1过载","4","1","1","2","34",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["17","6.9.97.1","RCgroup_1_Comp2Overload","1号空调压缩机2过载","4","1","1","2","47",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["18","6.9.97.1","RCgroup_1_Comp1Hipres","1号空调压缩机1高压","4","1","1","2","35",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["19","6.9.97.1","RCgroup_1_Comp2Hipres","1号空调压缩机2高压","4","1","1","2","48",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["20","6.9.97.1","RCgroup_1_Comp1Lopres","1号空调压缩机1低压","4","1","1","2","37",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","6.9.97.1","RCgroup_1_Comp2Lopres","1号空调压缩机2低压","4","1","1","2","50",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["22","6.9.97.1","RCgroup_1_PresenceofWaterAlarm","1号空调积水报警","4","1","1","2","39",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["23","6.9.97.1","RCgroup_1_HiRoomTemp","1号空调高温报警","4","1","1","2","41",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["24","6.9.97.1","RCgroup_1_LoRoomTemp","1号空调低温报警","4","1","1","2","42",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["25","6.9.97.1","RCgroup_1_HiRoomHumi","1号空调高湿报警","4","1","1","2","43",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["26","6.9.97.1","RCgroup_1_LoRoomHumi","1号空调低湿报警","4","1","1","2","44",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["27","6.9.97.1","RCgroup_1_ProbeFailHumidity","1号空调湿度探测失败","4","1","1","2","51",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["28","6.9.97.1","RCgroup_1_ProbeFailTemp","1号空调温度探测失败","4","1","1","2","52",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["29","6.9.97.1","RCgroup_1_ProbeFailPressure","1号空调压力探测失败","4","1","1","2","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["30","6.9.97.1","RCgroup_1_Communications","1号空调通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
[]
["1","6.9.97.2","RCgroup_2_UnitSates","2号空调机组状态","4","1","1","2","119",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"1","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","0,","报警,"]
["2","6.9.97.2","RCgroup_2_SetpointTemp","2号空调温度设定点","4","2","1","3","16",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"65","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.9.97.2","RCgroup_2_SetpointHumi","2号空调湿度设定点","4","2","1","3","230",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"25","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.9.97.2","RCgroup_2_ReturnAirTemp","2号空调回风温度","4","2","1","3","2",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"65","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.9.97.2","RCgroup_2_ReturnAirHumidity","2号空调回风湿度","4","2","1","3","129",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"25","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.9.97.2","RCgroup_2_MainFan","2号空调主扇状态","4","1","1","2","5",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.9.97.2","RCgroup_2_Dehumidification","2号空调除湿器状态","4","1","1","2","6",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.9.97.2","RCgroup_2_Humidifier","2号空调加湿器状态","4","1","1","2","7",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.9.97.2","RCgroup_2_Comp1","2号空调压缩机1状态","4","1","1","2","15",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.9.97.2","RCgroup_2_Comp2","2号空调压缩机2状态","4","1","1","2","16",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","6.9.97.2","RCgroup_2_Heater1","2号空调加热器1状态","4","1","1","2","19",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","6.9.97.2","RCgroup_2_Heater2","2号空调加热器2状态","4","1","1","2","20",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","6.9.97.2","RCgroup_2_MainFanOverLoad","2号空调主扇过载","4","1","1","2","31",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["14","6.9.97.2","RCgroup_2_AirFlowSwitchAlarm","2号空调空气流量开关报警","4","1","1","2","32",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["15","6.9.97.2","RCgroup_2_AirFilterAlarm","2号空调空气过滤器报警","4","1","1","2","33",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["16","6.9.97.2","RCgroup_2_Comp1Overload","2号空调压缩机1过载","4","1","1","2","34",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["17","6.9.97.2","RCgroup_2_Comp2Overload","2号空调压缩机2过载","4","1","1","2","47",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["18","6.9.97.2","RCgroup_2_Comp1Hipres","2号空调压缩机1高压","4","1","1","2","35",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["19","6.9.97.2","RCgroup_2_Comp2Hipres","2号空调压缩机2高压","4","1","1","2","48",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["20","6.9.97.2","RCgroup_2_Comp1Lopres","2号空调压缩机1低压","4","1","1","2","37",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","6.9.97.2","RCgroup_2_Comp2Lopres","2号空调压缩机2低压","4","1","1","2","50",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["22","6.9.97.2","RCgroup_2_PresenceofWaterAlarm","2号空调积水报警","4","1","1","2","39",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["23","6.9.97.2","RCgroup_2_HiRoomTemp","2号空调高温报警","4","1","1","2","41",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["24","6.9.97.2","RCgroup_2_LoRoomTemp","2号空调低温报警","4","1","1","2","42",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["25","6.9.97.2","RCgroup_2_HiRoomHumi","2号空调高湿报警","4","1","1","2","43",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["26","6.9.97.2","RCgroup_2_LoRoomHumi","2号空调低湿报警","4","1","1","2","44",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["27","6.9.97.2","RCgroup_2_ProbeFailHumidity","2号空调湿度探测失败","4","1","1","2","51",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["28","6.9.97.2","RCgroup_2_ProbeFailTemp","2号空调温度探测失败","4","1","1","2","52",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["29","6.9.97.2","RCgroup_2_ProbeFailPressure","2号空调压力探测失败","4","1","1","2","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["30","6.9.97.2","RCgroup_2_Communications","2号空调通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
[]
["1","6.9.97.3","RCgroup_3_UnitSates","3号空调机组状态","4","1","1","2","119",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"1","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","0,","报警,"]
["2","6.9.97.3","RCgroup_3_SetpointTemp","3号空调温度设定点","4","2","1","3","16",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"65","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.9.97.3","RCgroup_3_SetpointHumi","3号空调湿度设定点","4","2","1","3","230",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"25","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.9.97.3","RCgroup_3_ReturnAirTemp","3号空调回风温度","4","2","1","3","2",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"65","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.9.97.3","RCgroup_3_ReturnAirHumidity","3号空调回风湿度","4","2","1","3","129",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"25","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.9.97.3","RCgroup_3_MainFan","3号空调主扇状态","4","1","1","2","5",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.9.97.3","RCgroup_3_Dehumidification","3号空调除湿器状态","4","1","1","2","6",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.9.97.3","RCgroup_3_Humidifier","3号空调加湿器状态","4","1","1","2","7",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.9.97.3","RCgroup_3_Comp1","3号空调压缩机1状态","4","1","1","2","15",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.9.97.3","RCgroup_3_Comp2","3号空调压缩机2状态","4","1","1","2","16",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","6.9.97.3","RCgroup_3_Heater1","3号空调加热器1状态","4","1","1","2","19",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","6.9.97.3","RCgroup_3_Heater2","3号空调加热器2状态","4","1","1","2","20",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","6.9.97.3","RCgroup_3_MainFanOverLoad","3号空调主扇过载","4","1","1","2","31",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["14","6.9.97.3","RCgroup_3_AirFlowSwitchAlarm","3号空调空气流量开关报警","4","1","1","2","32",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["15","6.9.97.3","RCgroup_3_AirFilterAlarm","3号空调空气过滤器报警","4","1","1","2","33",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["16","6.9.97.3","RCgroup_3_Comp1Overload","3号空调压缩机1过载","4","1","1","2","34",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["17","6.9.97.3","RCgroup_3_Comp2Overload","3号空调压缩机2过载","4","1","1","2","47",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["18","6.9.97.3","RCgroup_3_Comp1Hipres","3号空调压缩机1高压","4","1","1","2","35",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["19","6.9.97.3","RCgroup_3_Comp2Hipres","3号空调压缩机2高压","4","1","1","2","48",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["20","6.9.97.3","RCgroup_3_Comp1Lopres","3号空调压缩机1低压","4","1","1","2","37",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","6.9.97.3","RCgroup_3_Comp2Lopres","3号空调压缩机2低压","4","1","1","2","50",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["22","6.9.97.3","RCgroup_3_PresenceofWaterAlarm","3号空调积水报警","4","1","1","2","39",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["23","6.9.97.3","RCgroup_3_HiRoomTemp","3号空调高温报警","4","1","1","2","41",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["24","6.9.97.3","RCgroup_3_LoRoomTemp","3号空调低温报警","4","1","1","2","42",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["25","6.9.97.3","RCgroup_3_HiRoomHumi","3号空调高湿报警","4","1","1","2","43",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["26","6.9.97.3","RCgroup_3_LoRoomHumi","3号空调低湿报警","4","1","1","2","44",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["27","6.9.97.3","RCgroup_3_ProbeFailHumidity","3号空调湿度探测失败","4","1","1","2","51",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["28","6.9.97.3","RCgroup_3_ProbeFailTemp","3号空调温度探测失败","4","1","1","2","52",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["29","6.9.97.3","RCgroup_3_ProbeFailPressure","3号空调压力探测失败","4","1","1","2","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["30","6.9.97.3","RCgroup_3_Communications","3号空调通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]

{"sheet":"CSpreadSheetBackup","index":1,"n_rows":36,"n_cols":78,"rows_kept":36,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述","F77","F78"]
["1","6.9.97.1","RCgroup_1_UnitSates","1号空调机组状态","4","1","1","2","119",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"1","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","0,","报警,"]
["2","6.9.97.1","RCgroup_1_SetpointTemp","1号空调温度设定点","4","2","1","3","16",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"65","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.9.97.1","RCgroup_1_SetpointHumi","1号空调湿度设定点","4","2","1","3","230",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"25","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.9.97.1","RCgroup_1_ReturnAirTemp","1号空调回风温度","4","2","1","3","2",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","℃","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"65","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.9.97.1","RCgroup_1_ReturnAirHumidity","1号空调回风湿度","4","2","1","3","129",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","900","0.1000000015","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"25","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.9.97.1","RCgroup_1_MainFan","1号空调主扇状态","4","1","1","2","5",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.9.97.1","RCgroup_1_Dehumidification","1号空调除湿器状态","4","1","1","2","6",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","6.9.97.1","RCgroup_1_Humidifier","1号空调加湿器状态","4","1","1","2","7",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","6.9.97.1","RCgroup_1_Comp1","1号空调加热器1状态","4","1","1","2","15",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","6.9.97.1","RCgroup_1_Comp2","1号空调加热器2状态","4","1","1","2","16",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","6.9.97.1","RCgroup_1_Heater1","1号空调加热器1状态","4","1","1","2","19",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","6.9.97.1","RCgroup_1_Heater2","1号空调加热器2状态","4","1","1","2","20",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","6.9.97.1","RCgroup_1_Comp1Alarm1","1号空调压缩机1报警","4","1","1","2","81",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["14","6.9.97.1","RCgroup_1_Comp1Alarm2","1号空调压缩机2报警","4","1","1","2","82",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["15","6.9.97.1","RCgroup_1_TempAlarm","1号空调温度报警","4","1","1","2","83",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["16","6.9.97.1","RCgroup_1_HumiAlarm","1号空调湿度报警","4","1","1","2","84",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["17","6.9.97.1","RCgroup_1_AllAlarm","1号空调任意报警","4","1","1","2","30",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["18","6.9.97.1","RCgroup_1_MainFanOverLoad","1号空调主扇过载","4","1","1","2","31",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["19","6.9.97.1","RCgroup_1_AirFlowSwitchAlarm","1号空调空气流量开关报警","4","1","1","2","32",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["20","6.9.97.1","RCgroup_1_AirFilterAlarm","1号空调空气过滤器报警","4","1","1","2","33",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["21","6.9.97.1","RCgroup_1_Comp1Overload","1号空调压缩机1过载","4","1","1","2","34",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["22","6.9.97.1","RCgroup_1_Comp2Overload","1号空调压缩机2过载","4","1","1","2","47",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["23","6.9.97.1","RCgroup_1_Comp1Hipres","1号空调压缩机1高压","4","1","1","2","35",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["24","6.9.97.1","RCgroup_1_Comp2Hipres","1号空调压缩机2高压","4","1","1","2","48",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["25","6.9.97.1","RCgroup_1_Comp1Lopres","1号空调压缩机1低压","4","1","1","2","37",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["26","6.9.97.1","RCgroup_1_Comp2Lopres","1号空调压缩机2低压","4","1","1","2","50",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["27","6.9.97.1","RCgroup_1_PresenceofWaterAlarm","1号空调积水报警","4","1","1","2","39",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["28","6.9.97.1","RCgroup_1_HiRoomTemp","1号空调高温报警","4","1","1","2","41",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["29","6.9.97.1","RCgroup_1_LoRoomTemp","1号空调低温报警","4","1","1","2","42",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["30","6.9.97.1","RCgroup_1_HiRoomHumi","1号空调高湿报警","4","1","1","2","43",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["31","6.9.97.1","RCgroup_1_LoRoomHumi","1号空调低湿报警","4","1","1","2","44",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["32","6.9.97.1","RCgroup_1_ProbeFailHumidity","1号空调湿度探测失败","4","1","1","2","51",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["33","6.9.97.1","RCgroup_1_ProbeFailTemp","1号空调温度探测失败","4","1","1","2","52",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["34","6.9.97.1","RCgroup_1_ProbeFailPressure","1号空调压力探测失败","4","1","1","2","53",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警,"]
["35","6.9.97.1","RCgroup_1_Communications","1号空调通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]