{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":37,"n_cols":76,"rows_kept":37,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","5.1.56.1","ComAp_1_GeneratorVL1","发电机L1相电压","4","2","1","3","8192",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","5.1.56.1","ComAp_1_GeneratorVL2","发电机L2相电压","4","2","1","3","8193",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","5.1.56.1","ComAp_1_GeneratorVL3","发电机L3相电压","4","2","1","3","8194",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","5.1.56.1","ComAp_1_GenVL12","发电机L12电压","4","2","1","3","9628",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","5.1.56.1","ComAp_1_GenVL23","发电机L23电压","4","2","1","3","9629",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","5.1.56.1","ComAp_1_GenVL31","发电机L31电压","4","2","1","3","9630",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","5.1.56.1","ComAp_1_GenCurrL1","发电机L1相电流","4","2","1","3","8198",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","5.1.56.1","ComAp_1_GenCurrL2","发电机L2相电流","4","2","1","3","8199",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","5.1.56.1","ComAp_1_GenCurrL3","发电机L3相电流","4","2","1","3","8200",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","5.1.56.1","ComAp_1_ActPwrL1","发电机L1有功功率","4","2","1","3","8524",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","5.1.56.1","ComAp_1_ActPwrL2","发电机L2有功功率","4","2","1","3","8525",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","5.1.56.1","ComAp_1_ActPwrL3","发电机L3有功功率","4","2","1","3","8526",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","5.1.56.1","ComAp_1_ActPower","发电机总有功功率","4","2","1","3","8202",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","5.1.56.1","ComAp_1_ReactPwrL1","发电机L1无功功率","4","2","1","3","8527",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","5.1.56.1","ComAp_1_ReactPwrL2","发电机L2无功功率","4","2","1","3","8528",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","5.1.56.1","ComAp_1_ReactPwrL3","发电机L3无功功率","4","2","1","3","8529",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","5.1.56.1","ComAp_1_ReactPwr","发电机总无功功率","4","2","1","3","8565",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","5.1.56.1","ComAp_1_ApparPwrL1","发电机L1视在功率","4","2","1","3","8530",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KVA","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","5.1.56.1","ComAp_1_ApparPwrL2","发电机L2视在功率","4","2","1","3","8531",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KVA","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","5.1.56.1","ComAp_1_ApparPwrL3","发电机L3视在功率","4","2","1","3","8532",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KVA","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","5.1.56.1","ComAp_1_ApparPwr","发电机总视在功率","4","2","1","3","8565",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KVA","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","5.1.56.1","ComAp_1_PwrFactorL1","发电机L1功率因数","4","2","1","3","8533",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","5.1.56.1","ComAp_1_PwrFactorL2","发电机L2功率因数","4","2","1","3","8534",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","5.1.56.1","ComAp_1_PwrFactorL3","发电机L3功率因数","4","2","1","3","8535",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","5.1.56.1","ComAp_1_PwrFactor","总功率因数","4","2","1","3","8204",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","5.1.56.1","ComAp_1_GenFreq","发电频率","4","2","1","3","8210",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","5.1.56.1","ComAp_1_EngineSpeedRPM","发动机转速","4","2","1","3","8209",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","RMP","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","5.1.56.1","ComAp_1_kWhours","千瓦小时数","4","2","1","3","8205",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KWH","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","5.1.56.1","ComAp_1_RunHours","运行小时数","4","2","1","3","8206",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","H","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","5.1.56.1","ComAp_1_NumStarts","启动次数","4","2","1","3","8207",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","次","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","5.1.56.1","ComAp_1_BattVolt","电池电压","4","2","1","3","8213",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","5.1.56.1","ComAp_1_OilPress","油压","4","2","1","3","8227",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Bar","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","5.1.56.1","ComAp_1_WaterTemp","水温","4","2","1","3","8228",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","5.1.56.1","ComAp_1_Fuel Level","水位","4","2","1","3","8229",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","5.1.56.1","ComAp_1_AlarmList","报警表","4","2","1","3","8229",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","17","272,273,275,276,379,392,385,395,449,396,397,406,455,409,411,470,","低水位,紧急停机,遥控关,高水温,低油压,发电压不平停机,市电电压不平衡,电流不平衡停机,过载停机,GCB停机,超速停机,IOM故障停机,速度传感器故障,电池耗尽停机,电流短路停机,ECU故障,"]
["36","5.1.56.1","ComAp_1_Communications","发电机通信状态","1000","2","1","3",{"$nulls":3},"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","通信中断,"]