{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["变量dat文件","CSpreadSheetBackup"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":320,"n_cols":76,"rows_kept":320,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","9.1.114.1","FL_1_MainAP_Volt","主回路A相电压","4","2","1","3","0",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","FL_1_MainBP_Volt","主回路B相电压","4","2","1","3","1",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","FL_1_MainCP_Volt","主回路C相电压","4","2","1","3","2",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","9.1.114.1","FL_1_MainABL_Volt","主回路AB线电压","4","2","1","3","3",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","9.1.114.1","FL_1_MainBCL_Volt","主回路BC线电压","4","2","1","3","4",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","9.1.114.1","FL_1_MainCAL_Volt","主回路CA线电压","4","2","1","3","5",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","9.1.114.1","FL_1_MainAP_Curr","主回路A相电流","4","2","1","3","6",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.04","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","9.1.114.1","FL_1_MainBP_Curr","主回路B相电流","4","2","1","3","7",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.04","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","9.1.114.1","FL_1_MainCP_Curr","主回路C相电流","4","2","1","3","8",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.04","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","9.1.114.1","FL_1_MainAP_APower","主回路A相有功","4","2","1","3","14",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","4.0","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","9.1.114.1","FL_1_MainBP_Apower","主回路B相有功","4","2","1","3","15",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","4.0","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","9.1.114.1","FL_1_MainCP_Apower","主回路C相有功","4","2","1","3","16",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","4.0","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","9.1.114.1","FL_1_MainAP_RPower","主回路A相无功","4","2","1","3","17",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","var","300","4.0","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.1","FL_1_MainBP_Rpower","主回路B相无功","4","2","1","3","18",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","var","300","4.0","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","9.1.114.1","FL_1_MainCP_Rpower","主回路C相无功","4","2","1","3","19",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","var","300","4.0","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","9.1.114.1","FL_1_Main_Frequency","主回路频率","4","2","1","3","23",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","9.1.114.1","FL_1_Main_Switch","主回路主开关开关量","4","2","1","3","36",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","9.1.114.1","FL_1_Main_AlarmIndicator","主回路报警指示灯状态","4","2","1","3","37",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","9.1.114.1","FL_1_Main_AlarmBuzzer","主回路报警蜂鸣器状态","4","2","1","3","38",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","9.1.114.1","FL_1_MainAP_THDVolt","主回路A相电压THD ","4","2","1","3","39",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","9.1.114.1","FL_1_MainBP_THDVolt","主回路B相电压THD ","4","2","1","3","40",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.1","FL_1_MainCP_THDVolt","主回路C相电压THD ","4","2","1","3","41",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.1","FL_1_MainAP_THDCurr","主回路A相电流THD","4","2","1","3","42",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.1","FL_1_MainBP_THDCurr","主回路B相电流THD","4","2","1","3","43",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.1","FL_1_MainCP_THDCurr","主回路C相电流THD","4","2","1","3","44",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","9.1.114.1","FL_1_Main_LinearCur","主回路中线性电流","4","2","1","3","45",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.04","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","9.1.114.1","FL_1_Main_AvgCur","主回路平均电流","4","2","1","3","46",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.04","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","9.1.114.1","FL_1_Main_LineAvgVolt","主回路线电压平均值","4","2","1","3","47",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","9.1.114.1","FL_1_Main_PhaseAvgVolt","主回路相电压平均值","4","2","1","3","48",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","9.1.114.1","FL_1_BSV_101","支路开关量101","4","2","1","3","90",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","9.1.114.1","FL_1_BSV_102","支路开关量102","4","2","1","3","91",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","9.1.114.1","FL_1_BSV_103","支路开关量103","4","2","1","3","92",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","9.1.114.1","FL_1_BSV_104","支路开关量104","4","2","1","3","93",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","9.1.114.1","FL_1_BSV_105","支路开关量105","4","2","1","3","94",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["36","9.1.114.1","FL_1_BSV_106","支路开关量106","4","2","1","3","95",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["37","9.1.114.1","FL_1_BSV_107","支路开关量107","4","2","1","3","96",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["38","9.1.114.1","FL_1_BSV_108","支路开关量108","4","2","1","3","97",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["39","9.1.114.1","FL_1_BSV_109","支路开关量109","4","2","1","3","98",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["40","9.1.114.1","FL_1_BSV_110","支路开关量110","4","2","1","3","99",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["41","9.1.114.1","FL_1_BSV_111","支路开关量111","4","2","1","3","100",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["42","9.1.114.1","FL_1_BSV_112","支路开关量112","4","2","1","3","101",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["43","9.1.114.1","FL_1_BSV_113","支路开关量113","4","2","1","3","102",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["44","9.1.114.1","FL_1_BSV_114","支路开关量114","4","2","1","3","103",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["46","9.1.114.1","FL_1_BSV_201","支路开关量201","4","2","1","3","130",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["47","9.1.114.1","FL_1_BSV_202","支路开关量202","4","2","1","3","131",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["48","9.1.114.1","FL_1_BSV_203","支路开关量203","4","2","1","3","132",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["49","9.1.114.1","FL_1_BSV_204","支路开关量204","4","2","1","3","133",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["50","9.1.114.1","FL_1_BSV_205","支路开关量205","4","2","1","3","134",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["51","9.1.114.1","FL_1_BSV_206","支路开关量206","4","2","1","3","135",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["52","9.1.114.1","FL_1_BSV_207","支路开关量207","4","2","1","3","136",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["53","9.1.114.1","FL_1_BSV_208","支路开关量208","4","2","1","3","137",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["54","9.1.114.1","FL_1_BSV_209","支路开关量209","4","2","1","3","138",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["55","9.1.114.1","FL_1_BSV_210","支路开关量210","4","2","1","3","139",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["56","9.1.114.1","FL_1_BSV_211","支路开关量211","4","2","1","3","140",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["57","9.1.114.1","FL_1_BSV_212","支路开关量212","4","2","1","3","141",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["58","9.1.114.1","FL_1_BSV_213","支路开关量213","4","2","1","3","142",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["59","9.1.114.1","FL_1_BSV_214","支路开关量214","4","2","1","3","143",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["60","9.1.114.1","FL_1_BSV_215","支路开关量215","4","2","1","3","144",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["61","9.1.114.1","FL_1_BSV_216","支路开关量216","4","2","1","3","145",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["62","9.1.114.1","FL_1_BSV_217","支路开关量217","4","2","1","3","146",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["63","9.1.114.1","FL_1_BSV_218","支路开关量218","4","2","1","3","147",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["64","9.1.114.1","FL_1_BSV_219","支路开关量219","4","2","1","3","148",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["65","9.1.114.1","FL_1_BSV_220","支路开关量220","4","2","1","3","149",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["66","9.1.114.1","FL_1_BSV_221","支路开关量221","4","2","1","3","150",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["67","9.1.114.1","FL_1_BSV_222","支路开关量222","4","2","1","3","151",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["68","9.1.114.1","FL_1_BSV_223","支路开关量223","4","2","1","3","152",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["69","9.1.114.1","FL_1_BSV_224","支路开关量224","4","2","1","3","153",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["71","9.1.114.1","FL_1_BSV_301","支路开关量301","4","2","1","3","160",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["72","9.1.114.1","FL_1_BSV_302","支路开关量302","4","2","1","3","161",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["73","9.1.114.1","FL_1_BSV_303","支路开关量303","4","2","1","3","162",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["74","9.1.114.1","FL_1_BSV_304","支路开关量304","4","2","1","3","163",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["75","9.1.114.1","FL_1_BSV_305","支路开关量305","4","2","1","3","164",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["76","9.1.114.1","FL_1_BSV_306","支路开关量306","4","2","1","3","165",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["77","9.1.114.1","FL_1_BSV_307","支路开关量307","4","2","1","3","166",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["78","9.1.114.1","FL_1_BSV_308","支路开关量308","4","2","1","3","167",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["79","9.1.114.1","FL_1_BSV_309","支路开关量309","4","2","1","3","168",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["80","9.1.114.1","FL_1_BSV_310","支路开关量310","4","2","1","3","169",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["81","9.1.114.1","FL_1_BSV_311","支路开关量311","4","2","1","3","170",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["82","9.1.114.1","FL_1_BSV_312","支路开关量312","4","2","1","3","171",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["83","9.1.114.1","FL_1_BSV_313","支路开关量313","4","2","1","3","172",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["84","9.1.114.1","FL_1_BSV_314","支路开关量314","4","2","1","3","173",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["85","9.1.114.1","FL_1_BSV_315","支路开关量315","4","2","1","3","174",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["86","9.1.114.1","FL_1_BSV_316","支路开关量316","4","2","1","3","175",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["87","9.1.114.1","FL_1_BSV_317","支路开关量317","4","2","1","3","176",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["88","9.1.114.1","FL_1_BSV_318","支路开关量318","4","2","1","3","177",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["89","9.1.114.1","FL_1_BSV_319","支路开关量319","4","2","1","3","178",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["90","9.1.114.1","FL_1_BSV_320","支路开关量320","4","2","1","3","179",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["91","9.1.114.1","FL_1_BSV_321","支路开关量321","4","2","1","3","180",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["92","9.1.114.1","FL_1_BSV_322","支路开关量322","4","2","1","3","181",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["93","9.1.114.1","FL_1_BSV_323","支路开关量323","4","2","1","3","182",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["94","9.1.114.1","FL_1_BSV_324","支路开关量324","4","2","1","3","183",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["96","9.1.114.1","FL_1_BSV_401","支路开关量401","4","2","1","3","190",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["97","9.1.114.1","FL_1_BSV_402","支路开关量402","4","2","1","3","191",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["98","9.1.114.1","FL_1_BSV_403","支路开关量403","4","2","1","3","192",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["99","9.1.114.1","FL_1_BSV_404","支路开关量404","4","2","1","3","193",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["100","9.1.114.1","FL_1_BSV_405","支路开关量405","4","2","1","3","194",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["101","9.1.114.1","FL_1_BSV_406","支路开关量406","4","2","1","3","195",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["102","9.1.114.1","FL_1_BSV_407","支路开关量407","4","2","1","3","196",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["103","9.1.114.1","FL_1_BSV_408","支路开关量408","4","2","1","3","197",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["104","9.1.114.1","FL_1_BSV_409","支路开关量409","4","2","1","3","198",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["105","9.1.114.1","FL_1_BSV_410","支路开关量410","4","2","1","3","199",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["106","9.1.114.1","FL_1_BSV_411","支路开关量411","4","2","1","3","200",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["107","9.1.114.1","FL_1_BSV_412","支路开关量412","4","2","1","3","201",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["108","9.1.114.1","FL_1_BSV_413","支路开关量413","4","2","1","3","202",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["109","9.1.114.1","FL_1_BSV_414","支路开关量414","4","2","1","3","203",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["110","9.1.114.1","FL_1_BSV_415","支路开关量415","4","2","1","3","204",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["111","9.1.114.1","FL_1_BSV_416","支路开关量416","4","2","1","3","205",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["112","9.1.114.1","FL_1_BSV_417","支路开关量417","4","2","1","3","206",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["113","9.1.114.1","FL_1_BSV_418","支路开关量418","4","2","1","3","207",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["114","9.1.114.1","FL_1_BSV_419","支路开关量419","4","2","1","3","208",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["115","9.1.114.1","FL_1_BSV_420","支路开关量420","4","2","1","3","209",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["116","9.1.114.1","FL_1_BSV_421","支路开关量421","4","2","1","3","210",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["117","9.1.114.1","FL_1_BSV_422","支路开关量422","4","2","1","3","211",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["118","9.1.114.1","FL_1_BSV_423","支路开关量423","4","2","1","3","212",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["119","9.1.114.1","FL_1_BSV_424","支路开关量424","4","2","1","3","213",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["121","9.1.114.1","FL_1_BSV_501","支路开关量501","4","2","1","3","220",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["122","9.1.114.1","FL_1_BSV_502","支路开关量502","4","2","1","3","221",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["123","9.1.114.1","FL_1_BSV_503","支路开关量503","4","2","1","3","222",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["124","9.1.114.1","FL_1_BSV_504","支路开关量504","4","2","1","3","223",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["125","9.1.114.1","FL_1_LigProdeStates","防雷器状态","4","2","1","3","224",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["127","9.1.114.1","FL_1_BSC_101A","支路电流值101A","4","2","1","3","230",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["128","9.1.114.1","FL_1_BSC_101B","支路电流值101B","4","2","1","3","231",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["129","9.1.114.1","FL_1_BSC_101C","支路电流值101C","4","2","1","3","232",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["130","9.1.114.1","FL_1_BSC_102A","支路电流值102A","4","2","1","3","233",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["131","9.1.114.1","FL_1_BSC_102B","支路电流值102B","4","2","1","3","234",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["132","9.1.114.1","FL_1_BSC_102C","支路电流值102C","4","2","1","3","235",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["133","9.1.114.1","FL_1_BSC_103A","支路电流值103A","4","2","1","3","236",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["134","9.1.114.1","FL_1_BSC_103B","支路电流值103B","4","2","1","3","237",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["135","9.1.114.1","FL_1_BSC_103C","支路电流值103C","4","2","1","3","238",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["136","9.1.114.1","FL_1_BSC_104A","支路电流值104A","4","2","1","3","239",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["137","9.1.114.1","FL_1_BSC_104B","支路电流值104B","4","2","1","3","240",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["138","9.1.114.1","FL_1_BSC_104C","支路电流值104C","4","2","1","3","241",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["139","9.1.114.1","FL_1_BSC_105","支路电流值105","4","2","1","3","242",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["140","9.1.114.1","FL_1_BSC_106","支路电流值106","4","2","1","3","243",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["141","9.1.114.1","FL_1_BSC_107","支路电流值107","4","2","1","3","244",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["142","9.1.114.1","FL_1_BSC_108","支路电流值108","4","2","1","3","245",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["143","9.1.114.1","FL_1_BSC_109","支路电流值109","4","2","1","3","246",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["144","9.1.114.1","FL_1_BSC_110","支路电流值110","4","2","1","3","247",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["145","9.1.114.1","FL_1_BSC_111","支路电流值111","4","2","1","3","248",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["146","9.1.114.1","FL_1_BSC_112","支路电流值112","4","2","1","3","249",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["147","9.1.114.1","FL_1_BSC_113","支路电流值113","4","2","1","3","250",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["148","9.1.114.1","FL_1_BSC_114","支路电流值114","4","2","1","3","251",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["150","9.1.114.1","FL_1_BSC_201","支路电流值201","4","2","1","3","280",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["151","9.1.114.1","FL_1_BSC_202","支路电流值202","4","2","1","3","281",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["152","9.1.114.1","FL_1_BSC_203","支路电流值203","4","2","1","3","282",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["153","9.1.114.1","FL_1_BSC_204","支路电流值204","4","2","1","3","283",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["154","9.1.114.1","FL_1_BSC_205","支路电流值205","4","2","1","3","284",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["155","9.1.114.1","FL_1_BSC_206","支路电流值206","4","2","1","3","285",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["156","9.1.114.1","FL_1_BSC_207","支路电流值207","4","2","1","3","286",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["157","9.1.114.1","FL_1_BSC_208","支路电流值208","4","2","1","3","287",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["158","9.1.114.1","FL_1_BSC_209","支路电流值209","4","2","1","3","288",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["159","9.1.114.1","FL_1_BSC_210","支路电流值210","4","2","1","3","289",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["160","9.1.114.1","FL_1_BSC_211","支路电流值211","4","2","1","3","290",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["161","9.1.114.1","FL_1_BSC_212","支路电流值212","4","2","1","3","291",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["162","9.1.114.1","FL_1_BSC_213","支路电流值213","4","2","1","3","292",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["163","9.1.114.1","FL_1_BSC_214","支路电流值214","4","2","1","3","293",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["164","9.1.114.1","FL_1_BSC_215","支路电流值215","4","2","1","3","294",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["165","9.1.114.1","FL_1_BSC_216","支路电流值216","4","2","1","3","295",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["166","9.1.114.1","FL_1_BSC_217","支路电流值217","4","2","1","3","296",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["167","9.1.114.1","FL_1_BSC_218","支路电流值218","4","2","1","3","297",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["168","9.1.114.1","FL_1_BSC_219","支路电流值219","4","2","1","3","298",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["169","9.1.114.1","FL_1_BSC_220","支路电流值220","4","2","1","3","299",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["170","9.1.114.1","FL_1_BSC_221","支路电流值221","4","2","1","3","300",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["171","9.1.114.1","FL_1_BSC_222","支路电流值222","4","2","1","3","301",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["172","9.1.114.1","FL_1_BSC_223","支路电流值223","4","2","1","3","302",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["173","9.1.114.1","FL_1_BSC_224","支路电流值224","4","2","1","3","303",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["175","9.1.114.1","FL_1_BSC_301","支路电流值301","4","2","1","3","320",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["176","9.1.114.1","FL_1_BSC_302","支路电流值302","4","2","1","3","321",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["177","9.1.114.1","FL_1_BSC_303","支路电流值303","4","2","1","3","322",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["178","9.1.114.1","FL_1_BSC_304","支路电流值304","4","2","1","3","323",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["179","9.1.114.1","FL_1_BSC_305","支路电流值305","4","2","1","3","324",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["180","9.1.114.1","FL_1_BSC_306","支路电流值306","4","2","1","3","325",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["181","9.1.114.1","FL_1_BSC_307","支路电流值307","4","2","1","3","326",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["182","9.1.114.1","FL_1_BSC_308","支路电流值308","4","2","1","3","327",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["183","9.1.114.1","FL_1_BSC_309","支路电流值309","4","2","1","3","328",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["184","9.1.114.1","FL_1_BSC_310","支路电流值310","4","2","1","3","329",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["185","9.1.114.1","FL_1_BSC_311","支路电流值311","4","2","1","3","330",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["186","9.1.114.1","FL_1_BSC_312","支路电流值312","4","2","1","3","331",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["187","9.1.114.1","FL_1_BSC_313","支路电流值313","4","2","1","3","332",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["188","9.1.114.1","FL_1_BSC_314","支路电流值314","4","2","1","3","333",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["189","9.1.114.1","FL_1_BSC_315","支路电流值315","4","2","1","3","334",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["190","9.1.114.1","FL_1_BSC_316","支路电流值316","4","2","1","3","335",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["191","9.1.114.1","FL_1_BSC_317","支路电流值317","4","2","1","3","336",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["192","9.1.114.1","FL_1_BSC_318","支路电流值318","4","2","1","3","337",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["193","9.1.114.1","FL_1_BSC_319","支路电流值319","4","2","1","3","338",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["194","9.1.114.1","FL_1_BSC_320","支路电流值320","4","2","1","3","339",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["195","9.1.114.1","FL_1_BSC_321","支路电流值321","4","2","1","3","340",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSC_322","支路电流值322","4","2","1","3","341",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["197","9.1.114.1","FL_1_BSC_323","支路电流值323","4","2","1","3","342",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["198","9.1.114.1","FL_1_BSC_324","支路电流值324","4","2","1","3","343",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["200","9.1.114.1","FL_1_BSC_401","支路电流值401","4","2","1","3","360",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["201","9.1.114.1","FL_1_BSC_402","支路电流值402","4","2","1","3","361",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["202","9.1.114.1","FL_1_BSC_403","支路电流值403","4","2","1","3","362",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["203","9.1.114.1","FL_1_BSC_404","支路电流值404","4","2","1","3","363",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["204","9.1.114.1","FL_1_BSC_405","支路电流值405","4","2","1","3","364",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["205","9.1.114.1","FL_1_BSC_406","支路电流值406","4","2","1","3","365",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["206","9.1.114.1","FL_1_BSC_407","支路电流值407","4","2","1","3","366",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["207","9.1.114.1","FL_1_BSC_408","支路电流值408","4","2","1","3","367",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["208","9.1.114.1","FL_1_BSC_409","支路电流值409","4","2","1","3","368",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["209","9.1.114.1","FL_1_BSC_410","支路电流值410","4","2","1","3","369",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["210","9.1.114.1","FL_1_BSC_411","支路电流值411","4","2","1","3","370",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["211","9.1.114.1","FL_1_BSC_412","支路电流值412","4","2","1","3","371",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["212","9.1.114.1","FL_1_BSC_413","支路电流值413","4","2","1","3","372",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["213","9.1.114.1","FL_1_BSC_414","支路电流值414","4","2","1","3","373",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["214","9.1.114.1","FL_1_BSC_415","支路电流值415","4","2","1","3","374",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["215","9.1.114.1","FL_1_BSC_416","支路电流值416","4","2","1","3","375",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["216","9.1.114.1","FL_1_BSC_417","支路电流值417","4","2","1","3","376",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["217","9.1.114.1","FL_1_BSC_418","支路电流值418","4","2","1","3","377",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["218","9.1.114.1","FL_1_BSC_419","支路电流值419","4","2","1","3","378",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["219","9.1.114.1","FL_1_BSC_420","支路电流值420","4","2","1","3","379",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["220","9.1.114.1","FL_1_BSC_421","支路电流值421","4","2","1","3","380",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["221","9.1.114.1","FL_1_BSC_422","支路电流值422","4","2","1","3","381",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["222","9.1.114.1","FL_1_BSC_423","支路电流值423","4","2","1","3","382",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["223","9.1.114.1","FL_1_BSC_424","支路电流值424","4","2","1","3","383",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["225","9.1.114.1","FL_1_BSC_501","支路电流值501","4","2","1","3","400",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["226","9.1.114.1","FL_1_BSC_502","支路电流值502","4","2","1","3","401",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["227","9.1.114.1","FL_1_BSC_503","支路电流值503","4","2","1","3","402",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["228","9.1.114.1","FL_1_BSC_504","支路电流值504","4","2","1","3","403",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["1","9.1.114.1","FL_1_Communications","通信状态","1000","0","0","1","0","","","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断开,"]
[]
["196","9.1.114.1","FL_1_BSP_101A","支路功率101A","4","2","1","3","830",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_101B","支路功率101B","4","2","1","3","831",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_101C","支路功率101C","4","2","1","3","832",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_102A","支路功率102A","4","2","1","3","833",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_102B","支路功率102B","4","2","1","3","834",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_102C","支路功率102C","4","2","1","3","835",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_103A","支路功率103A","4","2","1","3","836",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_103B","支路功率103B","4","2","1","3","837",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_103C","支路功率103C","4","2","1","3","838",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_104A","支路功率104A","4","2","1","3","839",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_104B","支路功率104B","4","2","1","3","840",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_104C","支路功率104C","4","2","1","3","841",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_105","支路功率105","4","2","1","3","842",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_106","支路功率106","4","2","1","3","843",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_107","支路功率107","4","2","1","3","844",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_108","支路功率108","4","2","1","3","845",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_109","支路功率109","4","2","1","3","846",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_110","支路功率110","4","2","1","3","847",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_111","支路功率111","4","2","1","3","848",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_112","支路功率112","4","2","1","3","849",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_113","支路功率113","4","2","1","3","850",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_114","支路功率114","4","2","1","3","851",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_201","支路功率201","4","2","1","3","880",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_202","支路功率202","4","2","1","3","881",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_203","支路功率203","4","2","1","3","882",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_204","支路功率204","4","2","1","3","883",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_205","支路功率205","4","2","1","3","884",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_206","支路功率206","4","2","1","3","885",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_207","支路功率207","4","2","1","3","886",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_208","支路功率208","4","2","1","3","887",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_209","支路功率209","4","2","1","3","888",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_210","支路功率210","4","2","1","3","889",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_211","支路功率211","4","2","1","3","890",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_212","支路功率212","4","2","1","3","891",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_213","支路功率213","4","2","1","3","892",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_214","支路功率214","4","2","1","3","893",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_215","支路功率215","4","2","1","3","894",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_216","支路功率216","4","2","1","3","895",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_217","支路功率217","4","2","1","3","896",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_218","支路功率218","4","2","1","3","897",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_219","支路功率219","4","2","1","3","898",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_220","支路功率220","4","2","1","3","899",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_221","支路功率221","4","2","1","3","900",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_222","支路功率222","4","2","1","3","901",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_223","支路功率223","4","2","1","3","902",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_224","支路功率224","4","2","1","3","903",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_301","支路功率301","4","2","1","3","930",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_302","支路功率302","4","2","1","3","931",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_303","支路功率303","4","2","1","3","932",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_304","支路功率304","4","2","1","3","933",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_305","支路功率305","4","2","1","3","934",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_306","支路功率306","4","2","1","3","935",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_307","支路功率307","4","2","1","3","936",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_308","支路功率308","4","2","1","3","937",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_309","支路功率309","4","2","1","3","938",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_310","支路功率310","4","2","1","3","939",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_311","支路功率311","4","2","1","3","940",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_312","支路功率312","4","2","1","3","941",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_313","支路功率313","4","2","1","3","942",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_314","支路功率314","4","2","1","3","943",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_315","支路功率315","4","2","1","3","944",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_316","支路功率316","4","2","1","3","945",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_317","支路功率317","4","2","1","3","946",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_318","支路功率318","4","2","1","3","947",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_319","支路功率319","4","2","1","3","948",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_320","支路功率320","4","2","1","3","949",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_321","支路功率321","4","2","1","3","950",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_322","支路功率322","4","2","1","3","951",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_323","支路功率323","4","2","1","3","952",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_324","支路功率324","4","2","1","3","953",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_401","支路功率401","4","2","1","3","980",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_402","支路功率402","4","2","1","3","981",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_403","支路功率403","4","2","1","3","982",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_404","支路功率404","4","2","1","3","983",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_405","支路功率405","4","2","1","3","984",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_406","支路功率406","4","2","1","3","985",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_407","支路功率407","4","2","1","3","986",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_408","支路功率408","4","2","1","3","987",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_409","支路功率409","4","2","1","3","988",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_410","支路功率410","4","2","1","3","989",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_411","支路功率411","4","2","1","3","990",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_412","支路功率412","4","2","1","3","991",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_413","支路功率413","4","2","1","3","992",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_414","支路功率414","4","2","1","3","993",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_415","支路功率415","4","2","1","3","994",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_416","支路功率416","4","2","1","3","995",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_417","支路功率417","4","2","1","3","996",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_418","支路功率418","4","2","1","3","997",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_419","支路功率419","4","2","1","3","998",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_420","支路功率420","4","2","1","3","999",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_421","支路功率421","4","2","1","3","1000",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_422","支路功率422","4","2","1","3","1001",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_423","支路功率423","4","2","1","3","1002",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_424","支路功率424","4","2","1","3","1003",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_501","支路功率501","4","2","1","3","1030",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_502","支路功率502","4","2","1","3","1031",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_503","支路功率503","4","2","1","3","1032",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_504","支路功率504","4","2","1","3","1033",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_505","支路功率505","4","2","1","3","1034",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]

{"sheet":"CSpreadSheetBackup","index":1,"n_rows":319,"n_cols":76,"rows_kept":319,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","9.1.114.1","FL_1_MainAP_Volt","主回路A相电压","4","2","1","3","0",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","FL_1_MainBP_Volt","主回路B相电压","4","2","1","3","1",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","FL_1_MainCP_Volt","主回路C相电压","4","2","1","3","2",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","9.1.114.1","FL_1_MainABL_Volt","主回路AB线电压","4","2","1","3","3",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","9.1.114.1","FL_1_MainBCL_Volt","主回路BC线电压","4","2","1","3","4",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","9.1.114.1","FL_1_MainCAL_Volt","主回路CA线电压","4","2","1","3","5",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","9.1.114.1","FL_1_MainAP_Curr","主回路A相电流","4","2","1","3","6",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.04","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","9.1.114.1","FL_1_MainBP_Curr","主回路B相电流","4","2","1","3","7",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.04","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","9.1.114.1","FL_1_MainCP_Curr","主回路C相电流","4","2","1","3","8",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.04","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","9.1.114.1","FL_1_MainAP_APower","主回路A相有功","4","2","1","3","14",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","4.0","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","9.1.114.1","FL_1_MainBP_Apower","主回路B相有功","4","2","1","3","15",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","4.0","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","9.1.114.1","FL_1_MainCP_Apower","主回路C相有功","4","2","1","3","16",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","4.0","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","9.1.114.1","FL_1_MainAP_RPower","主回路A相无功","4","2","1","3","17",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","var","300","4.0","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.1","FL_1_MainBP_Rpower","主回路B相无功","4","2","1","3","18",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","var","300","4.0","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","9.1.114.1","FL_1_MainCP_Rpower","主回路C相无功","4","2","1","3","19",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","var","300","4.0","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","9.1.114.1","FL_1_Main_Frequency","主回路频率","4","2","1","3","23",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","9.1.114.1","FL_1_Main_Switch","主回路主开关开关量","4","2","1","3","36",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","9.1.114.1","FL_1_Main_AlarmIndicator","主回路报警指示灯状态","4","2","1","3","37",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","9.1.114.1","FL_1_Main_AlarmBuzzer","主回路报警蜂鸣器状态","4","2","1","3","38",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","9.1.114.1","FL_1_MainAP_THDVolt","主回路A相电压THD","4","2","1","3","39",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","9.1.114.1","FL_1_MainBP_THDVolt","主回路B相电压THD","4","2","1","3","40",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.1","FL_1_MainCP_THDVolt","主回路C相电压THD","4","2","1","3","41",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.1","FL_1_MainAP_THDCurr","主回路A相电流THD","4","2","1","3","42",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.1","FL_1_MainBP_THDCurr","主回路B相电流THD","4","2","1","3","43",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.1","FL_1_MainCP_THDCurr","主回路C相电流THD","4","2","1","3","44",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","9.1.114.1","FL_1_Main_LinearCur","主回路中线性电流","4","2","1","3","45",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.04","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","9.1.114.1","FL_1_Main_AvgCur","主回路平均电流","4","2","1","3","46",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.04","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","9.1.114.1","FL_1_Main_LineAvgVolt","主回路线电压平均值","4","2","1","3","47",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","9.1.114.1","FL_1_Main_PhaseAvgVolt","主回路相电压平均值","4","2","1","3","48",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","9.1.114.1","FL_1_BSV_101","支路开关量101","4","2","1","3","90",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","9.1.114.1","FL_1_BSV_102","支路开关量102","4","2","1","3","91",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","9.1.114.1","FL_1_BSV_103","支路开关量103","4","2","1","3","92",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","9.1.114.1","FL_1_BSV_104","支路开关量104","4","2","1","3","93",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","9.1.114.1","FL_1_BSV_105","支路开关量105","4","2","1","3","94",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["36","9.1.114.1","FL_1_BSV_106","支路开关量106","4","2","1","3","95",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["37","9.1.114.1","FL_1_BSV_107","支路开关量107","4","2","1","3","96",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["38","9.1.114.1","FL_1_BSV_108","支路开关量108","4","2","1","3","97",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["39","9.1.114.1","FL_1_BSV_109","支路开关量109","4","2","1","3","98",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["40","9.1.114.1","FL_1_BSV_110","支路开关量110","4","2","1","3","99",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["41","9.1.114.1","FL_1_BSV_111","支路开关量111","4","2","1","3","100",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["42","9.1.114.1","FL_1_BSV_112","支路开关量112","4","2","1","3","101",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["43","9.1.114.1","FL_1_BSV_113","支路开关量113","4","2","1","3","102",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["44","9.1.114.1","FL_1_BSV_114","支路开关量114","4","2","1","3","103",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["46","9.1.114.1","FL_1_BSV_201","支路开关量201","4","2","1","3","130",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["47","9.1.114.1","FL_1_BSV_202","支路开关量202","4","2","1","3","131",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["48","9.1.114.1","FL_1_BSV_203","支路开关量203","4","2","1","3","132",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["49","9.1.114.1","FL_1_BSV_204","支路开关量204","4","2","1","3","133",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["50","9.1.114.1","FL_1_BSV_205","支路开关量205","4","2","1","3","134",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["51","9.1.114.1","FL_1_BSV_206","支路开关量206","4","2","1","3","135",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["52","9.1.114.1","FL_1_BSV_207","支路开关量207","4","2","1","3","136",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["53","9.1.114.1","FL_1_BSV_208","支路开关量208","4","2","1","3","137",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["54","9.1.114.1","FL_1_BSV_209","支路开关量209","4","2","1","3","138",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["55","9.1.114.1","FL_1_BSV_210","支路开关量210","4","2","1","3","139",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["56","9.1.114.1","FL_1_BSV_211","支路开关量211","4","2","1","3","140",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["57","9.1.114.1","FL_1_BSV_212","支路开关量212","4","2","1","3","141",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["58","9.1.114.1","FL_1_BSV_213","支路开关量213","4","2","1","3","142",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["59","9.1.114.1","FL_1_BSV_214","支路开关量214","4","2","1","3","143",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["60","9.1.114.1","FL_1_BSV_215","支路开关量215","4","2","1","3","144",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["61","9.1.114.1","FL_1_BSV_216","支路开关量216","4","2","1","3","145",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["62","9.1.114.1","FL_1_BSV_217","支路开关量217","4","2","1","3","146",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["63","9.1.114.1","FL_1_BSV_218","支路开关量218","4","2","1","3","147",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["64","9.1.114.1","FL_1_BSV_219","支路开关量219","4","2","1","3","148",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["65","9.1.114.1","FL_1_BSV_220","支路开关量220","4","2","1","3","149",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["66","9.1.114.1","FL_1_BSV_221","支路开关量221","4","2","1","3","150",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["67","9.1.114.1","FL_1_BSV_222","支路开关量222","4","2","1","3","151",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["68","9.1.114.1","FL_1_BSV_223","支路开关量223","4","2","1","3","152",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["69","9.1.114.1","FL_1_BSV_224","支路开关量224","4","2","1","3","153",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["71","9.1.114.1","FL_1_BSV_301","支路开关量301","4","2","1","3","160",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["72","9.1.114.1","FL_1_BSV_302","支路开关量302","4","2","1","3","161",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["73","9.1.114.1","FL_1_BSV_303","支路开关量303","4","2","1","3","162",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["74","9.1.114.1","FL_1_BSV_304","支路开关量304","4","2","1","3","163",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["75","9.1.114.1","FL_1_BSV_305","支路开关量305","4","2","1","3","164",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["76","9.1.114.1","FL_1_BSV_306","支路开关量306","4","2","1","3","165",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["77","9.1.114.1","FL_1_BSV_307","支路开关量307","4","2","1","3","166",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["78","9.1.114.1","FL_1_BSV_308","支路开关量308","4","2","1","3","167",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["79","9.1.114.1","FL_1_BSV_309","支路开关量309","4","2","1","3","168",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["80","9.1.114.1","FL_1_BSV_310","支路开关量310","4","2","1","3","169",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["81","9.1.114.1","FL_1_BSV_311","支路开关量311","4","2","1","3","170",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["82","9.1.114.1","FL_1_BSV_312","支路开关量312","4","2","1","3","171",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["83","9.1.114.1","FL_1_BSV_313","支路开关量313","4","2","1","3","172",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["84","9.1.114.1","FL_1_BSV_314","支路开关量314","4","2","1","3","173",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["85","9.1.114.1","FL_1_BSV_315","支路开关量315","4","2","1","3","174",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["86","9.1.114.1","FL_1_BSV_316","支路开关量316","4","2","1","3","175",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["87","9.1.114.1","FL_1_BSV_317","支路开关量317","4","2","1","3","176",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["88","9.1.114.1","FL_1_BSV_318","支路开关量318","4","2","1","3","177",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["89","9.1.114.1","FL_1_BSV_319","支路开关量319","4","2","1","3","178",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["90","9.1.114.1","FL_1_BSV_320","支路开关量320","4","2","1","3","179",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["91","9.1.114.1","FL_1_BSV_321","支路开关量321","4","2","1","3","180",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["92","9.1.114.1","FL_1_BSV_322","支路开关量322","4","2","1","3","181",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["93","9.1.114.1","FL_1_BSV_323","支路开关量323","4","2","1","3","182",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["94","9.1.114.1","FL_1_BSV_324","支路开关量324","4","2","1","3","183",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["96","9.1.114.1","FL_1_BSV_401","支路开关量401","4","2","1","3","190",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["97","9.1.114.1","FL_1_BSV_402","支路开关量402","4","2","1","3","191",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["98","9.1.114.1","FL_1_BSV_403","支路开关量403","4","2","1","3","192",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["99","9.1.114.1","FL_1_BSV_404","支路开关量404","4","2","1","3","193",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["100","9.1.114.1","FL_1_BSV_405","支路开关量405","4","2","1","3","194",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["101","9.1.114.1","FL_1_BSV_406","支路开关量406","4","2","1","3","195",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["102","9.1.114.1","FL_1_BSV_407","支路开关量407","4","2","1","3","196",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["103","9.1.114.1","FL_1_BSV_408","支路开关量408","4","2","1","3","197",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["104","9.1.114.1","FL_1_BSV_409","支路开关量409","4","2","1","3","198",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["105","9.1.114.1","FL_1_BSV_410","支路开关量410","4","2","1","3","199",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["106","9.1.114.1","FL_1_BSV_411","支路开关量411","4","2","1","3","200",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["107","9.1.114.1","FL_1_BSV_412","支路开关量412","4","2","1","3","201",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["108","9.1.114.1","FL_1_BSV_413","支路开关量413","4","2","1","3","202",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["109","9.1.114.1","FL_1_BSV_414","支路开关量414","4","2","1","3","203",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["110","9.1.114.1","FL_1_BSV_415","支路开关量415","4","2","1","3","204",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["111","9.1.114.1","FL_1_BSV_416","支路开关量416","4","2","1","3","205",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["112","9.1.114.1","FL_1_BSV_417","支路开关量417","4","2","1","3","206",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["113","9.1.114.1","FL_1_BSV_418","支路开关量418","4","2","1","3","207",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["114","9.1.114.1","FL_1_BSV_419","支路开关量419","4","2","1","3","208",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["115","9.1.114.1","FL_1_BSV_420","支路开关量420","4","2","1","3","209",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["116","9.1.114.1","FL_1_BSV_421","支路开关量421","4","2","1","3","210",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["117","9.1.114.1","FL_1_BSV_422","支路开关量422","4","2","1","3","211",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["118","9.1.114.1","FL_1_BSV_423","支路开关量423","4","2","1","3","212",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["119","9.1.114.1","FL_1_BSV_424","支路开关量424","4","2","1","3","213",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["121","9.1.114.1","FL_1_BSV_501","支路开关量501","4","2","1","3","220",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["122","9.1.114.1","FL_1_BSV_502","支路开关量502","4","2","1","3","221",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["123","9.1.114.1","FL_1_BSV_503","支路开关量503","4","2","1","3","222",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["124","9.1.114.1","FL_1_BSV_504","支路开关量504","4","2","1","3","223",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["125","9.1.114.1","FL_1_LigProdeStates","防雷器状态","4","2","1","3","224",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["127","9.1.114.1","FL_1_BSC_101A","支路电流值101A","4","2","1","3","230",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["128","9.1.114.1","FL_1_BSC_101B","支路电流值101B","4","2","1","3","231",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["129","9.1.114.1","FL_1_BSC_101C","支路电流值101C","4","2","1","3","232",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["130","9.1.114.1","FL_1_BSC_102A","支路电流值102A","4","2","1","3","233",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["131","9.1.114.1","FL_1_BSC_102B","支路电流值102B","4","2","1","3","234",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["132","9.1.114.1","FL_1_BSC_102C","支路电流值102C","4","2","1","3","235",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["133","9.1.114.1","FL_1_BSC_103A","支路电流值103A","4","2","1","3","236",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["134","9.1.114.1","FL_1_BSC_103B","支路电流值103B","4","2","1","3","237",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["135","9.1.114.1","FL_1_BSC_103C","支路电流值103C","4","2","1","3","238",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["136","9.1.114.1","FL_1_BSC_104A","支路电流值104A","4","2","1","3","239",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["137","9.1.114.1","FL_1_BSC_104B","支路电流值104B","4","2","1","3","240",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["138","9.1.114.1","FL_1_BSC_104C","支路电流值104C","4","2","1","3","241",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["139","9.1.114.1","FL_1_BSC_105","支路电流值105","4","2","1","3","242",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["140","9.1.114.1","FL_1_BSC_106","支路电流值106","4","2","1","3","243",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["141","9.1.114.1","FL_1_BSC_107","支路电流值107","4","2","1","3","244",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["142","9.1.114.1","FL_1_BSC_108","支路电流值108","4","2","1","3","245",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["143","9.1.114.1","FL_1_BSC_109","支路电流值109","4","2","1","3","246",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["144","9.1.114.1","FL_1_BSC_110","支路电流值110","4","2","1","3","247",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["145","9.1.114.1","FL_1_BSC_111","支路电流值111","4","2","1","3","248",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["146","9.1.114.1","FL_1_BSC_112","支路电流值112","4","2","1","3","249",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["147","9.1.114.1","FL_1_BSC_113","支路电流值113","4","2","1","3","250",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["148","9.1.114.1","FL_1_BSC_114","支路电流值114","4","2","1","3","251",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["150","9.1.114.1","FL_1_BSC_201","支路电流值201","4","2","1","3","280",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["151","9.1.114.1","FL_1_BSC_202","支路电流值202","4","2","1","3","281",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["152","9.1.114.1","FL_1_BSC_203","支路电流值203","4","2","1","3","282",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["153","9.1.114.1","FL_1_BSC_204","支路电流值204","4","2","1","3","283",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["154","9.1.114.1","FL_1_BSC_205","支路电流值205","4","2","1","3","284",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["155","9.1.114.1","FL_1_BSC_206","支路电流值206","4","2","1","3","285",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["156","9.1.114.1","FL_1_BSC_207","支路电流值207","4","2","1","3","286",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["157","9.1.114.1","FL_1_BSC_208","支路电流值208","4","2","1","3","287",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["158","9.1.114.1","FL_1_BSC_209","支路电流值209","4","2","1","3","288",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["159","9.1.114.1","FL_1_BSC_210","支路电流值210","4","2","1","3","289",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["160","9.1.114.1","FL_1_BSC_211","支路电流值211","4","2","1","3","290",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["161","9.1.114.1","FL_1_BSC_212","支路电流值212","4","2","1","3","291",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["162","9.1.114.1","FL_1_BSC_213","支路电流值213","4","2","1","3","292",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["163","9.1.114.1","FL_1_BSC_214","支路电流值214","4","2","1","3","293",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["164","9.1.114.1","FL_1_BSC_215","支路电流值215","4","2","1","3","294",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["165","9.1.114.1","FL_1_BSC_216","支路电流值216","4","2","1","3","295",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["166","9.1.114.1","FL_1_BSC_217","支路电流值217","4","2","1","3","296",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["167","9.1.114.1","FL_1_BSC_218","支路电流值218","4","2","1","3","297",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["168","9.1.114.1","FL_1_BSC_219","支路电流值219","4","2","1","3","298",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["169","9.1.114.1","FL_1_BSC_220","支路电流值220","4","2","1","3","299",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["170","9.1.114.1","FL_1_BSC_221","支路电流值221","4","2","1","3","300",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["171","9.1.114.1","FL_1_BSC_222","支路电流值222","4","2","1","3","301",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["172","9.1.114.1","FL_1_BSC_223","支路电流值223","4","2","1","3","302",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["173","9.1.114.1","FL_1_BSC_224","支路电流值224","4","2","1","3","303",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["175","9.1.114.1","FL_1_BSC_301","支路电流值301","4","2","1","3","320",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["176","9.1.114.1","FL_1_BSC_302","支路电流值302","4","2","1","3","321",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["177","9.1.114.1","FL_1_BSC_303","支路电流值303","4","2","1","3","322",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["178","9.1.114.1","FL_1_BSC_304","支路电流值304","4","2","1","3","323",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["179","9.1.114.1","FL_1_BSC_305","支路电流值305","4","2","1","3","324",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["180","9.1.114.1","FL_1_BSC_306","支路电流值306","4","2","1","3","325",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["181","9.1.114.1","FL_1_BSC_307","支路电流值307","4","2","1","3","326",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["182","9.1.114.1","FL_1_BSC_308","支路电流值308","4","2","1","3","327",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["183","9.1.114.1","FL_1_BSC_309","支路电流值309","4","2","1","3","328",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["184","9.1.114.1","FL_1_BSC_310","支路电流值310","4","2","1","3","329",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["185","9.1.114.1","FL_1_BSC_311","支路电流值311","4","2","1","3","330",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["186","9.1.114.1","FL_1_BSC_312","支路电流值312","4","2","1","3","331",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["187","9.1.114.1","FL_1_BSC_313","支路电流值313","4","2","1","3","332",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["188","9.1.114.1","FL_1_BSC_314","支路电流值314","4","2","1","3","333",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["189","9.1.114.1","FL_1_BSC_315","支路电流值315","4","2","1","3","334",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["190","9.1.114.1","FL_1_BSC_316","支路电流值316","4","2","1","3","335",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["191","9.1.114.1","FL_1_BSC_317","支路电流值317","4","2","1","3","336",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["192","9.1.114.1","FL_1_BSC_318","支路电流值318","4","2","1","3","337",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["193","9.1.114.1","FL_1_BSC_319","支路电流值319","4","2","1","3","338",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["194","9.1.114.1","FL_1_BSC_320","支路电流值320","4","2","1","3","339",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["195","9.1.114.1","FL_1_BSC_321","支路电流值321","4","2","1","3","340",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSC_322","支路电流值322","4","2","1","3","341",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["197","9.1.114.1","FL_1_BSC_323","支路电流值323","4","2","1","3","342",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["198","9.1.114.1","FL_1_BSC_324","支路电流值324","4","2","1","3","343",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["200","9.1.114.1","FL_1_BSC_401","支路电流值401","4","2","1","3","360",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["201","9.1.114.1","FL_1_BSC_402","支路电流值402","4","2","1","3","361",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["202","9.1.114.1","FL_1_BSC_403","支路电流值403","4","2","1","3","362",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["203","9.1.114.1","FL_1_BSC_404","支路电流值404","4","2","1","3","363",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["204","9.1.114.1","FL_1_BSC_405","支路电流值405","4","2","1","3","364",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["205","9.1.114.1","FL_1_BSC_406","支路电流值406","4","2","1","3","365",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["206","9.1.114.1","FL_1_BSC_407","支路电流值407","4","2","1","3","366",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["207","9.1.114.1","FL_1_BSC_408","支路电流值408","4","2","1","3","367",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["208","9.1.114.1","FL_1_BSC_409","支路电流值409","4","2","1","3","368",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["209","9.1.114.1","FL_1_BSC_410","支路电流值410","4","2","1","3","369",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["210","9.1.114.1","FL_1_BSC_411","支路电流值411","4","2","1","3","370",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["211","9.1.114.1","FL_1_BSC_412","支路电流值412","4","2","1","3","371",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["212","9.1.114.1","FL_1_BSC_413","支路电流值413","4","2","1","3","372",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["213","9.1.114.1","FL_1_BSC_414","支路电流值414","4","2","1","3","373",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["214","9.1.114.1","FL_1_BSC_415","支路电流值415","4","2","1","3","374",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["215","9.1.114.1","FL_1_BSC_416","支路电流值416","4","2","1","3","375",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["216","9.1.114.1","FL_1_BSC_417","支路电流值417","4","2","1","3","376",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["217","9.1.114.1","FL_1_BSC_418","支路电流值418","4","2","1","3","377",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["218","9.1.114.1","FL_1_BSC_419","支路电流值419","4","2","1","3","378",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["219","9.1.114.1","FL_1_BSC_420","支路电流值420","4","2","1","3","379",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["220","9.1.114.1","FL_1_BSC_421","支路电流值421","4","2","1","3","380",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["221","9.1.114.1","FL_1_BSC_422","支路电流值422","4","2","1","3","381",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["222","9.1.114.1","FL_1_BSC_423","支路电流值423","4","2","1","3","382",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["223","9.1.114.1","FL_1_BSC_424","支路电流值424","4","2","1","3","383",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["225","9.1.114.1","FL_1_BSC_501","支路电流值501","4","2","1","3","400",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["226","9.1.114.1","FL_1_BSC_502","支路电流值502","4","2","1","3","401",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["227","9.1.114.1","FL_1_BSC_503","支路电流值503","4","2","1","3","402",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["228","9.1.114.1","FL_1_BSC_504","支路电流值504","4","2","1","3","403",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["1","9.1.114.1","FL_1_Communications","通信状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断开,"]
["196","9.1.114.1","FL_1_BSP_101A","支路功率101A","4","2","1","3","830",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_101B","支路功率101B","4","2","1","3","831",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_101C","支路功率101C","4","2","1","3","832",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_102A","支路功率102A","4","2","1","3","833",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_102B","支路功率102B","4","2","1","3","834",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_102C","支路功率102C","4","2","1","3","835",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_103A","支路功率103A","4","2","1","3","836",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_103B","支路功率103B","4","2","1","3","837",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_103C","支路功率103C","4","2","1","3","838",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_104A","支路功率104A","4","2","1","3","839",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_104B","支路功率104B","4","2","1","3","840",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_104C","支路功率104C","4","2","1","3","841",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_105","支路功率105","4","2","1","3","842",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_106","支路功率106","4","2","1","3","843",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_107","支路功率107","4","2","1","3","844",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_108","支路功率108","4","2","1","3","845",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_109","支路功率109","4","2","1","3","846",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_110","支路功率110","4","2","1","3","847",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_111","支路功率111","4","2","1","3","848",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_112","支路功率112","4","2","1","3","849",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_113","支路功率113","4","2","1","3","850",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_114","支路功率114","4","2","1","3","851",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_201","支路功率201","4","2","1","3","880",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_202","支路功率202","4","2","1","3","881",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_203","支路功率203","4","2","1","3","882",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_204","支路功率204","4","2","1","3","883",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_205","支路功率205","4","2","1","3","884",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_206","支路功率206","4","2","1","3","885",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_207","支路功率207","4","2","1","3","886",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_208","支路功率208","4","2","1","3","887",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_209","支路功率209","4","2","1","3","888",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_210","支路功率210","4","2","1","3","889",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_211","支路功率211","4","2","1","3","890",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_212","支路功率212","4","2","1","3","891",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_213","支路功率213","4","2","1","3","892",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_214","支路功率214","4","2","1","3","893",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_215","支路功率215","4","2","1","3","894",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_216","支路功率216","4","2","1","3","895",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_217","支路功率217","4","2","1","3","896",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_218","支路功率218","4","2","1","3","897",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_219","支路功率219","4","2","1","3","898",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_220","支路功率220","4","2","1","3","899",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_221","支路功率221","4","2","1","3","900",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_222","支路功率222","4","2","1","3","901",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_223","支路功率223","4","2","1","3","902",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_224","支路功率224","4","2","1","3","903",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_301","支路功率301","4","2","1","3","930",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_302","支路功率302","4","2","1","3","931",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_303","支路功率303","4","2","1","3","932",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_304","支路功率304","4","2","1","3","933",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_305","支路功率305","4","2","1","3","934",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_306","支路功率306","4","2","1","3","935",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_307","支路功率307","4","2","1","3","936",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_308","支路功率308","4","2","1","3","937",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_309","支路功率309","4","2","1","3","938",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_310","支路功率310","4","2","1","3","939",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_311","支路功率311","4","2","1","3","940",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_312","支路功率312","4","2","1","3","941",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_313","支路功率313","4","2","1","3","942",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_314","支路功率314","4","2","1","3","943",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_315","支路功率315","4","2","1","3","944",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_316","支路功率316","4","2","1","3","945",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_317","支路功率317","4","2","1","3","946",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_318","支路功率318","4","2","1","3","947",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_319","支路功率319","4","2","1","3","948",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_320","支路功率320","4","2","1","3","949",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_321","支路功率321","4","2","1","3","950",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_322","支路功率322","4","2","1","3","951",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_323","支路功率323","4","2","1","3","952",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_324","支路功率324","4","2","1","3","953",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_401","支路功率401","4","2","1","3","980",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_402","支路功率402","4","2","1","3","981",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_403","支路功率403","4","2","1","3","982",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_404","支路功率404","4","2","1","3","983",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_405","支路功率405","4","2","1","3","984",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_406","支路功率406","4","2","1","3","985",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_407","支路功率407","4","2","1","3","986",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_408","支路功率408","4","2","1","3","987",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_409","支路功率409","4","2","1","3","988",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_410","支路功率410","4","2","1","3","989",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_411","支路功率411","4","2","1","3","990",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_412","支路功率412","4","2","1","3","991",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_413","支路功率413","4","2","1","3","992",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_414","支路功率414","4","2","1","3","993",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_415","支路功率415","4","2","1","3","994",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_416","支路功率416","4","2","1","3","995",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_417","支路功率417","4","2","1","3","996",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_418","支路功率418","4","2","1","3","997",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_419","支路功率419","4","2","1","3","998",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_420","支路功率420","4","2","1","3","999",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_421","支路功率421","4","2","1","3","1000",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_422","支路功率422","4","2","1","3","1001",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_423","支路功率423","4","2","1","3","1002",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_424","支路功率424","4","2","1","3","1003",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_501","支路功率501","4","2","1","3","1030",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_502","支路功率502","4","2","1","3","1031",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_503","支路功率503","4","2","1","3","1032",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_504","支路功率504","4","2","1","3","1033",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["196","9.1.114.1","FL_1_BSP_505","支路功率505","4","2","1","3","1034",null,null,"0","60","720","0",null,null,"0","0","0","0","0","0","0","0","0","w","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]