{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":25,"n_cols":76,"rows_kept":25,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["35","5.32.131.1","TH485_Temp1","主机房温度1","10004","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","15","30","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"15","0","100","0","0","0","0","0","0","0","1","1","1","0","0","0","0","0","0","0","0","0","0"]
["36","5.32.131.1","TH485_Humidity1","主机房湿度1","10005","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","20","85","0","0","0","%","300","0.1000000015","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"20","0","100","0","0","0","0","0","0","0","1","1","1","0","0","0","0","0","0","0","0","0","0"]
["37","5.32.131.2","TH485_Temp2","主机房温度2","10004","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","15","30","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"15","0","100","0","0","0","0","0","0","0","1","1","1","0","0","0","0","0","0","0","0","0","0"]
["38","5.32.131.2","TH485_Humidity2","主机房湿度2","10005","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","20","85","0","0","0","%","300","0.1000000015","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"20","0","100","0","0","0","0","0","0","0","1","1","1","0","0","0","0","0","0","0","0","0","0"]
["39","5.32.131.3","TH485_Temp3","主机房温度3","10004","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","15","30","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"15","0","100","0","0","0","0","0","0","0","1","1","1","0","0","0","0","0","0","0","0","0","0"]
["40","5.32.131.3","TH485_Humidity3","主机房湿度3","10005","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","20","85","0","0","0","%","300","0.1000000015","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"20","0","100","0","0","0","0","0","0","0","1","1","1","0","0","0","0","0","0","0","0","0","0"]
["41","5.32.131.4","TH485_Temp4","主机房温度4","10004","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","15","30","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"15","0","100","0","0","0","0","0","0","0","1","1","1","0","0","0","0","0","0","0","0","0","0"]
["42","5.32.131.4","TH485_Humidity4","主机房湿度4","10005","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","20","85","0","0","0","%","300","0.1000000015","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"20","0","100","0","0","0","0","0","0","0","1","1","1","0","0","0","0","0","0","0","0","0","0"]
["43","5.32.131.5","TH485_Temp5","主机房温度5","10004","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","15","30","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"15","0","100","0","0","0","0","0","0","0","1","1","1","0","0","0","0","0","0","0","0","0","0"]
["44","5.32.131.5","TH485_Humidity5","主机房湿度5","10005","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","20","85","0","0","0","%","300","0.1000000015","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"20","0","100","0","0","0","0","0","0","0","1","1","1","0","0","0","0","0","0","0","0","0","0"]
["45","5.32.131.6","TH485_Temp6","主机房温度6","10004","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","15","30","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"15","0","100","0","0","0","0","0","0","0","1","1","1","0","0","0","0","0","0","0","0","0","0"]
["46","5.32.131.6","TH485_Humidity6","主机房湿度6","10005","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","20","85","0","0","0","%","300","0.1000000015","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"20","0","100","0","0","0","0","0","0","0","1","1","1","0","0","0","0","0","0","0","0","0","0"]
["47","5.32.131.7","TH485_Temp7","主机房温度7","10004","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","15","30","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"15","0","100","0","0","0","0","0","0","0","1","1","1","0","0","0","0","0","0","0","0","0","0"]
["48","5.32.131.7","TH485_Humidity7","主机房湿度7","10005","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","20","85","0","0","0","%","300","0.1000000015","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"20","0","100","0","0","0","0","0","0","0","1","1","1","0","0","0","0","0","0","0","0","0","0"]
["49","5.32.131.8","TH485_Temp8","主机房温度8","10004","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","15","30","0","0","0","℃","300","0.1000000015","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"15","0","100","0","0","0","0","0","0","0","1","1","1","0","0","0","0","0","0","0","0","0","0"]
["50","5.32.131.8","TH485_Humidity8","主机房湿度8","10005","4","2","4","0",null,null,"0","30","60","1",null,null,"0","0","0","0","20","85","0","0","0","%","300","0.1000000015","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"20","0","100","0","0","0","0","0","0","0","1","1","1","0","0","0","0","0","0","0","0","0","0"]
["1","5.32.131.1","TH485_1Communications","主机房温湿度1通信状态","1000","0","0","1","0","","","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断开,"]
["1","5.32.131.2","TH485_2Communications","主机房温湿度2通信状态","1000","0","0","1","0","","","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断开,"]
["1","5.32.131.3","TH485_3Communications","主机房温湿度3通信状态","1000","0","0","1","0","","","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断开,"]
["1","5.32.131.4","TH485_4Communications","主机房温湿度4通信状态","1000","0","0","1","0","","","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断开,"]
["1","5.32.131.5","TH485_5Communications","主机房温湿度5通信状态","1000","0","0","1","0","","","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断开,"]
["1","5.32.131.6","TH485_6Communications","主机房温湿度6通信状态","1000","0","0","1","0","","","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断开,"]
["1","5.32.131.7","TH485_7Communications","主机房温湿度7通信状态","1000","0","0","1","0","","","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断开,"]
["1","5.32.131.8","TH485_8Communications","主机房温湿度8通信状态","1000","0","0","1","0","","","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","131",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断开,"]