{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["变量dat文件","CSpreadSheetBackup"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":10,"n_cols":76,"rows_kept":10,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","9.1.114.1","YD2010_1_PositivePV","空调用电 电能值","10006","4","2","3","66",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["1","9.1.114.2","YD2010_2_PositivePV","机柜用电 电能值","10006","4","2","3","66",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["1","9.1.114.3","YD2010_3_PositivePV","UPS1用电 电能值","10006","4","2","3","66",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["1","9.1.114.4","YD2010_4_PositivePV","UPS2用电 电能值","10006","4","2","3","66",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
[]
["1","9.1.114.1","YD2010_1_NegativePV","空调用电 负电能值","10006","4","2","3","70",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["1","9.1.114.2","YD2010_2_NegativePV","机柜用电 负电能值","10006","4","2","3","70",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["1","9.1.114.3","YD2010_3_NegativePV","UPS1用电 负电能值","10006","4","2","3","70",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["1","9.1.114.4","YD2010_4_NegativePV","UPS2用电 负电能值","10006","4","2","3","70",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","10000000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]

{"sheet":"CSpreadSheetBackup","index":1,"n_rows":57,"n_cols":76,"rows_kept":57,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","9.1.114.1","YD2010_1_PhaseVoltageUa","机房总用电A相电压","4","2","1","3","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","YD2010_1_LineVoltageUca","机房总用电A线电压","4","2","1","3","2",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","YD2010_1_PhaseCurrentIa","机房总用电A相电流","4","2","1","3","4",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","A","300","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","9.1.114.1","YD2010_1_PhaseActivePowerPa","机房总用电A相有功功率","3","2","1","3","8",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","KW","300","0.0004000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","9.1.114.1","YD2010_1_PhaseVoltageUb","机房总用电B相电压","4","2","1","3","16",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","9.1.114.1","YD2010_1_LineVoltageUab","机房总用电B线电压","4","2","1","3","18",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","9.1.114.1","YD2010_1_PhaseCurrentIb","机房总用电B相电流","4","2","1","3","20",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","A","300","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","9.1.114.1","YD2010_1_PhaseActivePowerPb","机房总用电B相有功功率","3","2","1","3","24",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","KW","300","0.0004000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","9.1.114.1","YD2010_1_PhaseVoltageUc","机房总用电C相电压","4","2","1","3","32",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","9.1.114.1","YD2010_1_LineVoltageUbc","机房总用电C线电压","4","2","1","3","34",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","9.1.114.1","YD2010_1_PhaseCurrentIc","机房总用电C相电流","4","2","1","3","36",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","A","300","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","9.1.114.1","YD2010_1_PhaseActivePowerPc","机房总用电C相有功功率","3","2","1","3","40",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","KW","300","0.0004000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","9.1.114.1","YD2010_1_Frequency","机房总用电频率","4","2","1","3","54",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.1","YD2010_1_Netstatus","机房总用电通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["15","9.1.114.2","YD2010_2_PhaseVoltageUa","机柜用电A相电压","4","2","1","3","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","9.1.114.2","YD2010_2_LineVoltageUca","机柜用电A线电压","4","2","1","3","2",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","9.1.114.2","YD2010_2_PhaseCurrentIa","机柜用电A相电流","4","2","1","3","4",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","A","300","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","9.1.114.2","YD2010_2_PhaseActivePowerPa","机柜用电A相有功功率","3","2","1","3","8",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","KW","300","0.0004000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","9.1.114.2","YD2010_2_PhaseVoltageUb","机柜用电B相电压","4","2","1","3","16",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","9.1.114.2","YD2010_2_LineVoltageUab","机柜用电B线电压","4","2","1","3","18",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","9.1.114.2","YD2010_2_PhaseCurrentIb","机柜用电B相电流","4","2","1","3","20",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","A","300","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.2","YD2010_2_PhaseActivePowerPb","机柜用电B相有功功率","3","2","1","3","24",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","KW","300","0.0004000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.2","YD2010_2_PhaseVoltageUc","机柜用电C相电压","4","2","1","3","32",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.2","YD2010_2_LineVoltageUbc","机柜用电C线电压","4","2","1","3","34",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.2","YD2010_2_PhaseCurrentIc","机柜用电C相电流","4","2","1","3","36",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","A","300","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","9.1.114.2","YD2010_2_PhaseActivePowerPc","机柜用电C相有功功率","3","2","1","3","40",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","KW","300","0.0004000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","9.1.114.2","YD2010_2_Frequency","机柜用电频率","4","2","1","3","54",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","9.1.114.2","YD2010_2_Netstatus","机柜用电通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["29","9.1.114.3","YD2010_3_PhaseVoltageUa","UPS1用电A相电压","4","2","1","3","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","9.1.114.3","YD2010_3_LineVoltageUca","UPS1用电A线电压","4","2","1","3","2",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","9.1.114.3","YD2010_3_PhaseCurrentIa","UPS1用电A相电流","4","2","1","3","4",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","A","300","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","9.1.114.3","YD2010_3_PhaseActivePowerPa","UPS1用电A相有功功率","3","2","1","3","8",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","KW","300","0.0004000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","9.1.114.3","YD2010_3_PhaseVoltageUb","UPS1用电B相电压","4","2","1","3","16",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","9.1.114.3","YD2010_3_LineVoltageUab","UPS1用电B线电压","4","2","1","3","18",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","9.1.114.3","YD2010_3_PhaseCurrentIb","UPS1用电B相电流","4","2","1","3","20",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","A","300","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["36","9.1.114.3","YD2010_3_PhaseActivePowerPb","UPS1用电B相有功功率","3","2","1","3","24",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","KW","300","0.0004000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["37","9.1.114.3","YD2010_3_PhaseVoltageUc","UPS1用电C相电压","4","2","1","3","32",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["38","9.1.114.3","YD2010_3_LineVoltageUbc","UPS1用电C线电压","4","2","1","3","34",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["39","9.1.114.3","YD2010_3_PhaseCurrentIc","UPS1用电C相电流","4","2","1","3","36",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","A","300","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["40","9.1.114.3","YD2010_3_PhaseActivePowerPc","UPS1用电C相有功功率","3","2","1","3","40",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","KW","300","0.0004000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["41","9.1.114.3","YD2010_3_Frequency","UPS1用电频率","4","2","1","3","54",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["42","9.1.114.3","YD2010_3_Netstatus","UPS1用电通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["29","9.1.114.4","YD2010_4_PhaseVoltageUa","UPS2用电A相电压","4","2","1","3","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","9.1.114.4","YD2010_4_LineVoltageUca","UPS2用电A线电压","4","2","1","3","2",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","9.1.114.4","YD2010_4_PhaseCurrentIa","UPS2用电A相电流","4","2","1","3","4",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","A","300","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","9.1.114.4","YD2010_4_PhaseActivePowerPa","UPS2用电A相有功功率","3","2","1","3","8",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","KW","300","0.0004000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","9.1.114.4","YD2010_4_PhaseVoltageUb","UPS2用电B相电压","4","2","1","3","16",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","9.1.114.4","YD2010_4_LineVoltageUab","UPS2用电B线电压","4","2","1","3","18",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","9.1.114.4","YD2010_4_PhaseCurrentIb","UPS2用电B相电流","4","2","1","3","20",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","A","300","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["36","9.1.114.4","YD2010_4_PhaseActivePowerPb","UPS2用电B相有功功率","3","2","1","3","24",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","KW","300","0.0004000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["37","9.1.114.4","YD2010_4_PhaseVoltageUc","UPS2用电C相电压","4","2","1","3","32",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["38","9.1.114.4","YD2010_4_LineVoltageUbc","UPS2用电C线电压","4","2","1","3","34",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["39","9.1.114.4","YD2010_4_PhaseCurrentIc","UPS2用电C相电流","4","2","1","3","36",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","A","300","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["40","9.1.114.4","YD2010_4_PhaseActivePowerPc","UPS2用电C相有功功率","3","2","1","3","40",null,null,"0","60","720","1",null,null,"5","0","300","0","0","0","0","0","0","KW","300","0.0004000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["41","9.1.114.4","YD2010_4_Frequency","UPS2用电频率","4","2","1","3","54",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["42","9.1.114.4","YD2010_4_Netstatus","UPS2用电通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]