{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["变量dat文件","CSpreadSheetBackup"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":45,"n_cols":76,"rows_kept":45,"flags":["formulas_cached_only"]}
["ID","Uid","变量名称","描述","变量类型","长度","寄存器","功能码","寄存地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","9.1.114.1","FDJ_1_1","Alarm relay status","4","2","1","3",48,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","FDJ_1_2","Voltage between phase 1 & 2","4","2","1","3",50,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","FDJ_1_3","Voltage between phase 2 & 3","4","2","1","3",51,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","9.1.114.1","FDJ_1_4","Voltage between phase 3 &1","4","2","1","3",52,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","9.1.114.1","FDJ_1_5","Voltage between Neutral & phase 1","4","2","1","3",53,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","9.1.114.1","FDJ_1_6","Voltage between Neutral & phase 2","4","2","1","3",54,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","9.1.114.1","FDJ_1_7","Voltage between Neutral & phase 3","4","2","1","3",55,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","9.1.114.1","FDJ_1_8","Current in phase 1","4","2","1","3",56,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","mA","300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","9.1.114.1","FDJ_1_9","Current in phase 2","4","2","1","3",57,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","mA","300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","9.1.114.1","FDJ_1_10","Current in phase 3","4","2","1","3",58,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","mA","300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","9.1.114.1","FDJ_1_11","Frequency","4","2","1","3",60,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","9.1.114.1","FDJ_1_12","Number of running hours","4","2","1","3",61,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hours","300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","9.1.114.1","FDJ_1_13","Lub oil pressure","4","2","1","3",62,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Bars","300","0.100000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.1","FDJ_1_14","Water temperature","4","2","1","3",63,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","°C","300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","9.1.114.1","FDJ_1_15","Fuel oil level","4","2","1","3",64,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","9.1.114.1","FDJ_1_16","Lub oil temperature","4","2","1","3",65,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","°C","300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","9.1.114.1","FDJ_1_17","Battery voltage","4","2","1","3",67,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","mV","300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["1","9.1.114.1","FDJ_1_18","Emergency stop","4","2","1","3",195,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10000","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["2","9.1.114.1","FDJ_1_19","Overload or Short circuit","4","2","1","3",195,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10006","114",null,null,"0","6","6",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["3","9.1.114.1","FDJ_1_20","Overspeed","4","2","1","3",195,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10007","114",null,null,"0","7","7",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["4","9.1.114.1","FDJ_1_21","Battery low voltage","4","2","1","3",195,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10008","114",null,null,"0","8","8",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["5","9.1.114.1","FDJ_1_22","Battery high voltage","4","2","1","3",195,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10009","114",null,null,"0","9","9",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["6","9.1.114.1","FDJ_1_23","Alternator low voltage","4","2","1","3",195,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10012","114",null,null,"0","12","12",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["7","9.1.114.1","FDJ_1_24","Alternator high voltage","4","2","1","3",195,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10013","114",null,null,"0","13","13",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["8","9.1.114.1","FDJ_1_25","Module 3 CAN bus fault","4","2","1","3",196,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10000","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["9","9.1.114.1","FDJ_1_26","Module 4 CAN bus fault","4","2","1","3",196,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10001","114",null,null,"0","1","1",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["10","9.1.114.1","FDJ_1_27","Module 5 CAN bus fault","4","2","1","3",196,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10002","114",null,null,"0","2","2",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["11","9.1.114.1","FDJ_1_28","Module 6 CAN bus fault","4","2","1","3",196,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10003","114",null,null,"0","3","3",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["12","9.1.114.1","FDJ_1_29","Emergency breaker open fault","4","2","1","3",196,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10010","114",null,null,"0","10","10",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["13","9.1.114.1","FDJ_1_30","Battery charger fault","4","2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10002","114",null,null,"0","2","2",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["14","9.1.114.1","FDJ_1_31","Cooling fan tripped","4","2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10003","114",null,null,"0","3","3",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["15","9.1.114.1","FDJ_1_32","Fuel tank low level failure","4","2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10007","114",null,null,"0","7","7",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["16","9.1.114.1","FDJ_1_33","Lub oil leakage fault","4","2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10010","114",null,null,"0","10","10",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["17","9.1.114.1","FDJ_1_34","Fuel oil leakage fault","4","2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10011","114",null,null,"0","11","11",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["18","9.1.114.1","FDJ_1_35","Generating set circuit breaker open","4","2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10014","114",null,null,"0","14","14",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["19","9.1.114.1","FDJ_1_36","Overload alarm","4","2","1","3",197,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10015","114",null,null,"0","15","15",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["20","9.1.114.1","FDJ_1_37","Air shutter shutdown","4","2","1","3",198,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10013","114",null,null,"0","13","13",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["21","9.1.114.1","FDJ_1_38","Fuel oil very low level fault","4","2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10005","114",null,null,"0","5","5",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["22","9.1.114.1","FDJ_1_39","Fuel oil very high level fault","4","2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10006","114",null,null,"0","6","6",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["23","9.1.114.1","FDJ_1_40","Cylinder head temperature fault","4","2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10008","114",null,null,"0","8","8",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["24","9.1.114.1","FDJ_1_41","Water temperature fault (calorstat inlet) ","4","2","1","3",199,null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10009","114",null,null,"0","9","9",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
[]
["24","9.1.114.1","FDJ_1_42","Engine speed","4","2","1","3","66",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10009","114",null,null,"0","9","9",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["30","9.1.114.1","FDJ_1_Communications","发电机通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]

{"sheet":"CSpreadSheetBackup","index":1,"n_rows":42,"n_cols":76,"rows_kept":42,"flags":["formulas_cached_only"]}
["ID","Uid","变量名称","描述","变量类型","长度","寄存器","功能码","寄存地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","9.1.114.1","FDJ_1_10","Alarm relay status","4","2","1","3","48.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","FDJ_1_12","Voltage between phase 1 & 2","4","2","1","3","50.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","FDJ_1_13","Voltage between phase 2 & 3","4","2","1","3","51.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","9.1.114.1","FDJ_1_14","Voltage between phase 3 &1","4","2","1","3","52.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","9.1.114.1","FDJ_1_15","Voltage between Neutral & phase 1","4","2","1","3","53.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","9.1.114.1","FDJ_1_16","Voltage between Neutral & phase 2","4","2","1","3","54.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","9.1.114.1","FDJ_1_17","Voltage between Neutral & phase 3","4","2","1","3","55.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.01000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","9.1.114.1","FDJ_1_18","Current in phase 1","4","2","1","3","56.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","mA","300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","9.1.114.1","FDJ_1_19","Current in phase 2","4","2","1","3","57.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","mA","300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","9.1.114.1","FDJ_1_20","Current in phase 3","4","2","1","3","58.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","mA","300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","9.1.114.1","FDJ_1_22","Frequency","4","2","1","3","60.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","9.1.114.1","FDJ_1_23","Number of running hours","4","2","1","3","61.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hours","300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","9.1.114.1","FDJ_1_24","Lub oil pressure","4","2","1","3","62.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Bars","300","0.100000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.1","FDJ_1_25","Water temperature","4","2","1","3","63.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","°C","300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","9.1.114.1","FDJ_1_26","Fuel oil level","4","2","1","3","64.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","9.1.114.1","FDJ_1_27","Lub oil temperature","4","2","1","3","65.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","°C","300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","9.1.114.1","FDJ_1_29","Battery voltage","4","2","1","3","67.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","mV","300","1.000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","9.1.114.1","FDJ_1_82","Emergency stop","4","2","1","3","195.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10000","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["19","9.1.114.1","FDJ_1_88","Overload or Short circuit","4","2","1","3","195.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10006","114",null,null,"0","6","6",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["20","9.1.114.1","FDJ_1_89","Overspeed","4","2","1","3","195.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10007","114",null,null,"0","7","7",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["21","9.1.114.1","FDJ_1_90","Battery low voltage","4","2","1","3","195.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10008","114",null,null,"0","8","8",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["22","9.1.114.1","FDJ_1_91","Battery high voltage","4","2","1","3","195.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10009","114",null,null,"0","9","9",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["23","9.1.114.1","FDJ_1_94","Alternator low voltage","4","2","1","3","195.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10012","114",null,null,"0","12","12",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["24","9.1.114.1","FDJ_1_95","Alternator high voltage","4","2","1","3","195.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10013","114",null,null,"0","13","13",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["25","9.1.114.1","FDJ_1_98","Module 3 CAN bus fault","4","2","1","3","196.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10000","114",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["26","9.1.114.1","FDJ_1_99","Module 4 CAN bus fault","4","2","1","3","196.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10001","114",null,null,"0","1","1",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["27","9.1.114.1","FDJ_1_100","Module 5 CAN bus fault","4","2","1","3","196.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10002","114",null,null,"0","2","2",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["28","9.1.114.1","FDJ_1_101","Module 6 CAN bus fault","4","2","1","3","196.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10003","114",null,null,"0","3","3",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["29","9.1.114.1","FDJ_1_108","Emergency breaker open fault","4","2","1","3","196.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10010","114",null,null,"0","10","10",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["30","9.1.114.1","FDJ_1_116","Battery charger fault","4","2","1","3","197.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10002","114",null,null,"0","2","2",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["31","9.1.114.1","FDJ_1_117","Cooling fan tripped","4","2","1","3","197.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10003","114",null,null,"0","3","3",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["32","9.1.114.1","FDJ_1_121","Fuel tank low level failure","4","2","1","3","197.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10007","114",null,null,"0","7","7",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["33","9.1.114.1","FDJ_1_124","Lub oil leakage fault","4","2","1","3","197.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10010","114",null,null,"0","10","10",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["34","9.1.114.1","FDJ_1_125","Fuel oil leakage fault","4","2","1","3","197.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10011","114",null,null,"0","11","11",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["35","9.1.114.1","FDJ_1_128","Generating set circuit breaker open","4","2","1","3","197.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10014","114",null,null,"0","14","14",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["36","9.1.114.1","FDJ_1_129","Overload alarm","4","2","1","3","197.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10015","114",null,null,"0","15","15",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["37","9.1.114.1","FDJ_1_143","Air shutter shutdown","4","2","1","3","198.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10013","114",null,null,"0","13","13",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["38","9.1.114.1","FDJ_1_151","Fuel oil very low level fault","4","2","1","3","199.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10005","114",null,null,"0","5","5",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["39","9.1.114.1","FDJ_1_152","Fuel oil very high level fault","4","2","1","3","199.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10006","114",null,null,"0","6","6",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["40","9.1.114.1","FDJ_1_154","Cylinder head temperature fault","4","2","1","3","199.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10008","114",null,null,"0","8","8",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["41","9.1.114.1","FDJ_1_155","Water temperature fault (calorstat inlet)","4","2","1","3","199.0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000","3","0","1","1","0","0","0","10009","114",null,null,"0","9","9",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]