{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":50,"n_cols":76,"rows_kept":50,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","5.4.63.1","STU1_Ai1","STU1_temp_ai1","4","2","1","3","1","cmd-0","type-0","0","30","60","1",null,null,"20","4","66","0","10","30","0","0","0","℃","900","1.0000000000","3","0","0","0","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","5.4.63.1","STU1_Ai2","STU1_Humi_ai2","4","2","1","3","2","cmd-0","type-0","0","30","60","1",null,null,"20","4","114","2","25","85","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","5.4.63.1","STU1_Ai3","STU1_temp_ai3","4","2","1","3","3","cmd-0","type-0","0","30","60","1",null,null,"20","4","66","0","10","30","0","0","0","℃","900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","5.4.63.1","STU1_Ai4","STU1_Humi_ai4","4","2","1","3","4","cmd-0","type-0","0","30","60","1",null,null,"20","4","114","2","25","85","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","5.4.63.1","STU1_Ai5","STU1_temp_ai5","4","2","1","3","5","cmd-0","type-0","0","30","60","1",null,null,"20","4","66","0","10","30","0","0","0","℃","900","1.0000000000","3","0","0","0","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","5.4.63.1","STU1_Ai6","STU1_Humi_ai6","4","2","1","3","6","cmd-0","type-0","0","30","60","1",null,null,"20","4","114","2","25","85","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","5.4.63.1","STU1_Ai7","STU1_temp_ai7","4","2","1","3","7","cmd-0","type-0","0","30","60","1",null,null,"20","4","66","0","10","30","0","0","0","℃","900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","5.4.63.1","STU1_Ai8","STU1_Humi_ai8","4","2","1","3","8","cmd-0","type-0","0","30","60","1",null,null,"20","4","114","2","25","85","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","5.4.63.1","STU1_Di1","STU1_di1","4","2","1","3","9","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","报警,"]
["10","5.4.63.1","STU1_Di2","STU1_di2","4","2","1","3","10","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","报警,"]
["11","5.4.63.1","STU1_Di3","STU1_di3","4","2","1","3","11","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","报警,"]
["12","5.4.63.1","STU1_Di4","STU1_di4","4","2","1","3","12","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","报警,"]
["13","5.4.63.1","STU1_Di5","STU1_di5","4","2","1","3","13","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","报警,"]
["14","5.4.63.1","STU1_Di6","STU1_di6","4","2","1","3","14","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","报警,"]
["15","5.4.63.1","STU1_Di7","STU1_di7","4","2","1","3","15","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","报警,"]
["16","5.4.63.1","STU1_Di8","STU1_di8","4","2","1","3","16","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","报警,"]
["17","5.4.63.1","STU1_Do1","STU1_do1","4","2","1","3","17","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","0","0","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","5.4.63.1","STU1_Do2","STU1_do2","4","2","1","3","18","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","0","0","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","5.4.63.1","STU1_Do3","STU1_do3","4","2","1","3","19","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","0","0","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","5.4.63.1","STU1_Do4","STU1_do4","4","2","1","3","20","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","0","0","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","5.4.63.1","STU1_Do5","STU1_do5","4","2","1","3","21","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","0","0","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","5.4.63.1","STU1_Do6","STU1_do6","4","2","1","3","22","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","0","0","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","5.4.63.1","STU1_DO1_Set","三号五楼灯光控制","4","2","1","16","22","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","1","0","0","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["1","5.4.63.1","STU2_Communications","STU1通信状态","1000","0","0","1","0","","","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断开,"]
[]
["1","5.4.63.2","STU2_Ai1","STU2_temp_ai1","4","2","1","3","1","cmd-0","type-0","0","30","60","1",null,null,"20","4","66","0","10","30","0","0","0","℃","900","1.0000000000","3","0","0","0","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","5.4.63.2","STU2_Ai2","STU2_Humi_ai2","4","2","1","3","2","cmd-0","type-0","0","30","60","1",null,null,"20","4","114","2","25","85","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","5.4.63.2","STU2_Ai3","STU2_temp_ai3","4","2","1","3","3","cmd-0","type-0","0","30","60","1",null,null,"20","4","66","0","10","30","0","0","0","℃","900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","5.4.63.2","STU2_Ai4","STU2_Humi_ai4","4","2","1","3","4","cmd-0","type-0","0","30","60","1",null,null,"20","4","114","2","25","85","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","5.4.63.2","STU2_Ai5","STU2_temp_ai5","4","2","1","3","5","cmd-0","type-0","0","30","60","1",null,null,"20","4","66","0","10","30","0","0","0","℃","900","1.0000000000","3","0","0","0","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","5.4.63.2","STU2_Ai6","STU2_Humi_ai6","4","2","1","3","6","cmd-0","type-0","0","30","60","1",null,null,"20","4","114","2","25","85","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","5.4.63.2","STU2_Ai7","STU2_temp_ai7","4","2","1","3","7","cmd-0","type-0","0","30","60","1",null,null,"20","4","66","0","10","30","0","0","0","℃","900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","5.4.63.2","STU2_Ai8","STU2_Humi_ai8","4","2","1","3","8","cmd-0","type-0","0","30","60","1",null,null,"20","4","114","2","25","85","0","0","0","%","900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","5.4.63.2","STU2_Di1","STU2_di1","4","2","1","3","9","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","报警,"]
["10","5.4.63.2","STU2_Di2","STU2_di2","4","2","1","3","10","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","报警,"]
["11","5.4.63.2","STU2_Di3","STU2_di3","4","2","1","3","11","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","报警,"]
["12","5.4.63.2","STU2_Di4","STU2_di4","4","2","1","3","12","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","报警,"]
["13","5.4.63.2","STU2_Di5","STU2_di5","4","2","1","3","13","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","报警,"]
["14","5.4.63.2","STU2_Di6","STU2_di6","4","2","1","3","14","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","报警,"]
["15","5.4.63.2","STU2_Di7","STU2_di7","4","2","1","3","15","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","报警,"]
["16","5.4.63.2","STU2_Di8","STU2_di8","4","2","1","3","16","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","报警,"]
["17","5.4.63.2","STU2_Do1","STU2_do1","4","2","1","3","17","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","0","0","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","5.4.63.2","STU2_Do2","STU2_do2","4","2","1","3","18","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","0","0","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","5.4.63.2","STU2_Do3","STU2_do3","4","2","1","3","19","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","0","0","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","5.4.63.2","STU2_Do4","STU2_do4","4","2","1","3","20","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","0","0","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","5.4.63.2","STU2_Do5","STU2_do5","4","2","1","3","21","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","0","0","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","5.4.63.2","STU2_Do6","STU2_do6","4","2","1","3","22","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","0","0","0","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","5.4.63.2","STU2_DO1_Set","三号五楼灯光控制","4","2","1","16","22","cmd-10","type-0","0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"900","1.0000000000","3","1","0","0","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["1","5.4.63.2","STU2_Communications","STU2通信状态","1000","0","0","1","0","","","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","63",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断开,"]