{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["变量dat文件","CSpreadSheetBackup"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":52,"n_cols":76,"rows_kept":52,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","9.1.114.1","TEPW1_A_Phase","六号一楼电量仪A相电压","4","2","1","3","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","TEPW1_B_Phase","六号一楼电量仪B相电压","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","TEPW1_C_Phase","六号一楼电量仪C相电压","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","9.1.114.1","TEPW1_Aver_Phase","六号一楼电量仪合相电压","4","2","1","3","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","9.1.114.1","TEPW1_A_Curr","六号一楼电量仪A相电流","4","2","1","3","4",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","9.1.114.1","TEPW1_B_Curr","六号一楼电量仪B相电流","4","2","1","3","20",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","9.1.114.1","TEPW1_C_Curr","六号一楼电量仪C相电流","4","2","1","3","36",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","9.1.114.1","TEPW1_Aver_Curr","六号一楼电量仪合相电流","4","2","1","3","52",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","9.1.114.1","TEPW1_Freq","六号一楼电量仪频率","3","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","9.1.114.1","TEPW1_AHavePower","六号一楼电量仪A相有功功率","4","2","1","3","8",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","9.1.114.1","TEPW1_BHavePower","六号一楼电量仪B相有功功率","4","2","1","3","24",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","9.1.114.1","TEPW1_CHavePower","六号一楼电量仪C相有功功率","4","2","1","3","40",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","9.1.114.1","TEPW1_Aver_HavePower","六号一楼电量仪合相有功功率","4","2","1","3","56",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.1","TEPW1_A_Line","六号一楼电量仪A线电压","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","9.1.114.1","TEPW1_B_Line","六号一楼电量仪B线电压","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","9.1.114.1","TEPW1_C_Line","六号一楼电量仪C线电压","4","2","1","3","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","9.1.114.1","TEPW1_Communications","六号楼一楼电量仪串口状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114","关","开","0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","通信中断,"]
["18","9.1.114.2","TEPW2_A_Phase","三号五楼电量仪A相电压","4","2","1","3","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","9.1.114.2","TEPW2_B_Phase","三号五楼电量仪B相电压","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","9.1.114.2","TEPW2_C_Phase","三号五楼电量仪C相电压","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","9.1.114.2","TEPW2_Aver_Phase","三号五楼电量仪合相电压","4","2","1","3","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.2","TEPW2_A_Curr","三号五楼电量仪A相电流","4","2","1","3","4",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.2","TEPW2_B_Curr","三号五楼电量仪B相电流","4","2","1","3","20",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.2","TEPW2_C_Curr","三号五楼电量仪C相电流","4","2","1","3","36",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.2","TEPW2_Aver_Curr","三号五楼电量仪合相电流","4","2","1","3","52",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","9.1.114.2","TEPW2_Freq","三号五楼电量仪频率","3","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","9.1.114.2","TEPW2_AHavePower","三号五楼电量仪A相有功功率","4","2","1","3","8",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","9.1.114.2","TEPW2_BHavePower","三号五楼电量仪B相有功功率","4","2","1","3","24",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","9.1.114.2","TEPW2_CHavePower","三号五楼电量仪C相有功功率","4","2","1","3","40",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","9.1.114.2","TEPW2_Aver_HavePower","三号五楼电量仪合相有功功率","4","2","1","3","56",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","9.1.114.2","TEPW2_A_Line","三号五楼电量仪A线电压","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","9.1.114.2","TEPW2_B_Line","三号五楼电量仪B线电压","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","9.1.114.2","TEPW2_C_Line","三号五楼电量仪C线电压","4","2","1","3","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","9.1.114.2","TEPW2_Communications","三号楼五楼电量仪串口状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114","关","开","0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","通信中断,"]
["35","9.1.114.3","TEPW3_A_Phase","三号四楼电量仪A相电压","4","2","1","3","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["36","9.1.114.3","TEPW3_B_Phase","三号四楼电量仪B相电压","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["37","9.1.114.3","TEPW3_C_Phase","三号四楼电量仪C相电压","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["38","9.1.114.3","TEPW3_Aver_Phase","三号四楼电量仪合相电压","4","2","1","3","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["39","9.1.114.3","TEPW3_A_Curr","三号四楼电量仪A相电流","4","2","1","3","4",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["40","9.1.114.3","TEPW3_B_Curr","三号四楼电量仪B相电流","4","2","1","3","20",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["41","9.1.114.3","TEPW3_C_Curr","三号四楼电量仪C相电流","4","2","1","3","36",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["42","9.1.114.3","TEPW3_Aver_Curr","三号四楼电量仪合相电流","4","2","1","3","52",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["43","9.1.114.3","TEPW3_Freq","三号四楼电量仪频率","3","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["44","9.1.114.3","TEPW3_AHavePower","三号四楼电量仪A相有功功率","4","2","1","3","8",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["45","9.1.114.3","TEPW3_BHavePower","三号四楼电量仪B相有功功率","4","2","1","3","24",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["46","9.1.114.3","TEPW3_CHavePower","三号四楼电量仪C相有功功率","4","2","1","3","40",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["47","9.1.114.3","TEPW3_Aver_HavePower","三号四楼电量仪合相有功功率","4","2","1","3","56",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["48","9.1.114.3","TEPW3_A_Line","三号四楼电量仪A线电压","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["49","9.1.114.3","TEPW3_B_Line","三号四楼电量仪B线电压","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["50","9.1.114.3","TEPW3_C_Line","三号四楼电量仪C线电压","4","2","1","3","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["51","9.1.114.3","TEPW3_Communications","三号楼四楼电量仪串口状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114","关","开","0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","通信中断,"]

{"sheet":"CSpreadSheetBackup","index":1,"n_rows":52,"n_cols":76,"rows_kept":52,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["223","9.1.114.1","TEPW1_A_Phase","六号一楼电量仪A相电压","4","2","1","3","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["224","9.1.114.1","TEPW1_B_Phase","六号一楼电量仪B相电压","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["225","9.1.114.1","TEPW1_C_Phase","六号一楼电量仪C相电压","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["226","9.1.114.1","TEPW1_Aver_Phase","六号一楼电量仪合相电压","4","2","1","3","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["227","9.1.114.1","TEPW1_A_Curr","六号一楼电量仪A相电流","4","2","1","3","4",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["228","9.1.114.1","TEPW1_B_Curr","六号一楼电量仪B相电流","4","2","1","3","20",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["229","9.1.114.1","TEPW1_C_Curr","六号一楼电量仪C相电流","4","2","1","3","36",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["230","9.1.114.1","TEPW1_Aver_Curr","六号一楼电量仪合相电流","4","2","1","3","52",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["231","9.1.114.1","TEPW1_Freq","六号一楼电量仪频率","3","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["232","9.1.114.1","TEPW1_AHavePower","六号一楼电量仪A相有功功率","4","2","1","3","8",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["233","9.1.114.1","TEPW1_BHavePower","六号一楼电量仪B相有功功率","4","2","1","3","24",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["234","9.1.114.1","TEPW1_CHavePower","六号一楼电量仪C相有功功率","4","2","1","3","40",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["235","9.1.114.1","TEPW1_Aver_HavePower","六号一楼电量仪合相有功功率","4","2","1","3","56",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["236","9.1.114.1","TEPW1_A_Line","六号一楼电量仪A线电压","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["237","9.1.114.1","TEPW1_B_Line","六号一楼电量仪B线电压","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["238","9.1.114.1","TEPW1_C_Line","六号一楼电量仪C线电压","4","2","1","3","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["430","9.1.114.1","TEPW1_ComStatus","六号楼一楼电量仪串口状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114","关","开","0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["239","9.1.114.2","TEPW2_A_Phase","三号五楼电量仪A相电压","4","2","1","3","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["240","9.1.114.2","TEPW2_B_Phase","三号五楼电量仪B相电压","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["241","9.1.114.2","TEPW2_C_Phase","三号五楼电量仪C相电压","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["242","9.1.114.2","TEPW2_Aver_Phase","三号五楼电量仪合相电压","4","2","1","3","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["243","9.1.114.2","TEPW2_A_Curr","三号五楼电量仪A相电流","4","2","1","3","4",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["244","9.1.114.2","TEPW2_B_Curr","三号五楼电量仪B相电流","4","2","1","3","20",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["245","9.1.114.2","TEPW2_C_Curr","三号五楼电量仪C相电流","4","2","1","3","36",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["246","9.1.114.2","TEPW2_Aver_Curr","三号五楼电量仪合相电流","4","2","1","3","52",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["247","9.1.114.2","TEPW2_Freq","三号五楼电量仪频率","3","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["248","9.1.114.2","TEPW2_AHavePower","三号五楼电量仪A相有功功率","4","2","1","3","8",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["249","9.1.114.2","TEPW2_BHavePower","三号五楼电量仪B相有功功率","4","2","1","3","24",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["250","9.1.114.2","TEPW2_CHavePower","三号五楼电量仪C相有功功率","4","2","1","3","40",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["251","9.1.114.2","TEPW2_Aver_HavePower","三号五楼电量仪合相有功功率","4","2","1","3","56",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["252","9.1.114.2","TEPW2_A_Line","三号五楼电量仪A线电压","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["253","9.1.114.2","TEPW2_B_Line","三号五楼电量仪B线电压","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["254","9.1.114.2","TEPW2_C_Line","三号五楼电量仪C线电压","4","2","1","3","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["432","9.1.114.2","TEPW2_ComStatus","三号楼五楼电量仪串口状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114","关","开","0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["255","9.1.114.3","TEPW3_A_Phase","三号四楼电量仪A相电压","4","2","1","3","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["256","9.1.114.3","TEPW3_B_Phase","三号四楼电量仪B相电压","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["257","9.1.114.3","TEPW3_C_Phase","三号四楼电量仪C相电压","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["258","9.1.114.3","TEPW3_Aver_Phase","三号四楼电量仪合相电压","4","2","1","3","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["259","9.1.114.3","TEPW3_A_Curr","三号四楼电量仪A相电流","4","2","1","3","4",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["260","9.1.114.3","TEPW3_B_Curr","三号四楼电量仪B相电流","4","2","1","3","20",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["261","9.1.114.3","TEPW3_C_Curr","三号四楼电量仪C相电流","4","2","1","3","36",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["262","9.1.114.3","TEPW3_Aver_Curr","三号四楼电量仪合相电流","4","2","1","3","52",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["263","9.1.114.3","TEPW3_Freq","三号四楼电量仪频率","3","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["264","9.1.114.3","TEPW3_AHavePower","三号四楼电量仪A相有功功率","4","2","1","3","8",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["265","9.1.114.3","TEPW3_BHavePower","三号四楼电量仪B相有功功率","4","2","1","3","24",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["266","9.1.114.3","TEPW3_CHavePower","三号四楼电量仪C相有功功率","4","2","1","3","40",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["267","9.1.114.3","TEPW3_Aver_HavePower","三号四楼电量仪合相有功功率","4","2","1","3","56",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0",null,"900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["268","9.1.114.3","TEPW3_A_Line","三号四楼电量仪A线电压","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["269","9.1.114.3","TEPW3_B_Line","三号四楼电量仪B线电压","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["270","9.1.114.3","TEPW3_C_Line","三号四楼电量仪C线电压","4","2","1","3","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["438","9.1.114.3","TEPW3_ComStatus","三号楼四楼电量仪串口状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114","关","开","0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]