{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["变量dat文件","CSpreadSheetBackup"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":48,"n_cols":76,"rows_kept":48,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","9.1.114.1","PM800_1_APhaseCurrent","1号PM800电量仪A相电流","4","2","1","3","1099",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","PM800_1_BPhaseCurrent","1号PM800电量仪B相电流","4","2","1","3","1100",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","PM800_1_CPhaseCurrent","1号PM800电量仪C相电流","4","2","1","3","1101",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","9.1.114.1","PM800_1_ABLineVoltage","1号PM800电量仪AB线电压","4","2","1","3","1119",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","9.1.114.1","PM800_1_BCLineVoltage","1号PM800电量仪BC线电压","4","2","1","3","1120",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","9.1.114.1","PM800_1_CALineVoltage","1号PM800电量仪CA线电压","4","2","1","3","1121",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","9.1.114.1","PM800_1_APhaseVoltage","1号PM800电量仪A相电压","4","2","1","3","1123",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","9.1.114.1","PM800_1_BPhaseVoltage","1号PM800电量仪B相电压","4","2","1","3","1124",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","9.1.114.1","PM800_1_CPhaseVoltage","1号PM800电量仪C相电压","4","2","1","3","1125",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","9.1.114.1","PM800_1_APhaseActivePower","1号PM800电量仪A相有功功率","4","2","1","3","1139",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","9.1.114.1","PM800_1_BPhaseActivePower","1号PM800电量仪B相有功功率","4","2","1","3","1140",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","9.1.114.1","PM800_1_CPhaseActivePower","1号PM800电量仪C相有功功率","4","2","1","3","1141",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","9.1.114.1","PM800_1_TotalActivePower","1号PM800电量仪总有功功率","4","2","1","3","1142",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.1","PM800_1_APhaseWattlessPower","1号PM800电量仪A相无功功率","4","2","1","3","1143",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","9.1.114.1","PM800_1_BPhaseWattlessPower","1号PM800电量仪B相无功功率","4","2","1","3","1144",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","9.1.114.1","PM800_1_CPhaseWattlessPower","1号PM800电量仪C相无功功率","4","2","1","3","1145",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","9.1.114.1","PM800_1_TotalWattlessPower","1号PM800电量仪总无功功率","4","2","1","3","1146",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","9.1.114.1","PM800_1_APhaseApparentPower","1号PM800电量仪A相视在功率","4","2","1","3","1147",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","9.1.114.1","PM800_1_BPhaseApparentPower","1号PM800电量仪B相视在功率","4","2","1","3","1148",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","9.1.114.1","PM800_1_CPhaseApparentPower","1号PM800电量仪C相视在功率","4","2","1","3","1149",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","9.1.114.1","PM800_1_TotalApparentPower","1号PM800电量仪总视在功率","4","2","1","3","1150",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.1","PM800_1_Frequency","1号PM800电量仪频率","4","2","1","3","1179",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.1","PM800_1_Communications","1号PM800电量仪通信状态","1000","2","1","3",{"$nulls":3},"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","通信中断,"]
[]
["1","9.1.114.2","PM800_2_APhaseCurrent","2号PM800电量仪A相电流","4","2","1","3","1099",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.2","PM800_2_BPhaseCurrent","2号PM800电量仪B相电流","4","2","1","3","1100",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.2","PM800_2_CPhaseCurrent","2号PM800电量仪C相电流","4","2","1","3","1101",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","9.1.114.2","PM800_2_ABLineVoltage","2号PM800电量仪AB线电压","4","2","1","3","1119",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","9.1.114.2","PM800_2_BCLineVoltage","2号PM800电量仪BC线电压","4","2","1","3","1120",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","9.1.114.2","PM800_2_CALineVoltage","2号PM800电量仪CA线电压","4","2","1","3","1121",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","9.1.114.2","PM800_2_APhaseVoltage","2号PM800电量仪A相电压","4","2","1","3","1123",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","9.1.114.2","PM800_2_BPhaseVoltage","2号PM800电量仪B相电压","4","2","1","3","1124",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","9.1.114.2","PM800_2_CPhaseVoltage","2号PM800电量仪C相电压","4","2","1","3","1125",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","9.1.114.2","PM800_2_APhaseActivePower","2号PM800电量仪A相有功功率","4","2","1","3","1139",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","9.1.114.2","PM800_2_BPhaseActivePower","2号PM800电量仪B相有功功率","4","2","1","3","1140",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","9.1.114.2","PM800_2_CPhaseActivePower","2号PM800电量仪C相有功功率","4","2","1","3","1141",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","9.1.114.2","PM800_2_TotalActivePower","2号PM800电量仪总有功功率","4","2","1","3","1142",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.2","PM800_2_APhaseWattlessPower","2号PM800电量仪A相无功功率","4","2","1","3","1143",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","9.1.114.2","PM800_2_BPhaseWattlessPower","2号PM800电量仪B相无功功率","4","2","1","3","1144",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","9.1.114.2","PM800_2_CPhaseWattlessPower","2号PM800电量仪C相无功功率","4","2","1","3","1145",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","9.1.114.2","PM800_2_TotalWattlessPower","2号PM800电量仪总无功功率","4","2","1","3","1146",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","9.1.114.2","PM800_2_APhaseApparentPower","2号PM800电量仪A相视在功率","4","2","1","3","1147",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","9.1.114.2","PM800_2_BPhaseApparentPower","2号PM800电量仪B相视在功率","4","2","1","3","1148",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","9.1.114.2","PM800_2_CPhaseApparentPower","2号PM800电量仪C相视在功率","4","2","1","3","1149",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","9.1.114.2","PM800_2_TotalApparentPower","2号PM800电量仪总视在功率","4","2","1","3","1150",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.2","PM800_2_Frequency","2号PM800电量仪频率","4","2","1","3","1179",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.2","PM800_2_Communications","2号PM800电量仪通信状态","1000","2","1","3",{"$nulls":3},"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","通信中断,"]

{"sheet":"CSpreadSheetBackup","index":1,"n_rows":47,"n_cols":76,"rows_kept":47,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","9.1.114.1","PM800_1_APhaseCurrent","PM800电量仪A相电流","4","2","1","3","1100",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","PM800_1_BPhaseCurrent","PM801电量仪B相电流","4","2","1","3","1101",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","PM800_1_CPhaseCurrent","PM802电量仪C相电流","4","2","1","3","1102",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","9.1.114.1","PM800_1_ABLineVoltage","PM800电量仪AB线电压","4","2","1","3","1120",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","9.1.114.1","PM800_1_BCLineVoltage","PM800电量仪BC线电压","4","2","1","3","1121",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","9.1.114.1","PM800_1_CALineVoltage","PM800电量仪CA线电压","4","2","1","3","1122",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","9.1.114.1","PM800_1_APhaseVoltage","PM800电量仪A相电压","4","2","1","3","1124",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","9.1.114.1","PM800_1_BPhaseVoltage","PM801电量仪B相电压","4","2","1","3","1125",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","9.1.114.1","PM800_1_CPhaseVoltage","PM802电量仪C相电压","3","2","1","3","1126",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","9.1.114.1","PM800_1_APhaseActivePower","PM800电量仪A相有功功率","4","2","1","3","1140",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","9.1.114.1","PM800_1_BPhaseActivePower","PM801电量仪B相有功功率","4","2","1","3","1141",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","9.1.114.1","PM800_1_CPhaseActivePower","PM802电量仪C相有功功率","4","2","1","3","1142",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","9.1.114.1","PM800_1_TotalActivePower","PM802电量仪总有功功率","4","2","1","3","1143",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.1","PM800_1_APhaseWattlessPower","PM800电量仪A相无功功率","4","2","1","3","1144",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","9.1.114.1","PM800_1_BPhaseWattlessPower","PM801电量仪B相无功功率","4","2","1","3","1145",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","9.1.114.1","PM800_1_CPhaseWattlessPower","PM802电量仪C相无功功率","4","2","1","3","1146",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","9.1.114.1","PM800_1_TotalWattlessPower","PM802电量仪总无功功率","4","2","1","3","1147",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","9.1.114.1","PM800_1_APhaseApparentPower","PM800电量仪A相视在功率","4","2","1","3","1148",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","9.1.114.1","PM800_1_BPhaseApparentPower","PM801电量仪B相视在功率","4","2","1","3","1149",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","9.1.114.1","PM800_1_CPhaseApparentPower","PM802电量仪C相视在功率","4","2","1","3","1150",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","9.1.114.1","PM800_1_TotalApparentPower","PM802电量仪总视在功率","4","2","1","3","1151",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.1","PM800_1_Frequency","PM802电量仪频率","4","2","1","3","1180",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.1","PM800_1_Communications","PM802电量仪通信状态","1000","2","1","3",{"$nulls":3},"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","通信中断,"]
["1","9.1.114.2","PM800_2_APhaseCurrent","PM800电量仪A相电流","4","2","1","3","1100",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.2","PM800_2_BPhaseCurrent","PM801电量仪B相电流","4","2","1","3","1101",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.2","PM800_2_CPhaseCurrent","PM802电量仪C相电流","4","2","1","3","1102",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","9.1.114.2","PM800_2_ABLineVoltage","PM800电量仪AB线电压","4","2","1","3","1120",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","9.1.114.2","PM800_2_BCLineVoltage","PM800电量仪BC线电压","4","2","1","3","1121",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","9.1.114.2","PM800_2_CALineVoltage","PM800电量仪CA线电压","4","2","1","3","1122",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","9.1.114.2","PM800_2_APhaseVoltage","PM800电量仪A相电压","4","2","1","3","1124",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","9.1.114.2","PM800_2_BPhaseVoltage","PM801电量仪B相电压","4","2","1","3","1125",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","9.1.114.2","PM800_2_CPhaseVoltage","PM802电量仪C相电压","3","2","1","3","1126",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","9.1.114.2","PM800_2_APhaseActivePower","PM800电量仪A相有功功率","4","2","1","3","1140",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","9.1.114.2","PM800_2_BPhaseActivePower","PM801电量仪B相有功功率","4","2","1","3","1141",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","9.1.114.2","PM800_2_CPhaseActivePower","PM802电量仪C相有功功率","4","2","1","3","1142",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","9.1.114.2","PM800_2_TotalActivePower","PM802电量仪总有功功率","4","2","1","3","1143",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.2","PM800_2_APhaseWattlessPower","PM800电量仪A相无功功率","4","2","1","3","1144",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","9.1.114.2","PM800_2_BPhaseWattlessPower","PM801电量仪B相无功功率","4","2","1","3","1145",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","9.1.114.2","PM800_2_CPhaseWattlessPower","PM802电量仪C相无功功率","4","2","1","3","1146",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","9.1.114.2","PM800_2_TotalWattlessPower","PM802电量仪总无功功率","4","2","1","3","1147",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","9.1.114.2","PM800_2_APhaseApparentPower","PM800电量仪A相视在功率","4","2","1","3","1148",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","9.1.114.2","PM800_2_BPhaseApparentPower","PM801电量仪B相视在功率","4","2","1","3","1149",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","9.1.114.2","PM800_2_CPhaseApparentPower","PM802电量仪C相视在功率","4","2","1","3","1150",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","900","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","9.1.114.2","PM800_2_TotalApparentPower","PM802电量仪总视在功率","4","2","1","3","1151",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","KW","300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","99999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.2","PM800_2_Frequency","PM802电量仪频率","4","2","1","3","1180",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.2","PM800_2_Communications","PM802电量仪通信状态","1000","2","1","3",{"$nulls":3},"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","通信中断,"]