{"text_format":"3","workbook":"xls","n_sheets":15,"sheets":["0封面","2 设置参数","3 设置时间","4 读控制器EEPROM数值","5 写控制器EEPROM数值","6 写RAM临时变化的数值","7 设置单元开&关","8 单元警报重置","9 控制器状态2","10 控制器ID","11 单元配置","C5000 增加项","16 令牌","1 长状态请求1","21 长状态请求2"],"not_rendered":{"images":2,"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"0封面","index":0,"n_rows":48,"n_cols":1,"rows_kept":48,"flags":["formulas_cached_only"]}
{"$rows_empty":11}
["GmbH Klimatechnik"]
[]
["Monitoring Dataprotocoll"]
[]
["C1001/2 C4000 C5000 C6000"]
{"$rows_empty":30}
["Release V1.1"]
["January 15 2001"]

{"sheet":"2 设置参数","index":1,"n_rows":117,"n_cols":8,"rows_kept":117,"flags":["formulas_cached_only"]}
[null,"Set Parameter"]
[null,"设置参数"]
["Set Parameter (PC -> MC)"]
["设置参数(电脑->空调)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x"]
[1,"command id","命令ID",null,2,"x","x","x"]
[2,"number of following bytes","下面的字节数",null,92,"x","x","x"]
[3,"not used","未用"]
[4,"not used","未用"]
[5,"not used","未用"]
[6,"not used","未用"]
[7,"not used","未用"]
[8,"not used","未用"]
[9,"not used","未用"]
[10,"setpoint temperature","设置点温度","10,0 .. 30,0°C","0 .. 200","x","x","x"]
[11,"setpoint humidity","设置点湿度","10 .. 90 %","10 .. 90","x","x","x"]
[12,"return air temperature too high","回风温度太高","0 ..30 °C","0 .. 30","x","x","x"]
[13,"supply air temperature too high","进风温度太高","0 ..30 °C","0 .. 30",null,"x","x"]
[14,"return air temperature too low","回风温度太低","0 ..30 °C","0 .. 30","x","x","x"]
[15,"supply air temperature too low","进风温度太低","0 ..30 °C","0 .. 30",null,"x","x"]
[16,"water temperature too high","水温太高","0 .. 50°C","0 ..50",null,"x","x"]
[17,"water temperature too low","水温太低"," - 50..0..30 °C","0 .. 80",null,"x","x"]
[18,"return humidity too high","回风湿度太高","0 ..90","0 .. 90","x","x","x"]
[19,"supply humidity too high","进风湿度太高","0 ..90","0 .. 90",null,"x","x"]
[20,"return humidity too low","回风湿度太低","0 ..90","0 .. 90","x","x","x"]
[21,"supply humidity too low","进风湿度太低","0 ..90","0 .. 90",null,"x","x"]
[null,"         -------------------------------------  d a t a    m o d u l e   1  数据模块1-----------------------------------------"]
[22,"compressor start  (setpoint + val)","压缩机开始(设置点 + 数值)","0.0..10.0K","0 .. 100","x","x","x"]
[23,"compressor hysteresis","压缩机延迟","0.0..10.0K","0 .. 100","x","x","x"]
[24,"suction valve start","抽风机阀门开始","0.0..10.0K","0 .. 100",null,"x","x"]
[25,"suction valve proportional band","抽风机阀门比例频率","0.0..10.0K","0 .. 100",null,"x","x"]
[26,"drycooler start temperature","干冷机开始的温度","0.0..10.0K","0 .. 100",null,"x","x"]
[27,"drycooler enable temperature","干冷机启用的温度","0..35°C","0 .. 35",null,"x","x"]
[28,"glycol-pump start temperature","干冷机-泵开始的温度","0.0..10.0K","0 .. 100",null,"x","x"]
[29,"GE/CW valve off temperature","GE/CW阀门关闭温度","0..45°C","0 .. 45",null,"x","x"]
[30,"GE/CW valve start temperature","GE/CW阀门开始温度","0.0..10.0K","0 .. 100","x","x","x"]
[31,"GE/CW valve proportional band","GE/CW阀门比例频率","0.0..10.0K","0 .. 100","x","x","x"]
[32,"reheat 1 start temperature","加热器1开始温度","0.0..10.0K","0 .. 100","x","x","x"]
[33,"reheat 1 hysteresis","加热器1延迟","0.0..10.0K","0 .. 100","x","x","x"]
[34,"reheat 2 start temperature","加热器2开始温度","0.0..10.0K","0 .. 100","x","x","x"]
[35,"reheat 2 hysteresis","加热器2延迟","0.0..10.0K","0 .. 100",null,"x","x"]
[36,"reheat 3 start temperature","加热器3开始温度","0.0..10.0K","0 .. 100",null,"x","x"]
[37,"reheat 3 hysteresis","加热器3延迟","0.0..10.0K","0 .. 100",null,"x","x"]
[38,"PWW valve start temperature","PWW阀门开始温度","0.0..10.0K","0 .. 100",null,"x","x"]
[39,"PWW valve proportional band","PWW阀门比例频率","0.0..10.0K","0 .. 100",null,"x","x"]
[40,"dehumidification start","除湿器开始","0..90%","0 .. 90","x","x","x"]
[41,"dehumidification hysteresis","除湿器延迟","0..90%","0 .. 90","x","x","x"]
[42,"humidification start","加湿器开始","0..90%","0 .. 90","x","x","x"]
[43,"humidification hysteresis","加湿器延迟","0..90%","0 .. 90","x","x","x"]
[44,"humidification proportional start","加湿器比例开始","0..90%","0 .. 90",null,"x","x"]
[45,"humidification proportional band","加湿器比例频率","0..90%","0 .. 90",null,"x","x"]
[null,"         -------------------------------------  d a t a    m o d u l e   2  数据模块2-----------------------------------------"]
[46,"compressor start  (setpoint + val)","压缩机开始(设置点 + 数值)","0.0..10.0K","0 .. 100","x","x","x"]
[47,"compressor hysteresis","压缩机延迟","0.0..10.0K","0 .. 100",null,"x","x"]
[48,"suction valve start","抽风机阀门开始","0.0..10.0K","0 .. 100",null,"x","x"]
[49,"suction valve proportional band","抽风机阀门比例频率","0.0..10.0K","0 .. 100",null,"x","x"]
[50,"drycooler start temperature","干冷机开始的温度","0.0..10.0K","0 .. 100",null,"x","x"]
[51,"reheat 1 start temperature","加热器1开始温度","0.0..10.0K","0 .. 100",null,"x","x"]
[52,"reheat 1 hysteresis","加热器1延迟","0.0..10.0K","0 .. 100",null,"x","x"]
[53,"reheat 2 start temperature","加热器2开始温度","0.0..10.0K","0 .. 100",null,"x","x"]
[54,"reheat 2 hysteresis","加热器2延迟","0.0..10.0K","0 .. 100",null,"x","x"]
[55,"reheat 3 start temperature","加热器3开始温度","0.0..10.0K","0 .. 100",null,"x","x"]
[56,"reheat 3 hysteresis","加热器3延迟","0.0..10.0K","0 .. 100",null,"x","x"]
[57,"dehumidification start","除湿器开始","0..90%","0 .. 90",null,"x","x"]
[58,"dehumidification hysteresis","除湿器延迟","0..90%","0 .. 90",null,"x","x"]
[59,"humidification start","加湿器开始","0..90%","0 .. 90",null,"x","x"]
[60,"humidification hysteresis","加湿器延迟","0..90%","0 .. 90",null,"x","x"]
[null,"         -------------------------------------  d a t a    m o d u l e   3  数据模块3-----------------------------------------"]
[61,"compressor start  (setpoint + val)","压缩机开始(设置点 + 数值)","0.0..10.0K","0 .. 100",null,"x","x"]
[62,"compressor hysteresis","压缩机延迟","0.0..10.0K","0 .. 100",null,"x","x"]
[63,"suction valve start","抽风机阀门开始","0.0..10.0K","0 .. 100",null,"x","x"]
[64,"suction valve proportional band","抽风机阀门比例频率","0.0..10.0K","0 .. 100",null,"x","x"]
[65,"drycooler start temperature","干冷机开始的温度","0.0..10.0K","0 .. 100",null,"x","x"]
[66,"reheat 1 start temperature","加热器1开始温度","0.0..10.0K","0 .. 100",null,"x","x"]
[67,"reheat 1 hysteresis","加热器1延迟","0.0..10.0K","0 .. 100",null,"x","x"]
[68,"reheat 2 start temperature","加热器2开始温度","0.0..10.0K","0 .. 100",null,"x","x"]
[69,"reheat 2 hysteresis","加热器2延迟","0.0..10.0K","0 .. 100",null,"x","x"]
[70,"reheat 3 start temperature","加热器3开始温度","0.0..10.0K","0 .. 100",null,"x","x"]
[71,"reheat 3 hysteresis","加热器3延迟","0.0..10.0K","0 .. 100",null,"x","x"]
[72,"dehumidification start","除湿器开始","0..90%","0 .. 90",null,"x","x"]
[73,"dehumidification hysteresis","除湿器延迟","0..90%","0 .. 90",null,"x","x"]
[74,"humidification start","加湿器开始","0..90%","0 .. 90",null,"x","x"]
[75,"humidification hysteresis","加湿器延迟","0..90%","0 .. 90",null,"x","x"]
[null,"         -------------------------------------  d a t a    m o d u l e   4   数据模块4-----------------------------------------"]
[76,"compressor start  (setpoint + val)","压缩机开始(设置点 + 数值)","0.0..10.0K","0 .. 100",null,"x","x"]
[77,"compressor hysteresis","压缩机延迟","0.0..10.0K","0 .. 100",null,"x","x"]
[78,"suction valve start","抽风机阀门开始","0.0..10.0K","0 .. 100",null,"x","x"]
[79,"suction valve proportional band","抽风机阀门比例频率","0.0..10.0K","0 .. 100",null,"x","x"]
[80,"drycooler start temperature","干冷机开始的温度","0.0..10.0K","0 .. 100",null,"x","x"]
[81,"reheat 1 start temperature","加热器1开始温度","0.0..10.0K","0 .. 100",null,"x","x"]
[82,"reheat 1 hysteresis","加热器1延迟","0.0..10.0K","0 .. 100",null,"x","x"]
[83,"reheat 2 start temperature","加热器2开始温度","0.0..10.0K","0 .. 100",null,"x","x"]
[84,"reheat 2 hysteresis","加热器2延迟","0.0..10.0K","0 .. 100",null,"x","x"]
[85,"reheat 3 start temperature","加热器3开始温度","0.0..10.0K","0 .. 100",null,"x","x"]
[86,"reheat 3 hysteresis","加热器3延迟","0.0..10.0K","0 .. 100",null,"x","x"]
[87,"dehumidification start","除湿器开始","0..90%","0 .. 90",null,"x","x"]
[88,"dehumidification hysteresis","除湿器延迟","0..90%","0 .. 90",null,"x","x"]
[89,"humidification start","加湿器开始","0..90%","0 .. 90",null,"x","x"]
[90,"humidification hysteresis","加湿器延迟","0..90%","0 .. 90",null,"x","x"]
[null,"         -------------------------------------  g e n e r a l   d a t a   -----------------------------------------"]
[91,"general status byte 1","一般状态字节1","bit-coded","see table","x","x","x"]
[92,"general status byte 2","一般状态字节2","bit-coded","see table","x","x","x"]
[93,"LB checksum","低位校验","1..255",null,"x","x","x"]
[94,"HB checksum","高位校验","1..255",null,"x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 92."]
[null,"16位校验是2的补数,补数为从字节0到字节92的合计。"]
["Set Parameter Acknowledge (MC -> PC)"]
["设置参数确认(空调->电脑)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x"]
[1,"command id","命令ID",null,2,"x","x","x"]
[2,"number of following bytes","下面的字节数",null,2,"x","x","x"]
[3,"LB checksum","低位校验","1..255",null,"x","x","x"]
[4,"HB checksum","高位校验","1..255",null,"x","x","x"]
[" ","The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 2."]
[null,"16位校验是2的补数,补数为从字节0到字节2的合计。"]

{"sheet":"3 设置时间","index":2,"n_rows":28,"n_cols":8,"rows_kept":28,"flags":["formulas_cached_only"]}
[null,"Set Time"]
[null,"设置时间"]
["Set Time (PC -> MC)"]
["设置时间(电脑->空调)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,null,"x","x"]
[1,"command id","命令ID",null,3,null,"x","x"]
[2,"number of following bytes","下面的字节数",null,7,null,"x","x"]
[3,"year","年","0..99",null,null,"x","x"]
[4,"month","月","1..12",null,null,"x","x"]
[5,"day","日","1..31",null,null,"x","x"]
[6,"hour","时","0..23",null,null,"x","x"]
[7,"minute","分","0..59",null,null,"x","x"]
[8,"LB checksum","低位校验","0..255",null,null,"x","x"]
[9,"HB checksum","高位校验","0..255",null,null,"x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 7."]
[null,"16位校验是2的补数,补数为从字节0到字节7的合计。"]
[]
["Set Time Acknowledge (MC -> PC)"]
["设置时间确认(空调>电脑)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,null,"x","x"]
[1,"command id","命令ID",null,3,null,"x","x"]
[2,"number of following bytes","下面的字节数",null,2,null,"x","x"]
[3,"LB checksum","低位校验","0..255",null,null,"x","x"]
[4,"HB checksum","高位校验","0..255",null,null,"x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 2."]
[null,"16位校验是2的补数,补数为从字节0到字节2的合计。"]

{"sheet":"4 读控制器EEPROM数值","index":3,"n_rows":46,"n_cols":8,"rows_kept":46,"flags":["formulas_cached_only"]}
[null,"Read Controller EEPROM Data"]
[null,"读控制器EEPROM数值"]
["Read EEPROM Data (PC -> MC)"]
["读控制器EEPROM数值(电脑->空调)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x"]
[1,"command id","命令ID",null,4,"x","x","x"]
[2,"number of following bytes","下面的字节数",null,3,"x","x","x"]
[3,"EEPROM address to be read","需读的EEPROM地址","0..255","0..255","x","x","x"]
[4,"LB checksum","低位校验","0..255",null,"x","x","x"]
[5,"HB checksum","高位校验","0..255",null,"x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 3."]
[null,"16位校验是2的补数,补数为从字节0到字节3的合计。"]
[]
["Read EEPROM Data (MC -> PC)"]
["读控制器EEPROM数值(空调>电脑)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x"]
[1,"command id","命令ID",null,4,"x","x","x"]
[2,"number of following bytes","下面的字节数",null,3,"x","x","x"]
[3,"contents of EEPROM (value)","EEPROM(数值)的内容","0..255","0..255","x","x","x"]
[4,"LB checksum","低位校验","0..255",null,"x","x","x"]
[5,"HB checksum","高位校验","0..255",null,"x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 3."]
[null,"16位校验是2的补数,补数为从字节0到字节3的合计。"]
[]
["EEPROM  Address List:"]
["EEPROM  地址列表:"]
["Address","Description",null,"Range","Value","C1001/2","C4000","C5000"]
["56-57","LB/HB runtime fan 1","低位/高位 运行时 风扇1","0..65536","0..65536",null,"O.T.E.","?"]
["58-59","LB/HB runtime compressor 1","低位/高位 运行时 压缩机1","0..65536","0..65536",null,"O.T.E.","?"]
["60-61","LB/HB runtime humidifier 1","低位/高位 运行时 加湿器1","0..65536","0..65536",null,"O.T.E.","?"]
["62-63","LB/HB runtime reheat 1 / pump 1","低位/高位 运行时 加温器1/泵1","0..65536","0..65536",null,"O.T.E.","?"]
["64-65","LB/HB runtime reheat 2 / pump 2","低位/高位 运行时 加温器2/泵2","0..65536","0..65536",null,"O.T.E.","?"]
["66-67","LB/HB runtime fan 2","低位/高位 运行时 风扇2","0..65536","0..65536",null,"O.T.E.","?"]
["68-69","LB/HB runtime compressor 2","低位/高位 运行时 压缩机2","0..65536","0..65536",null,"O.T.E.","?"]
["76-77","LB/HB runtime fan 3","低位/高位 运行时 风扇3","0..65536","0..65536",null,"O.T.E.","?"]
["78-79","LB/HB runtime compressor 3","低位/高位 运行时 压缩机3","0..65536","0..65536",null,"O.T.E.","?"]
["86-87","LB/HB runtime fan 4","低位/高位 运行时 风扇4","0..65536","0..65536",null,"O.T.E.","?"]
["88-89","LB/HB runtime compressor 4","低位/高位 运行时 压缩机4","0..65536","0..65536",null,"O.T.E.","?"]
[115,"setpoint temperature","设置点温度","10.0..35.0°C","0..250","x","x","x"]
[116,"setpoint humidity","设置点湿度","0..100%","0..100","x","x","x"]
[122,"return air temp. too high alarm","回风温度太高警报","0..50°C","0..50","x","x","x"]
[124,"return air temp. too low alarm","回风温度太低警报","0..50°C","0..50","x","x","x"]
[128,"return air humid. too high alarm","回风湿度太高警报","0..90%","0..90","x","x","x"]
[130,"return air humid. too low alarm","回风湿度太低警报","0..90%","0..90","x","x","x"]

{"sheet":"5 写控制器EEPROM数值","index":4,"n_rows":29,"n_cols":8,"rows_kept":29,"flags":["formulas_cached_only"]}
[null,"Write Controller EEPROM Data"]
[null,"写控制器EEPROM数值"]
["Write EEPROM Data (PC -> MC)"]
["写EEPROM数值(电脑->空调)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x"]
[1,"command id","命令ID",null,5,"x","x","x"]
[2,"number of following bytes","下面的字节数",null,4,"x","x","x"]
[3,"EEPROM address ","EEPROM地址","0..255","0..255","x","x","x"]
[4,"EEPROM data","EEPROM数据","0..255","0..255","x","x","x"]
[5,"LB checksum","低位校验","0..255",null,"x","x","x"]
[6,"HB checksum","高位校验","0..255",null,"x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 4."]
[null,"16位校验是2的补数,补数为从字节0到字节4的合计。"]
[]
["Write EEPROM Data (MC -> PC)"]
["写EEPROM数值(空调->电脑)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x"]
[1,"command id","命令ID",null,5,"x","x","x"]
[2,"number of following bytes","下面的字节数",null,2,"x","x","x"]
[3,"LB checksum","低位校验","0..255",null,"x","x","x"]
[4,"HB checksum","高位校验","0..255",null,"x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 2."]
[null,"16位校验是2的补数,补数为从字节0到字节2的合计。"]
[]
[]
["EEPROM  Address List:  see list for command 4 (READ EEPROM)"]
["EEPROM地址列表:  看命令4列表(读EEPROM)"]

{"sheet":"6 写RAM临时变化的数值","index":5,"n_rows":29,"n_cols":8,"rows_kept":29,"flags":["formulas_cached_only"]}
[null,"Write RAM Data for Temporary Changes"]
[null,"写RAM临时变化的数值"]
["Write RAM Data for temporary changes (PC -> MC)"]
["写RAM临时变化的数值(电脑->空调)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x"]
[1,"command id","命令ID",null,6,"x","x","x"]
[2,"number of following bytes","下面的字节数",null,4,"x","x","x"]
[3,"RAM address ","RAM地址","0..255","0..255","x","x","x"]
[4,"RAM data","RAM数据","0..255","0..255","x","x","x"]
[5,"LB checksum","低位校验","0..255",null,"x","x","x"]
[6,"HB checksum","高位校验","0..255",null,"x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 4."]
[null,"16位校验是2的补数,补数为从字节0到字节4的合计。"]
[]
["Write RAM Data for temporary changes (MC -> PC)"]
["写RAM临时变化的数值(空调->电脑)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x"]
[1,"command id","命令ID",null,6,"x","x","x"]
[2,"number of following bytes","下面的字节数",null,2,"x","x","x"]
[3,"LB checksum","低位校验","0..255",null,"x","x","x"]
[4,"HB checksum","高位校验","0..255",null,"x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 2."]
[null,"16位校验是2的补数,补数为从字节0到字节2的合计。"]
[]
[]
["RAM / EEPROM  Address List:  see list for command 4 (READ EEPROM)"]
["RAM/EEPROM地址列表:  看命令4列表(读EEPROM)"]

{"sheet":"7 设置单元开&关","index":6,"n_rows":51,"n_cols":8,"rows_kept":51,"flags":["formulas_cached_only"]}
[null,"Set Unit ON / OFF - Request Short Status"]
[null,"设置单元开/关-请求短消息状态"]
["Set Unit ON / OFF / REQUEST STATUS  (PC -> MC)"]
["设置单元开/关-请求短消息状态(电脑->空调)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x"]
[1,"command id","命令ID",null,7,"x","x","x"]
[2,"number of following bytes","下面的字节数",null,3,"x","x","x"]
[3,"STATUS-REQUEST / ON / OFF byte","状态-请求 开/关字节","bit-coded",null,"x","x","x"]
[4,"LB checksum","低位校验","0..255",null,"x","x","x"]
[5,"HB checksum","高位校验","0..255",null,"x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 3."]
[null,"16位校验是2的补数,补数为从字节0到字节3的合计。"]
[]
["Set Unit ON / OFF / REQUEST STATUS  (MC -> PC)"]
["设置单元开/关-请求短消息状态(空调->电脑)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x"]
[1,"command id","命令ID",null,7,"x","x","x"]
[2,"number of following bytes","下面的字节数",null,3,"x","x","x"]
[3,"S_STAT short unit status","S_STAT 单元短状态","bit-coded",null,"x","x","x"]
[4,"LB checksum","低位校验","0..255",null,"x","x","x"]
[5,"HB checksum","高位校验","0..255",null,"x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 3."]
[null,"16位校验是2的补数,补数为从字节0到字节3的合计。"]
[]
["Bit #","STATUS-REQUEST / ON / OFF byte状态-请求 开/关字节",null,"POS","Value","C1001/2","C4000","C5000"]
[0,"0 = unit off,  1 = unit on","0 = 单元关闭,  1 = 单元打开","0x01","bit","x","x","x"]
[1,"1 = request short status only","1=只请求短状态","0x02","bit","x","x","x"]
[2,"not used","未用","0x04","bit","x","x","x"]
[3,"not used","未用","0x08","bit","x","x","x"]
[4,"not used","未用","0x10","bit","x","x","x"]
[5,"not used","未用","0x20","bit","x","x","x"]
[6,"not used","未用","0x40","bit","x","x","x"]
[7,"not used","未用","0x80","bit","x","x","x"]
[null,"NOTE: if bit #1 is set to 1, the value of bit #0 is don't care !!"]
[null,"注意：如果比特#1设置为1,那么比特#0可不管!!"]
[]
["Bit #","S_STAT short unit status。S_STAT单元短状态",null,"POS","R/W","C1001/2","C4000","C5000"]
[0,"0 = PC-STOP (monitoring),  1 = on","0=电脑-停止(监测)，1=打开","0x01","R/W","x","x","x"]
[1,"0 = REMOTE STOP (contact),  1 = on","0=远程停止(干接点)，1=打开","0x02","R","x","x","x"]
[2,"0 = LOCAL STOP (key),  1 = on","0=本地停止(键)，1=打开","0x04","R","x","x","x"]
[3,"0 = TIMER-STOP (weekly oper.),  1 = on","0=时间计划停止(每周操作)，1=打开","0x08","R",null,null,"x"]
[4,"1 = WARNING (FILTER...)","1=警告(过滤器)","0x10","R","x","x","x"]
[5,"1 = HUMIDITY ALARM (low / high)","1=湿度警报(低/高)","0x20","R","x","x","x"]
[6,"1 = TEMPERATURE ALARM (low / high)","1=温度警报(低/高)","0x40","R","x","x","x"]
[7,"1 = COMMON ALARM","1=一般警报","0x80","R","x","x","x"]
[null,"NOTE: only if bits #0 to #3 are set to 1 the unit is in operation."]
[null,"If one of the bits #0,#1,#2,#3 is set to 0 the unit is in STOP condition."]
[null,"注意：如果比特#0-#3设置为1,那么单元在操作"]
[null,"如果比特#0、#1、#2或#3(其中一个)设置为0,那么单元在停止状态"]

{"sheet":"8 单元警报重置","index":7,"n_rows":23,"n_cols":8,"rows_kept":23,"flags":["formulas_cached_only"]}
[null,"Unit Alarm Reset "]
[null,"单元警报重置"]
["Unit Alarm Reset  (PC -> MC)"]
["单元警报重置(电脑->空调)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x"]
[1,"command id","命令ID",null,8,"x","x","x"]
[2,"number of following bytes","下面的字节数",null,2,"x","x","x"]
[3,"LB checksum","低位校验","0..255",null,"x","x","x"]
[4,"HB checksum","高位校验","0..255",null,"x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 2."]
[null,"16位校验是2的补数,补数为从字节0到字节2的合计。"]
[]
["Unit Alarm Reset  (MC -> PC)"]
["单元警报重置(空调->电脑)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x"]
[1,"command id","命令ID",null,8,"x","x","x"]
[2,"number of following bytes","下面的字节数",null,2,"x","x","x"]
[3,"LB checksum","低位校验","0..255",null,"x","x","x"]
[4,"HB checksum","高位校验","0..255",null,"x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 2."]
[null,"16位校验是2的补数,补数为从字节0到字节2的合计。"]

{"sheet":"9 控制器状态2","index":8,"n_rows":68,"n_cols":8,"rows_kept":68,"flags":["formulas_cached_only"]}
[null,"Controller Status 2, Component Runtime"]
[null,"控制器状态2,组件运行时间"]
["Controller Status 2, Component Runtime (PC -> MC)"]
["控制器状态2,组件运行时间(电脑->空调)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null," ","x","x"]
[1,"command id","命令ID",null,9," ","x","x"]
[2,"number of following bytes","下面的字节数",null,2," ","x","x"]
[3,"LB checksum","低位校验","0..255",null," ","x","x"]
[4,"HB checksum","高位校验","0..255",null," ","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 2."]
[null,"16位校验是2的补数,补数为从字节0到字节2的合计。"]
[]
["Controller Status 2, Component Runtime (MC -> PC)"]
["控制器状态2,组件运行时间(空调->电脑)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,null,"x","x"]
[1,"command id","命令ID",null,9,null,"x","x"]
[2,"number of following bytes","下面的字节数",null,43,null,"x","x"]
[3,"number of modules","模块数量","0..8","0..8",null,"x","x"]
[null,"         -------------------------------------  d a t a    m o d u l e   1  数据模块1-----------------------------------------"]
[4,"LB runtime fan 1","低位运行时风机1","0..65536",null,null,"x","x"]
[5,"HB runtime fan 1","高位运行时风机1"]
[6,"LB runtime compressor 1","低位运行时压缩机1","0..65536",null,null,"x","x"]
[7,"HB runtime compressor 1","高位运行时压缩机1"]
[8,"LB runtime humidifier 1","低位运行时加湿器1","0..65536",null,null,"x","x"]
[9,"HB runtime humidifier 1","高位运行时加湿器1"]
[10,"LB runtime pump 1 (reheat 1)","低位运行时泵1","0..65536",null,null,"x","x"]
[11,"HB runtime pump 1 (reheat 1)","高位运行时泵1"]
[12,"LB runtime pump 2 (reheat 2)","低位运行时泵2","0..65536",null,null,"x","x"]
[13,"HB runtime pump 2 (reheat 2)","高位运行时泵2"]
[null,"         -------------------------------------  d a t a    m o d u l e   2  数据模块2-----------------------------------------"]
[14,"LB runtime fan 1","低位运行时风机1","0..65536",null,null,"x","x"]
[15,"HB runtime fan 1","高位运行时风机1"]
[16,"LB runtime compressor 1","低位运行时压缩机1","0..65536",null,null,"x","x"]
[17,"HB runtime compressor 1","高位运行时压缩机1"]
[18,"LB runtime humidifier 1","低位运行时加湿器1","0..65536",null,null,"x","x"]
[19,"HB runtime humidifier 1","高位运行时加湿器1"]
[20,"LB runtime pump 1 (reheat 1)","低位运行时泵1","0..65536",null,null,"x","x"]
[21,"HB runtime pump 1 (reheat 1)","高位运行时泵1"]
[22,"LB runtime pump 2 (reheat 2)","低位运行时泵2","0..65536",null,null,"x","x"]
[23,"HB runtime pump 2 (reheat 2)","高位运行时泵2"]
[null,"         -------------------------------------  d a t a    m o d u l e   3  数据模块3-----------------------------------------"]
[24,"LB runtime fan 1","低位运行时风机1","0..65536",null,null,"x","x"]
[25,"HB runtime fan 1","高位运行时风机1"]
[26,"LB runtime compressor 1","低位运行时压缩机1","0..65536",null,null,"x","x"]
[27,"HB runtime compressor 1","高位运行时压缩机1"]
[28,"LB runtime humidifier 1","低位运行时加湿器1","0..65536",null,null,"x","x"]
[29,"HB runtime humidifier 1","高位运行时加湿器1"]
[30,"LB runtime pump 1 (reheat 1)","低位运行时泵1","0..65536",null,null,"x","x"]
[31,"HB runtime pump 1 (reheat 1)","高位运行时泵1"]
[32,"LB runtime pump 2 (reheat 2)","低位运行时泵2","0..65536",null,null,"x","x"]
[33,"HB runtime pump 2 (reheat 2)","高位运行时泵2"]
[null,"         -------------------------------------  d a t a    m o d u l e   4  数据模块4-----------------------------------------"]
[34,"LB runtime fan 1","低位运行时风机1","0..65536",null,null,"x","x"]
[35,"HB runtime fan 1","高位运行时风机1"]
[36,"LB runtime compressor 1","低位运行时压缩机1","0..65536",null,null,"x","x"]
[37,"HB runtime compressor 1","高位运行时压缩机1"]
[38,"LB runtime humidifier 1","低位运行时加湿器1","0..65536",null,null,"x","x"]
[39,"HB runtime humidifier 1","高位运行时加湿器1"]
[40,"LB runtime pump 1 (reheat 1)","低位运行时泵1","0..65536",null,null,"x","x"]
[41,"HB runtime pump 1 (reheat 1)","高位运行时泵1"]
[42,"LB runtime pump 2 (reheat 2)","低位运行时泵2","0..65536",null,null,"x","x"]
[43,"HB runtime pump 2 (reheat 2)","高位运行时泵2"]
[44,"LB checksum","低位校验","0..255",null,null,"x","x"]
[45,"HB checksum","高位校验","0..255",null,null,"x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 43."]
[null,"16位校验是2的补数,补数为从字节0到字节43的合计。"]

{"sheet":"10 控制器ID","index":9,"n_rows":45,"n_cols":8,"rows_kept":45,"flags":["formulas_cached_only"]}
[null,"Controller Identification "]
[null,"控制器ID"]
["Controller Identification  (PC -> MC)"]
["控制器ID(电脑->空调)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x"]
[1,"command id","命令ID",null,10,"x","x","x"]
[2,"number of following bytes","下面的字节数",null,2,"x","x","x"]
[3,"LB checksum","低位校验","0..255",null,"x","x","x"]
[4,"HB checksum","高位校验","0..255",null,"x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 2."]
[null,"16位校验是2的补数,补数为从字节0到字节2的合计。"]
[]
["Controller Identification (MC -> PC)"]
["控制器ID(空调->电脑)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x"]
[1,"command id","命令ID",null,10,"x","x","x"]
[2,"number of following bytes","下面的字节数",null,6,"x","x","x"]
[3,"software version","软件版本","0..255","0..255","x","x","x"]
[4,"hardware version","硬件版本","0..255","see table","x","x","x"]
[5,"reserved","预留",null,null,"x","x","x"]
[6,"unit type","单元类型","0..255","see table","x","x","x"]
[7,"LB checksum","低位校验","0..255",null,"x","x","x"]
[8,"HB checksum","高位校验","0..255",null,"x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 6."]
[null,"16位校验是2的补数,补数为从字节0到字节6的合计。"]
[]
["Value","Hardware Version"]
[0,"unknown type","未识别类型"]
[1,"STULZ C4000","斯图斯 C4000"]
[2,"STULZ C1001","斯图斯 C1001"]
[3,"STULZ C1002","斯图斯 C1002"]
[4,"STULZ C5000","斯图斯 C5000"]
[5,"not used"]
[6,"..."]
[]
[]
["Value","Unit Type"]
[0,"MC-only","只空调"]
[1,"DX (Compressor Unit)","DX(压缩机单元)"]
[2,"CW (Chilled Water Unit)","CW(冷冻水单元)"]
[3,"CH (Chiller)","CH(冷冻器)"]
[4,"not used","未用"]
[5,"..."]

{"sheet":"11 单元配置","index":10,"n_rows":67,"n_cols":8,"rows_kept":67,"flags":["formulas_cached_only"]}
[null,"Unit Configuration"]
[null,"单元配置"]
["Unit Configuration (PC -> MC)"]
["单元配置(电脑->空调)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x"]
[1,"command id","命令ID",null,11,"x","x","x"]
[2,"number of following bytes","下面的字节数",null,2,"x","x","x"]
[3,"LB checksum","低位校验","0..255",null,"x","x","x"]
[4,"HB checksum","高位校验","0..255",null,"x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 2."]
[null,"16位校验是2的补数,补数为从字节0到字节2的合计。"]
["Unit Configuration (MC -> PC)"]
["单元配置(空调->电脑)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x"]
[1,"command id","命令ID",null,11,"x","x","x"]
[2,"number of following bytes","下面的字节数",null,13,"x","x","x"]
[3,"number of modules","模块数量","0..8","0..8","x","x","x"]
[4,"LB configuration module 1","低位配置模块1","bit-coded","see table","x","x","x"]
[5,"HB configuration module 1","高位配置模块1","bit-coded","see table","x","x","x"]
[6,"LB configuration module 2","低位配置模块2","bit-coded","see table","x","x","x"]
[7,"HB configuration module 2","高位配置模块2","bit-coded","see table","x","x","x"]
[8,"LB configuration module 3","低位配置模块3","bit-coded","see table","x","x","x"]
[9,"HB configuration module 3","高位配置模块3","bit-coded","see table","x","x","x"]
[10,"LB configuration module 4","低位配置模块4","bit-coded","see table","x","x","x"]
[11,"HB configuration module 4","高位配置模块4","bit-coded","see table","x","x","x"]
[12,"general configuration byte 1","一般配置字节1","bit-coded","see table","x","x","x"]
[13,"general configuration byte 2 (not used)","一般配置字节2(未用)","bit-coded","see table","x","x","x"]
[14,"LB checksum","低位校验","0..255",null,"x","x","x"]
[15,"HB checksum","高位校验","0..255",null,"x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 13."]
[null,"16位校验是2的补数,补数为从字节0到字节13的合计。"]
[]
["Bit #","LB configuration module x 低位配置模块X",null,"POS","Value","C1001/2","C4000","C5000"]
[0,"reheat 1","加热器1","0x01","bit","x","x","x"]
[1,"reheat 2","加热器2","0x02","bit","x","x","x"]
[2,"reheat 3 / hotgas reheat","加热器3/热气加热器","0x04","bit",null,"x","x"]
[3,"glycol pump","乙二醇泵","0x08","bit",null,"x","x"]
[4,"drycooler","干冷器","0x10","bit",null,"x","x"]
[5,"compressor (1st stage)","压缩机(第1阶段)","0x20","bit","x","x","x"]
[6,"dehumidification","除湿","0x40","bit","x","x","x"]
[7,"humidification","加湿","0x80","bit","x","x","x"]
[null,"NOTE: bit set means component configured."]
[null,"注意：比特设置表示组件被配置"]
[]
["Bit #","HB configuration module x 高位配置模块X",null,"POS","Value","C1001/2","C4000","C5000"]
[0,"GE/CW valve","GE/CW阀门","0x01","bit","x","x","x"]
[1,"stand-by module","待机模块","0x02","bit",null,"x","x"]
[2,"compressor 2nd stage","压缩机第2阶段","0x04","bit",null,null,"x"]
[3,"not used","未用","0x08","bit"]
[4,"not used","未用","0x10","bit"]
[5,"not used","未用","0x20","bit"]
[6,"not used","未用","0x40","bit"]
[7,"not used","未用","0x80","bit"]
[null,"NOTE: bit set means component configured."]
[null,"注意：比特设置表示组件被配置"]
[]
["Bit #","General Configuration Byte 1 一般配置字节1",null,"POS","Value","C1001/2","C4000","C5000"]
[0,"0=controller, 1=supervisor","0=控制器，1=管理器","0x01","bit",null,"x","x"]
[1,"1=outside air sensor","1=室外空气传感器","0x02","bit",null,"x","x"]
[2,"control type: 0=return air, 1=supply air","控制器类型：0=回风，1=进风","0x04","bit",null,"x","x"]
[3,"temperature limited","温度限制","0x08","bit",null,"x"]
[4,"not used","未用","0x10","bit"]
[5,"not used","未用","0x20","bit"]
[6,"not used","未用","0x40","bit"]
[7,"not used","未用","0x80","bit"]

{"sheet":"C5000 增加项","index":11,"n_rows":78,"n_cols":8,"rows_kept":78,"flags":["formulas_cached_only"]}
[null,"C5000 Add On"]
[null,"C5000 增加项"]
["C5000 Add On (PC -> MC)"]
["C5000 增加项(电脑->空调)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x"]
[1,"command id","命令ID",null,12,"x","x","x"]
[2,"number of following bytes","下面的字节数",null,2,"x","x","x"]
[3,"LB checksum","低位校验","0..255",null,"x","x","x"]
[4,"HB checksum","高位校验","0..255",null,"x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 3."]
[null,"16位校验是2的补数,补数为从字节0到字节3的合计。"]
[]
["C5000 Add On (MC -> PC)"]
["C5000 增加项(空调->电脑)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",{"$nulls":3},"x"]
[1,"command id","命令ID",null,11,null,null,"x"]
[2,"number of following bytes","下面的字节数",null,13,null,null,"x"]
[3,"number of modules","模块数量","0..8","0..8",null,null,"x"]
[4,"LB configuration module 5","低位校验","bit-coded","see table",null,null,"x"]
[5,"HB configuration module 5","高位校验","bit-coded","see table",null,null,"x"]
[null,"         -------------------------------------  d a t a    m o d u l e   5  数据模块5-----------------------------------------"]
[6,"compressor start  (setpoint + val)","压缩机开始(设定点 +数值)","0.0..10.0 K","0..100",null,null,"x"]
[7,"compressor hysteresis","压缩机延迟","0.0..10.0 K","0..100",null,null,"x"]
[8,"suction valve start","吸引器阀门开始","0.0..10.0 K","0..100",null,null,"x"]
[9,"suction valve proportional band","吸引器阀门比例频率","0.0..10.0 K","0..100",null,null,"x"]
[10,"drycooler start temperature","干冷器开始温度","0..45°C","0..45",null,null,"x"]
[11,"reheat 1 start temperature","加热器1开始温度","0.0..10.0 K","0..100",null,null,"x"]
[12,"reheat 1 hysteresis","加热器1延迟","0.0..10.0 K","0..100",null,null,"x"]
[13,"reheat 2 start temperature","加热器2开始温度","0.0..10.0 K","0..100",null,null,"x"]
[14,"reheat 2 hysteresis","加热器2延迟","0.0..10.0 K","0..100",null,null,"x"]
[15,"reheat 3 start temperature","加热器3开始温度","0.0..10.0 K","0..100",null,null,"x"]
[16,"reheat 3 hysteresis","加热器3延迟","0.0..10.0 K","0..100",null,null,"x"]
[17,"dehumidification start","除湿开始","0..90%","0..90",null,null,"x"]
[18,"dehumidification hysteresis","除湿延迟","0..90%","0..90",null,null,"x"]
[19,"humidification start","加湿开始","0..90%","0..90",null,null,"x"]
[20,"humidification hysteresis","加湿延迟","0..90%","0..90",null,null,"x"]
{"$rows_empty":7}
["Bit #","LB configuration module x 低位配置模块 x",null,"POS","Value","C1001/2","C4000","C5000"]
[0,"reheat 1","加热器1","0x01","bit","x","x","x"]
[1,"reheat 2","加热器2","0x02","bit","x","x","x"]
[2,"reheat 3 / hotgas reheat","加热器3/热气加热","0x04","bit",null,"x","x"]
[3,"glycol pump","乙二醇泵","0x08","bit",null,"x","x"]
[4,"drycooler","干冷器","0x10","bit",null,"x","x"]
[5,"compressor (1st stage)","压缩机(第1阶段)","0x20","bit","x","x","x"]
[6,"dehumidification","除湿","0x40","bit","x","x","x"]
[7,"humidifikation","加湿","0x80","bit","x","x","x"]
[null,"NOTE: bit set means component configured."]
[]
[]
["Bit #","HB configuration module x 高位配置模块 x",null,"POS","Value","C1001/2","C4000","C5000"]
[0,"GE/CW valve","GE/CW阀门","0x01","bit","x","x","x"]
[1,"stand-by module","待机模块","0x02","bit",null,"x","x"]
[2,"compressor 2nd stage","压缩机第2阶段","0x04","bit",null,null,"x"]
[3,"not used","未用","0x08","bit"]
[4,"not used","未用","0x10","bit"]
[5,"not used","未用","0x20","bit"]
[6,"not used","未用","0x40","bit"]
[7,"not used","未用","0x80","bit"]
[null,"NOTE: bit set means component configured."]
[]
[]
["Bit #","General Configuration Byte 1 一般配置字节1",null,"POS","Value","C1001/2","C4000","C5000"]
[0,"0=controller, 1=supervisor","0=控制器，1=管理器","0x01","bit",null,"x","x"]
[1,"1=outside air sensor","1=室外空气传感器","0x02","bit",null,"x","x"]
[2,"control type: 0=return air, 1=supply air","控制器类型：0=回风，1=进风","0x04","bit",null,"x","x"]
[3,"temperature limited","温度限制","0x08","bit",null,"x"]
[4,"not used","未用","0x10","bit"]
[5,"not used","未用","0x20","bit"]
[6,"not used","未用","0x40","bit"]
[7,"not used","未用","0x80","bit"]

{"sheet":"16 令牌","index":12,"n_rows":15,"n_cols":8,"rows_kept":15,"flags":["formulas_cached_only"]}
[null,"Token Passing  (O.T.E.)"]
[null,"令牌传送(O.T.E.)"]
["Token Passing  [O.T.E.] (MC -> MC)"]
["令牌传送(O.T.E.)(空调->空调)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,null,"OTE"]
[1,"command id","命令ID",null,16,null,"OTE"]
[2,"number of following bytes","下面的字节数",null,3,null,"OTE"]
[3,"token 1=pass token, 0=acknowledge","令牌1=传送令牌，0=确认",{"$nulls":3},"OTE"]
[4,"LB checksum","低位校验","0..255",null,null,"OTE"]
[5,"HB checksum","高位校验","0..255",null,null,"OTE"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 3."]
[null,"Note: O.T.E. is a customized C4000 software."]
[null,"16位校验是2的补数,补数为从字节0到字节3的合计。"]
[null,"注意：O.T.E.是一个自定义C4000软件。"]

{"sheet":"1 长状态请求1","index":13,"n_rows":282,"n_cols":8,"rows_kept":282,"flags":["formulas_cached_only"]}
[null,"注意：C6000不使用长状态请求，C5000测试通过，C5000之前没测试"]
[null,"Long Status Request 1"]
[null,"长状态请求1"]
["Long Status Request (PC -> MC)"]
["长状态请求(电脑->空调)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x"]
[1,"command id","命令ID",null,1,"x","x","x"]
[2,"number of following bytes","下面的字节数",null,2,"x","x","x"]
[3,"LB checksum","低位校验","0..255",null,"x","x","x"]
[4,"HB checksum","高位校验","0..255",null,"x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 2."]
[null,"16位校验是2的补数,补数为从字节0到字节2的合计。"]
[]
["Long Status Request (MC -> PC)"]
["长状态请求(空调->电脑)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x"]
[1,"command id","命令ID",null,1,"x","x","x"]
[2,"number of following bytes","下面的字节数",null,137,"x","x","x"]
[3,"LB watertemperature -input-","低位 水温-输入-"," -50.0..+50.0 °C"," -500..+500",null,"x","x"]
[4,"HB       %","高位 %"]
[5,"LB return air temperature -input-","低位 回风温度-输入-","0.0..100.0°C","0..1000","x","x","x"]
[6,"HB       %","高位 %"]
[7,"LB supply air temperature -input-","低位 进风温度-输入-","0.0..100.0°C","0..1000",null,"x","x"]
[8,"HB       %","高位 %"]
[9,"LB return air humidity -input-","低位 回风湿度-输入-","0.0..100.0%","0..1000","x","x","x"]
[10,"HB       %","高位 %"]
[11,"LB supply air humidity -input-","低位 进风湿度-输入-","0.0..100.0%","0..1000",null,"x","x"]
[12,"HB       %","高位 %"]
[13,"LB outside air temperature -input-","低位 室外温度-输入-"," -50.0..+50.0 °C"," -500..+500",null,"x","x"]
[14,"HB       %","高位 %"]
[15,"LB outside air humidity -input-","低位 室外湿度-输入-","0.0..100.0%","0..1000",null,"x","x"]
[16,"HB       %","高位 %"]
[17,"temperature setpoint shift (±12.7°C)","温度设定点切换(±12.7°C)。","±127"," -127..+127",null,"x","x"]
[18,"humidity setpoint shift (±12.7%)","湿度设定点切换(±12.7%)。","±127"," -127..+127",null,"x","x"]
[19,"                    - reserved -","-保留-"]
[20,"                    - reserved -","-保留-"]
[21,"                    - reserved -","-保留-"]
[22,"modul 1 - 4 digital out compressor 2","模块1-4数字输出压缩机2","bit-coded","see table",null,null,"x"]
[23,"modul 1 - 4 digital in compressor 2","模块1-4数字输入压缩机2","bit-coded","see table",null,null,"x"]
[24,"SW-Version","SW-版本",{"$nulls":3},"x","x"]
[25,"module 1 digital out status byte 1","模块1数字输出状态字节1","bit-coded","see table","x","x","x"]
[26,"module 1 digital out status byte 2","模块1数字输出状态字节2","bit-coded","see table","x","x","x"]
[27,"module 2 digital out status byte 1","模块2数字输出状态字节1","bit-coded","see table","x","x","x"]
[28,"module 2 digital out status byte 2","模块2数字输出状态字节2","bit-coded","see table","x","x","x"]
[29,"module 3 digital out status byte 1","模块3数字输出状态字节1","bit-coded","see table",null,"x","x"]
[30,"module 3 digital out status byte 2","模块3数字输出状态字节2","bit-coded","see table",null,"x","x"]
[31,"module 4 digital out status byte 1","模块4数字输出状态字节1","bit-coded","see table",null,"x","x"]
[32,"module 4 digital out status byte 2","模块4数字输出状态字节2","bit-coded","see table",null,"x","x"]
[33,"module 1 digital in status byte 1","模块1数字输入状态字节1","bit-coded","see table","x","x","x"]
[34,"module 1 digital in status byte 2","模块1数字输入状态字节2","bit-coded","see table","x","x","x"]
[35,"module 2 digital in status byte 1","模块2数字输入状态字节1","bit-coded","see table","x","x","x"]
[36,"module 2 digital in status byte 2","模块2数字输入状态字节2","bit-coded","see table",null,"x","x"]
[37,"module 3 digital in status byte 1","模块3数字输入状态字节1","bit-coded","see table",null,"x","x"]
[38,"module 3 digital in status byte 2","模块3数字输入状态字节2","bit-coded","see table",null,"x","x"]
[39,"module 4 digital in status byte 1","模块4数字输入状态字节1","bit-coded","see table",null,"x","x"]
[40,"module 4 digital in status byte 2","模块4数字输入状态字节2","bit-coded","see table",null,"x","x"]
[41,"analogue out GE/CW valve (module 1)","模拟输出GE/CW阀门(模块1)","0-100%","0..255","x","x","x"]
[42,"analogue out PWW heating (module 1)","模拟输出PWW加热(模块1)","0-100%","0..255",null,"x","x"]
[43,"analogue out humidifier (module 1)","模拟输出加湿(模块1)","0-100%","0..255",null,"x","x"]
[44,"analogue out suction valve module 1","模拟输出吸引器阀门模块1","0-100%","0..255",null,"x","x"]
[45,"analogue out suction valve module 2","模拟输出吸引器阀门模块2","0-100%","0..255",null,"x","x"]
[46,"analogue out suction valve module 3","模拟输出吸引器阀门模块3","0-100%","0..255",null,"x","x"]
[47,"analogue out suction valve module 4","模拟输出吸引器阀门模块4","0-100%","0..255",null,"x","x"]
[48,"setpoint temperature","设置点温度","10.0-35.0°C","0..250","x","x","x"]
[49,"setpoint humidity","设置点湿度","10-90%","10..90","x","x","x"]
[50,"year","年","0..99","0..99",null,"x","x"]
[51,"month","月","1..12","1..12",null,"x","x"]
[52,"day","日","1..31","1..31",null,"x","x"]
[53,"hour","时","0..23","0..23",null,"x","x"]
[54,"minute","分","0..59","0..59",null,"x","x"]
[55,"return air temp. too high alarm","空调回风温度太高警报","0..30°C","0..30","x","x","x"]
[56,"supply air temp. too high alarm","空调进风温度太高警报","0..30°C","0..30",null,"x","x"]
[57,"return air temp. too low alarm","空调回风温度太低警报","0..30°C","0..30","x","x","x"]
[58,"supply air temp. too low alarm","空调进风温度太低警报","0..30°C","0..30",null,"x","x"]
[59,"water temp. too high alarm","水温太高警报","0..50°C","0..50",null,"x","x"]
[60,"water temp. too low alarm","水温太低警报"," -50..+30°C","0..80",null,"x","x"]
[61,"return air humid. too high alarm","空调回风湿度太高警报","0..90%","0..90","x","x","x"]
[62,"supply air humid. too high alarm","空调进风湿度太高警报","0..90%","0..90",null,"x","x"]
[63,"return air humid. too low alarm","空调回风湿度太低警报","0..90%","0..90","x","x","x"]
[64,"supply air humid. too low alarm","空调进风湿度太低警报","0..90%","0..90",null,"x","x"]
[null,"         -------------------------------------  d a t a    m o d u l e   1  数据模块1-----------------------------------------"]
[65,"compressor start  (setpoint + val)","压缩机开始(设定点 +数值)","0.0..10.0 K","0..100","x","x","x"]
[66,"compressor hysteresis","压缩机延迟","0.0..10.0 K","0..100","x","x","x"]
[67,"suction valve start","吸引器阀门开始","0.0..10.0 K","0..100",null,"x","x"]
[68,"suction valve proportional band","吸引器阀门比例频率","0.0..10.0 K","0..100",null,"x","x"]
[69,"drycooler start temperature","干冷器开始温度","0..45°C","0..45",null,"x","x"]
[70,"drycooler enable temperature","干冷器启用温度","0..45°C","0..45",null,"x"]
[71,"glycol-pump start temperature","乙二醇泵开始温度","0.0..10.0 K","0..100",null,"x","x"]
[72,"GE/CW valve off temperature","GE/CW阀门关闭温度","0..35°C","0..35",null,"x","x"]
[73,"GE/CW valve start temperature","GE/CW阀门开始温度","0.0..10.0 K","0..100","x","x","x"]
[74,"GE/CW valve proportional band","GE/CW阀门比例频率","0.0..10.0 K","0..100","x","x","x"]
[75,"reheat 1 start temperature","加热器1开始温度","0.0..10.0 K","0..100","x","x","x"]
[76,"reheat 1 hysteresis","加热器1延迟","0.0..10.0 K","0..100","x","x","x"]
[77,"reheat 2 start temperature","加热器2开始温度","0.0..10.0 K","0..100","x","x","x"]
[78,"reheat 2 hysteresis","加热器2延迟","0.0..10.0 K","0..100","x","x","x"]
[79,"reheat 3 start temperature","加热器3开始温度","0.0..10.0 K","0..100",null,"x","x"]
[80,"reheat 3 hysteresis","加热器3延迟","0.0..10.0 K","0..100",null,"x","x"]
[81,"PWW valve start temperature","PWW阀门开始温度","0.0..10.0 K","0..100",null,"x","x"]
[82,"PWW valve proportional band","PWW阀门比例频率","0.0..10.0 K","0..100",null,"x","x"]
[83,"dehumidification start","除湿开始","0..90%","0..90","x","x","x"]
[84,"dehumidification hysteresis","除湿延迟","0..90%","0..90","x","x","x"]
[85,"humidification start","加湿开始","0..90%","0..90","x","x","x"]
[86,"humidification hysteresis","加湿延迟","0..90%","0..90","x","x","x"]
[87,"humidification start (analogue)","加湿开始(模拟)","0..90%","0..90",null,"x","x"]
[88,"humidification proportional band (analogue)","加湿比例频率(模拟)","0..90%","0..90",null,"x","x"]
[null,"         -------------------------------------  d a t a    m o d u l e   2  数据模块2-----------------------------------------"]
[89,"compressor start  (setpoint + val)","压缩机开始(设定点 +数值)","0.0..10.0 K","0..100","x","x","x"]
[90,"compressor hysteresis","压缩机延迟","0.0..10.0 K","0..100","x","x","x"]
[91,"suction valve start","吸引器阀门开始","0.0..10.0 K","0..100",null,"x","x"]
[92,"suction valve proportional band","吸引器阀门比例频率","0.0..10.0 K","0..100",null,"x","x"]
[93,"drycooler start temperature","干冷器开始温度","0..45°C","0..45",null,"x","x"]
[94,"reheat 1 start temperature","加热器1开始温度","0.0..10.0 K","0..100","x","x","x"]
[95,"reheat 1 hysteresis","加热器1延迟","0.0..10.0 K","0..100","x","x","x"]
[96,"reheat 2 start temperature","加热器2开始温度","0.0..10.0 K","0..100","x","x","x"]
[97,"reheat 2 hysteresis","加热器2延迟","0.0..10.0 K","0..100","x","x","x"]
[98,"reheat 3 start temperature","加热器3开始温度","0.0..10.0 K","0..100",null,"x","x"]
[99,"reheat 3 hysteresis","加热器3延迟","0.0..10.0 K","0..100",null,"x","x"]
[100,"dehumidification start","除湿开始","0..90%","0..90","x","x","x"]
[101,"dehumidification hysteresis","除湿延迟","0..90%","0..90","x","x","x"]
[102,"humidification start","加湿开始","0..90%","0..90","x","x","x"]
[103,"humidification hysteresis","加湿延迟","0..90%","0..90","x","x","x"]
[null,"         -------------------------------------  d a t a    m o d u l e   3  数据模块3-----------------------------------------"]
[104,"compressor start  (setpoint + val)","压缩机开始(设定点 +数值)","0.0..10.0 K","0..100","x","x","x"]
[105,"compressor hysteresis","压缩机延迟","0.0..10.0 K","0..100","x","x","x"]
[106,"suction valve start","吸引器阀门开始","0.0..10.0 K","0..100",null,"x","x"]
[107,"suction valve proportional band","吸引器阀门比例频率","0.0..10.0 K","0..100",null,"x","x"]
[108,"drycooler start temperature","干冷器开始温度","0..45°C","0..45",null,"x","x"]
[109,"reheat 1 start temperature","加热器1开始温度","0.0..10.0 K","0..100","x","x","x"]
[110,"reheat 1 hysteresis","加热器1延迟","0.0..10.0 K","0..100","x","x","x"]
[111,"reheat 2 start temperature","加热器2开始温度","0.0..10.0 K","0..100","x","x","x"]
[112,"reheat 2 hysteresis","加热器2延迟","0.0..10.0 K","0..100","x","x","x"]
[113,"reheat 3 start temperature","加热器3开始温度","0.0..10.0 K","0..100",null,"x","x"]
[114,"reheat 3 hysteresis","加热器3延迟","0.0..10.0 K","0..100",null,"x","x"]
[115,"dehumidification start","除湿开始","0..90%","0..90","x","x","x"]
[116,"dehumidification hysteresis","除湿延迟","0..90%","0..90","x","x","x"]
[117,"humidification start","加湿开始","0..90%","0..90","x","x","x"]
[118,"humidification hysteresis","加湿延迟","0..90%","0..90","x","x","x"]
[null,"         -------------------------------------  d a t a    m o d u l e   4  数据模块4-----------------------------------------"]
[119,"compressor start  (setpoint + val)","压缩机开始(设定点 +数值)","0.0..10.0 K","0..100","x","x","x"]
[120,"compressor hysteresis","压缩机延迟","0.0..10.0 K","0..100","x","x","x"]
[121,"suction valve start","吸引器阀门开始","0.0..10.0 K","0..100",null,"x","x"]
[122,"suction valve proportional band","吸引器阀门比例频率","0.0..10.0 K","0..100",null,"x","x"]
[123,"drycooler start temperature","干冷器开始温度","0..45°C","0..45",null,"x","x"]
[124,"reheat 1 start temperature","加热器1开始温度","0.0..10.0 K","0..100","x","x","x"]
[125,"reheat 1 hysteresis","加热器1延迟","0.0..10.0 K","0..100","x","x","x"]
[126,"reheat 2 start temperature","加热器2开始温度","0.0..10.0 K","0..100","x","x","x"]
[127,"reheat 2 hysteresis","加热器2延迟","0.0..10.0 K","0..100","x","x","x"]
[128,"reheat 3 start temperature","加热器3开始温度","0.0..10.0 K","0..100",null,"x","x"]
[129,"reheat 3 hysteresis","加热器3延迟","0.0..10.0 K","0..100",null,"x","x"]
[130,"dehumidification start","除湿开始","0..90%","0..90","x","x","x"]
[131,"dehumidification hysteresis","除湿延迟","0..90%","0..90","x","x","x"]
[132,"humidification start","加湿开始","0..90%","0..90","x","x","x"]
[133,"humidification hysteresis","加湿延迟","0..90%","0..90","x","x","x"]
[null,"         -------------------------------------  g e n e r a l   d a t a   一般数据-----------------------------------------"]
[134,"general status byte 1","一般状态字节1","bit-coded","see table","x","x","x"]
[135,"general status byte 2","一般状态字节2","bit-coded","see table","x","x","x"]
[136,"error byte 1","错误字节1","bit-coded","see table","x","x","x"]
[137,"error byte 2","错误字节2","bit-coded","see table","x","x","x"]
[138,"LB checksum","低位校验","0..255",null,"x","x","x"]
[139,"HB checksum","高位校验","0..255",null,"x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 137."]
[null,"16位校验是2的补数,补数为从字节0到字节137的合计。"]
[]
[]
[]
[]
[]
["Bit #","General Status Byte 1 一般状态字节1",null,"POS","R / W","C1001/2","C4000","C5000"]
[0,"0 = PC-STOP (monitoring),  1 = on","0=电脑停止(监测)，1=开","0x01","R/W","x","x","x"]
[1,"0 = REMOTE STOP (contact),  1 = on","0=远程停止(干接点)，1=开","0x02","R","x","x","x"]
[2,"0 = LOCAL STOP (key),  1 = on","0=本地停止(键)，1=开","0x04","R","x","x","x"]
[3,"0 = TIMER-STOP (weekly oper.),  1 = on","0=时间计划停止(每周操作)，1=开","0x08","R",null,null,"x"]
[4,"not used ","未用","0x10","R"]
[5,"not used ","未用","0x20","R"]
[6,"not used ","未用","0x40","R"]
[7,"not used ","未用","0x80","R"]
[null,"NOTE: only if bits #0 to #3 are set to 1 the unit is in operation."]
[null,"If one of the bits #0,#1,#2,#3 is set to 0 the unit is in STOP condition."]
[null,"注意：如果比特#0-#3设置为1,那么单元在操作"]
[null,"如果比特#0、#1、#2或#3(其中一个)设置为0,那么单元在停止状态"]
[]
["Bit #","General Status Byte 2 一般状态字节2",null,"POS","R / W","C1001/2","C4000","C5000"]
[0,"not used ","未用","0x01","R"]
[1,"not used ","未用","0x02","R"]
[2,"not used ","未用","0x04","R"]
[3,"not used ","未用","0x08","R"]
[4,"not used ","未用","0x10","R"]
[5,"not used ","未用","0x20","R"]
[6,"not used ","未用","0x40","R"]
[7,"not used ","未用","0x80","R"]
[]
["Bit #","module 1 - 4 digital OUT compressor 2 模块1-4数字输出压缩机2",null,"POS","R / W","C1001/2","C4000","C5000"]
[0,"modul 1 compressor 2","模块1压缩机2","0x01","R",null,null,"x"]
[1,"modul 2 compressor 2","模块2压缩机2","0x02","R",null,null,"x"]
[2,"modul 3 compressor 2","模块3压缩机2","0x04","R",null,null,"x"]
[3,"modul 4 compressor 2","模块4压缩机2","0x08","R",null,null,"x"]
[4,"not used ","未用","0x10","R",null,null,"x"]
[5,"not used ","未用","0x20","R",null,null,"x"]
[6,"not used ","未用","0x40","R",null,null,"x"]
[7,"not used ","未用","0x80","R",null,null,"x"]
[null,"NOTE: if a bit is set to 1, than the corresponding component is in operation."]
[null,"注意：如果1个比特设置为1,那么相应组件在操作"]
["Bit #","module x digital OUT status byte 1","模块x数字输出状态字节1","POS","R / W","C1001/2","C4000","C5000"]
[0,"reheat 1","加热器1(C5000未用）","0x01","R","x","x","x"]
[1,"compressor","压缩机(C5000未用）","0x02","R","x","x","x"]
[2,"humidification","加湿器(C5000未测试不知道）","0x04","R","x","x","x"]
[3,"dehumidification","除湿器(C5000宇龙项目测试不正确）","0x08","R","x","x","x"]
[4,"fan","风机(C5000宇龙项目测试为制冷）","0x10","R","x","x","x"]
[5,"drycooler","干冷机(未测试不知道）","0x20","R",null,"x","x"]
[6,"alarm relays #1","警报继电器#1(C5000未用）","0x40","R","x","x","x"]
[7,"hot gas reheat / reheat 3","热风加热器/加热器3（C5000宇龙项目测试为电加热)","0x80","R",null,"x","x"]
[null,"NOTE: if a bit is set to 1, than the corresponding component is in operation."]
[null,"注意：如果1个比特设置为1,那么相应组件在操作"]
["Bit #","module x digital OUT status byte 2","模块x数字输出状态字节2","POS","R / W","C1001/2","C4000","C5000"]
[0,"reheat 2","加热器2(C5000未用）","0x01","R","x","x","x"]
[1,"glycol pump","乙二醇泵(C5000未用）","0x02","R",null,"x","x"]
[2,"louver (0=closed, 1=open)","通气窗(0=关，1=开)(C5000未用）","0x04","R","x","x","x"]
[3,"alarm relays #2","警报继电器#2(C5000未用）","0x08","R",null,"x","x"]
[4,"alarm relays #3","警报继电器#3(C5000未用）","0x10","R",null,"x"]
[5,"alarm relays #4","警报继电器#4(C5000未用）","0x20","R",null,"x"]
[6,"alarm relays #5","警报继电器#5(C5000未用）","0x40","R",null,"x"]
[7,"glycol pump 1 / 2 select","乙二醇泵1/2选择(C5000未用）","0x80","R",null,"x","x"]
[null,"NOTE: if a bit is set to 1, than the corresponding component is in operation."]
[null,"注意：如果1个比特设置为1,那么相应组件在操作"]
["Bit #","module 1 - 4 digital IN compressor 2","模块1-4数字输入压缩机2","POS","R / W","C1001/2","C4000","C5000"]
[0,"modul 1 compressor 2 low pressure","模块1压缩机2低压强","0x01","R",null,null,"x"]
[1,"modul 1 compressor 2 high pressure","模块1压缩机2高压强","0x02","R",null,null,"x"]
[2,"modul 2 compressor 2 low pressure","模块2压缩机2低压强","0x04","R",null,null,"x"]
[3,"modul 2 compressor 2 high pressure","模块2压缩机2高压强","0x08","R",null,null,"x"]
[4,"modul 3 compressor 2 low pressure","模块3压缩机2低压强","0x10","R",null,null,"x"]
[5,"modul 3 compressor 2 high pressure","模块3压缩机2高压强","0x20","R",null,null,"x"]
[6,"modul 4 compressor 2 low pressure","模块4压缩机2低压强","0x40","R",null,null,"x"]
[7,"modul 4 compressor 2 high pressure","模块4压缩机2高压强","0x80","R",null,null,"x"]
[null,"NOTE: if a bit is set to 1, than the corresponding alarm is active."]
[null,"注意：如果1个比特设置为1,那么相应警报正触发。"]
["Bit #","module x digital IN status byte 1","模块x数字输入状态字节1","POS","R / W","C1001/2","C4000","C5000"]
[0,"compressor low pressure","压缩机低压强","0x01","R","x","x","x"]
[1,"compressor high pressure","压缩机高压强","0x02","R","x","x","x"]
[2,"reheat 1 failure","加热器1失败","0x04","R","x","x","x"]
[3,"humidification failure","加湿器失败","0x08","R","x","x","x"]
[4,"air flow failure","空调流动失败","0x10","R","x","x","x"]
[5,"filter clogged","过滤器阻塞","0x20","R","x","x","x"]
[6,"aux. alarm #1","辅助警报#1","0x40","R","x","x","x"]
[7,"reheat 2 failure","加热器2失败","0x80","R","x","x","x"]
[null,"NOTE: if a bit is set to 1, than the corresponding alarm is active."]
[null,"注意：如果1个比特设置为1,那么相应警报正触发。"]
["Bit #","module x digital IN status byte 2","模块x数字输入状态字节2","POS","R / W","C1001/2","C4000","C5000"]
[0,"conductivity too high (< 5µS)","传导率太高 (< 5µS)","0x01","R",null,"x","x"]
[1,"ultrasonic failure","超声波失败","0x02","R",null,"x","x"]
[2,"glycol pump 1 failure","乙二醇泵1失败","0x04","R",null,"x","x"]
[3,"glycol pump 2 failure","乙二醇泵2失败","0x08","R",null,"x","x"]
[4,"drycooler failure","干冷机失败","0x10","R",null,"x","x"]
[5,"water detector","漏水检测","0x20","R","x","x"]
[6,"aux. alarm #2","辅助警报#2","0x40","R",null,"x","x"]
[7,"aux. alarm #3","辅助警报#3","0x80","R",null,"x","x"]
[null,"NOTE: if a bit is set to 1, than the corresponding alarm is active."]
[null,"注意：如果1个比特设置为1,那么相应警报正触发。"]
[]
["Bit #","error byte 1","错误字节1","POS","R / W","C1001/2","C4000","C5000"]
[0,"return air temp. too high alarm","回风温度太高警报","0x01","R","x","x","x"]
[1,"return air humid. too high alarm","回风湿度太高警报","0x02","R","x","x","x"]
[2,"supply air temp. too high alarm","进风温度太高警报","0x04","R",null,"x","x"]
[3,"supply air humid. too high alarm","进风湿度太高警报","0x08","R",null,"x","x"]
[4,"water temp. too high alarm","水温太高警报","0x10","R",null,"x","x"]
[5,"return air temp. too low alarm","回风温度太低警报","0x20","R","x","x","x"]
[6,"return air humid. too low alarm","回风湿度太低警报","0x40","R","x","x","x"]
[7,"supply air temp. too low alarm","进风温度太低警报","0x80","R",null,"x","x"]
[null,"NOTE: if a bit is set to 1, than the corresponding alarm is active."]
[null,"注意：如果1个比特设置为1,那么相应警报正触发。"]
["Bit #","error byte 2","错误字节2","POS","R / W","C1001/2","C4000","C5000"]
[0,"supply air humid. too low alarm","进风湿度太低警报","0x01","R",null,"x","x"]
[1,"water temp. too low alarm","水温太低警报","0x02","R",null,"x","x"]
[2,"supervisor failure","管理器失败","0x04","R",null,"x","x"]
[3,"freeze alarm","冻结警报","0x08","R",null,"x","x"]
[4,"fire / smoke detector","火灾/烟雾检测器","0x10","R","x","x","x"]
[5,"sensor failure","传感器失败","0x20","R","x","x","x"]
[6,"controller failure","控制器失败","0x40","R","x","x","x"]
[7,"IO-board transmission failure","IO传输失败","0x80","R",null,"x","x"]
[null,"NOTE: if a bit is set to 1, than the corresponding alarm is active."]
[null,"注意：如果1个比特设置为1,那么相应警报正触发。"]

{"sheet":"21 长状态请求2","index":14,"n_rows":387,"n_cols":9,"rows_kept":387,"flags":["formulas_cached_only"]}
[null,"注意：C5000不能使用长状态请求2，C6000已测试通过"]
[null,"Long Status Request (2)"]
[null,"长状态请求2"]
["Long Status Request (PC -> MC)"]
["长状态请求(电脑->空调)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000","C6000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x","x"]
[1,"command id","命令ID",null,33,"x","x","x","x"]
[2,"number of following bytes","下面的字节数",null,2,"x","x","x","x"]
[3,"LB checksum","低位校验","0..255",null,"x","x","x","x"]
[4,"HB checksum","高位校验","0..255",null,"x","x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 2."]
[null,"16位校验是2的补数,补数为从字节0到字节2的合计。"]
[]
["Long Status Request (MC -> PC)"]
["长状态请求(空调->电脑)"]
["Byte #","Description",null,"Range","Value","C1001/2","C4000","C5000","C6000"]
[0,"controller id","控制器ID","1..255",null,"x","x","x","x"]
[1,"command id","命令ID",null,33,"x","x","x","x"]
[2,"number of following bytes","下面的字节数",null,229,"x","x","x","x"]
[3,"LB watertemperature -input-","低位 水温-输入-"," -50.0..+50.0 °C"," -500..+500",null,"x","x","x"]
[4,"HB       %","高位 %"]
[5,"LB return air temperature -input-","低位 回风温度-输入-","0.0..100.0°C","0..1000","x","x","x","x"]
[6,"HB       %","高位 %"]
[7,"LB supply air temperature -input-","低位 进风温度-输入-","0.0..100.0°C","0..1000",null,"x","x","x"]
[8,"HB       %","高位 %"]
[9,"LB return air humidity -input-","低位 回风湿度-输入-","0.0..100.0%","0..1000","x","x","x","x"]
[10,"HB       %","高位 %"]
[11,"LB supply air humidity -input-","低位 进风湿度-输入-","0.0..100.0%","0..1000",null,"x","x","x"]
[12,"HB       %","高位 %"]
[13,"LB outside air temperature -input-","低位 室外温度-输入-"," -50.0..+50.0 °C"," -500..+500",null,"x","x","x"]
[14,"HB       %","高位 %"]
[15,"LB outside air humidity -input-","低位 室外湿度-输入-","0.0..100.0%","0..1000",null,"x","x","x"]
[16,"HB       %","高位 %"]
[17,"temperature setpoint shift (±12.7°C)","温度设定点切换(±12.7°C)。","±127"," -127..+127",null,"x","x","x"]
[18,"humidity setpoint shift (±12.7%)","湿度设定点切换(±12.7%)。","±127"," -127..+127",null,"x","x","x"]
[19,"                    - reserved -","-保留-"]
[20,"                    - reserved -","-保留-"]
[21,"                    - reserved -","-保留-"]
[22,"                    - reserved -","-保留-"]
[23,"                    - reserved -","-保留-"]
[24,"SW - Version","SW-版本",{"$nulls":3},"x","x","x"]
[25,"module 1 digital out status byte 1","模块1数字输出状态字节1","bit-coded","see table","x","x","x","x"]
[26,"module 1 digital out status byte 2","模块1数字输出状态字节2","bit-coded","see table","x","x","x","x"]
[27,"module 2 digital out status byte 1","模块2数字输出状态字节1","bit-coded","see table","x","x","x","x"]
[28,"module 2 digital out status byte 2","模块2数字输出状态字节2","bit-coded","see table","x","x","x","x"]
[29,"module 3 digital out status byte 1","模块3数字输出状态字节1","bit-coded","see table",null,"x","x","x"]
[30,"module 3 digital out status byte 2","模块3数字输出状态字节2","bit-coded","see table",null,"x","x","x"]
[31,"module 4 digital out status byte 1","模块4数字输出状态字节1","bit-coded","see table",null,"x","x","x"]
[32,"module 4 digital out status byte 2","模块4数字输出状态字节2","bit-coded","see table",null,"x","x","x"]
[33,"module 5 digital out status byte 1","模块5数字输出状态字节1","bit-coded","see table",{"$nulls":3},"x"]
[34,"module 5 digital out status byte 2","模块5数字输出状态字节2","bit-coded","see table",{"$nulls":3},"x"]
[35,"module 6 digital out status byte 1","模块6数字输出状态字节1","bit-coded","see table",{"$nulls":3},"x"]
[36,"module 6 digital out status byte 2","模块6数字输出状态字节2","bit-coded","see table",{"$nulls":3},"x"]
[37,"module 1 digital in status byte 1","模块1数字输入状态字节1","bit-coded","see table","x","x","x","x"]
[38,"module 1 digital in status byte 2","模块1数字输入状态字节2","bit-coded","see table","x","x","x","x"]
[39,"module 2 digital in status byte 1","模块2数字输入状态字节1","bit-coded","see table","x","x","x","x"]
[40,"module 2 digital in status byte 2","模块2数字输入状态字节2","bit-coded","see table",null,"x","x","x"]
[41,"module 3 digital in status byte 1","模块3数字输入状态字节1","bit-coded","see table",null,"x","x","x"]
[42,"module 3 digital in status byte 2","模块3数字输入状态字节2","bit-coded","see table",null,"x","x","x"]
[43,"module 4 digital in status byte 1","模块4数字输入状态字节1","bit-coded","see table",null,"x","x","x"]
[44,"module 4 digital in status byte 2","模块4数字输入状态字节2","bit-coded","see table",null,"x","x","x"]
[45,"module 5 digital in status byte 1","模块5数字输入状态字节1","bit-coded","see table",{"$nulls":3},"x"]
[46,"module 5 digital in status byte 2","模块5数字输入状态字节2","bit-coded","see table",{"$nulls":3},"x"]
[47,"module 6 digital in status byte 1","模块6数字输入状态字节1","bit-coded","see table",{"$nulls":3},"x"]
[48,"module 6 digital in status byte 2","模块6数字输入状态字节2","bit-coded","see table",{"$nulls":3},"x"]
[49,"module 1 analogue out GE/CW valve","模块1模拟输出GE/CW阀门","0-100%","0..255","x","x","x","x"]
[50,"module 2 analogue out GE/CW valve","模块2模拟输出GE/CW阀门","0-100%","0..255",null,null,"x","x"]
[51,"module 3 analogue out GE/CW valve","模块3模拟输出GE/CW阀门","0-100%","0..255",null,null,"x","x"]
[52,"module 4 analogue out GE/CW valve","模块4模拟输出GE/CW阀门","0-100%","0..255",null,null,"x","x"]
[53,"module 5 analogue out GE/CW valve","模块5模拟输出GE/CW阀门","0-100%","0..255",{"$nulls":3},"x"]
[54,"module 6 analogue out GE/CW valve","模块6模拟输出GE/CW阀门","0-100%","0..255",{"$nulls":3},"x"]
[55,"module 1 analogue out PWW heating","模块1模拟输出PWW加热","0-100%","0..255",null,"x","x","x"]
[56,"module 2 analogue out PWW heating","模块2模拟输出PWW加热","0-100%","0..255",null,null,"x","x"]
[57,"module 3 analogue out PWW heating","模块3模拟输出PWW加热","0-100%","0..255",null,null,"x","x"]
[58,"module 4 analogue out PWW heating","模块4模拟输出PWW加热","0-100%","0..255",null,null,"x","x"]
[59,"module 5 analogue out PWW heating","模块5模拟输出PWW加热","0-100%","0..255",{"$nulls":3},"x"]
[60,"module 6 analogue out PWW heating","模块6模拟输出PWW加热","0-100%","0..255",{"$nulls":3},"x"]
[61,"module 1 analogue out humidifier","模块1模拟输出加湿","0-100%","0..255",null,"x","x","x"]
[62,"module 2 analogue out humidifier","模块2模拟输出加湿","0-100%","0..255",null,null,"x","x"]
[63,"module 3 analogue out humidifier","模块3模拟输出加湿","0-100%","0..255",null,null,"x","x"]
[64,"module 4 analogue out humidifier","模块4模拟输出加湿","0-100%","0..255",null,null,"x","x"]
[65,"module 5 analogue out humidifier","模块5模拟输出加湿","0-100%","0..255",{"$nulls":3},"x"]
[66,"module 6 analogue out humidifier","模块6模拟输出加湿","0-100%","0..255",{"$nulls":3},"x"]
[67,"analogue out suction valve module 1","模块输出吸引器阀门模块1","0-100%","0..255",null,"x","x","x"]
[68,"analogue out suction valve module 2","模块输出吸引器阀门模块2","0-100%","0..255",null,"x","x","x"]
[69,"analogue out suction valve module 3","模块输出吸引器阀门模块3","0-100%","0..255",null,"x","x","x"]
[70,"analogue out suction valve module 4","模块输出吸引器阀门模块4","0-100%","0..255",null,"x","x","x"]
[71,"analogue out suction valve module 5","模块输出吸引器阀门模块5",{"$nulls":5},"x"]
[72,"analogue out suction valve module 6","模块输出吸引器阀门模块6",{"$nulls":5},"x"]
[73,"modul 1 - 6 digital out compressor 2","模块1-6数字输出压缩机2","bit-coded","see table",null,null,"x","x"]
[74,"modul 1 - 4 digital in compressor 2","模块1-4数字输入压缩机2","bit-coded","see table",null,null,"x","x"]
[75,"modul 5 - 6 digital in compressor 2","模块5-6数字输入压缩机2","bit-coded","see table",null,null,"x","x"]
[76,"                    - reserved -","预留"]
[77,"                    - reserved -","预留"]
[78,"                    - reserved -","预留"]
[79,"                    - reserved -","预留"]
[80,"                    - reserved -","预留"]
[81,"                    - reserved -","预留"]
[82,"                    - reserved -","预留"]
[83,"                    - reserved -","预留","-10 + 10","/10 + 10"]
[84,"setpoint temperature","设置点温度","10.0-35.0°C","0..250","x","x","x","x"]
[85,"setpoint humidity","设置点湿度","10-90%","10..90","x","x","x","x"]
[86,"year","年","0..99","0..99",null,"x","x","x"]
[87,"month","月","1..12","1..12",null,"x","x","x"]
[88,"day","日","1..31","1..31",null,"x","x","x"]
[89,"hour","时","0..23","0..23",null,"x","x","x"]
[90,"minute","分","0..59","0..59",null,"x","x","x"]
[91,"return air temp. too high alarm","回风温度太高警报","0..30°C","0..30","x","x","x","x"]
[92,"supply air temp. too high alarm","进风温度太高警报","0..30°C","0..30",null,"x","x","x"]
[93,"return air temp. too low alarm","回风温度太低警报","0..30°C","0..30","x","x","x","x"]
[94,"supply air temp. too low alarm","进风温度太低警报","0..30°C","0..30",null,"x","x","x"]
[95,"water temp. too high alarm","水温太高警报","0..50°C","0..50",null,"x","x","x"]
[96,"water temp. too low alarm","水温太低警报"," -50..+30°C","0..80",null,"x","x","x"]
[97,"return air humid. too high alarm","回风湿度太高警报","0..90%","0..90","x","x","x","x"]
[98,"supply air humid. too high alarm","进风湿度太高警报","0..90%","0..90",null,"x","x","x"]
[99,"return air humid. too low alarm","回风湿度太低警报","0..90%","0..90","x","x","x","x"]
[100,"supply air humid. too low alarm","进风湿度太低警报","0..90%","0..90",null,"x","x","x"]
[null," -------------------------------------  d a t a    m o d u l e   1  数据模块1-----------------------------------------"]
[101,"compressor start  (setpoint + val)","压缩机开始(设定点 +数值)","0.0..10.0 K","0..100","x","x","x","x"]
[102,"compressor hysteresis","压缩机延迟","0.0..10.0 K","0..100","x","x","x","x"]
[103,"suction valve start","吸引器阀门开始","0.0..10.0 K","0..100",null,"x","x","x"]
[104,"suction valve proportional band","吸引器阀门比例频率","0.0..10.0 K","0..100",null,"x","x","x"]
[105,"drycooler start temperature","干冷器开始温度","0..45°C","0..45",null,"x","x","x"]
[106,"drycooler enable temperature","干冷器启用温度","0..45°C","0..45",null,"x","x","x"]
[107,"glycol-pump start temperature","乙二醇泵开始温度","0.0..10.0 K","0..100",null,"x","x","x"]
[108,"GE/CW valve off temperature","GE/CW阀门关闭温度","0..35°C","0..35",null,"x","x","x"]
[109,"GE/CW valve start temperature","GE/CW阀门开始温度","0.0..10.0 K","0..100","x","x","x","x"]
[110,"GE/CW valve proportional band","GE/CW阀门比例频率","0.0..10.0 K","0..100","x","x","x","x"]
[111,"reheat 1 start temperature","加热器1开始温度","0.0..10.0 K","0..100","x","x","x","x"]
[112,"reheat 1 hysteresis","加热器1延迟","0.0..10.0 K","0..100","x","x","x","x"]
[113,"reheat 2 start temperature","加热器2开始温度","0.0..10.0 K","0..100","x","x","x","x"]
[114,"reheat 2 hysteresis","加热器2延迟","0.0..10.0 K","0..100","x","x","x","x"]
[115,"reheat 3 start temperature","加热器3开始温度","0.0..10.0 K","0..100",null,"x","x","x"]
[116,"reheat 3 hysteresis","加热器3延迟","0.0..10.0 K","0..100",null,"x","x","x"]
[117,"PWW valve start temperature","PWW阀门开始温度","0.0..10.0 K","0..100",null,"x","x","x"]
[118,"PWW valve proportional band","PWW阀门比例频率","0.0..10.0 K","0..100",null,"x","x","x"]
[119,"dehumidification start","除湿开始","0..90%","0..90","x","x","x","x"]
[120,"dehumidification hysteresis","除湿延迟","0..90%","0..90","x","x","x","x"]
[121,"humidification start","加湿开始","0..90%","0..90","x","x","x","x"]
[122,"humidification hysteresis","加湿延迟","0..90%","0..90","x","x","x","x"]
[123,"humidification start (analogue)","加湿开始(模拟)","0..90%","0..90",null,"x","x","x"]
[124,"humidification proportional band (analogue)","加湿比例频率(模拟)","0..90%","0..90",null,"x","x","x"]
[125,"                    - reserved -","预留"]
[null," -------------------------------------  d a t a    m o d u l e   2  数据模块2-----------------------------------------"]
[126,"compressor start  (setpoint + val)","压缩机开始(设定点 +数值)","0.0..10.0 K","0..100","x","x","x","x"]
[127,"compressor hysteresis","压缩机延迟","0.0..10.0 K","0..100","x","x","x","x"]
[128,"suction valve start","吸引器阀门开始","0.0..10.0 K","0..100",null,"x","x","x"]
[129,"suction valve proportional band","吸引器阀门比例频率","0.0..10.0 K","0..100",null,"x","x","x"]
[130,"drycooler start temperature","干冷器开始温度","0..45°C","0..45",null,"x","x","x"]
[131,"reheat 1 start temperature","加热器1开始温度","0.0..10.0 K","0..100","x","x","x","x"]
[132,"reheat 1 hysteresis","加热器1延迟","0.0..10.0 K","0..100","x","x","x","x"]
[133,"reheat 2 start temperature","加热器2开始温度","0.0..10.0 K","0..100","x","x","x","x"]
[134,"reheat 2 hysteresis","加热器2延迟","0.0..10.0 K","0..100","x","x","x","x"]
[135,"reheat 3 start temperature","加热器3开始温度","0.0..10.0 K","0..100",null,"x","x","x"]
[136,"reheat 3 hysteresis","加热器3延迟","0.0..10.0 K","0..100",null,"x","x","x"]
[137,"dehumidification start","除湿开始","0..90%","0..90","x","x","x","x"]
[138,"dehumidification hysteresis","除湿延迟","0..90%","0..90","x","x","x","x"]
[139,"humidification start","加湿开始","0..90%","0..90","x","x","x","x"]
[140,"humidification hysteresis","加湿延迟","0..90%","0..90","x","x","x","x"]
[141,"                    - reserved -","预留"]
[142,"                    - reserved -","预留"]
[143,"                    - reserved -","预留"]
[144,"                    - reserved -","预留"]
[145,"                    - reserved -","预留"]
[null," -------------------------------------  d a t a    m o d u l e   3  数据模块3-----------------------------------------"]
[146,"compressor start  (setpoint + val)","压缩机开始(设定点 +数值)","0.0..10.0 K","0..100","x","x","x","x"]
[147,"compressor hysteresis","压缩机延迟","0.0..10.0 K","0..100","x","x","x","x"]
[148,"suction valve start","吸引器阀门开始","0.0..10.0 K","0..100",null,"x","x","x"]
[149,"suction valve proportional band","吸引器阀门比例频率","0.0..10.0 K","0..100",null,"x","x","x"]
[150,"drycooler start temperature","干冷器开始温度","0..45°C","0..45",null,"x","x","x"]
[151,"reheat 1 start temperature","加热器1开始温度","0.0..10.0 K","0..100","x","x","x","x"]
[152,"reheat 1 hysteresis","加热器1延迟","0.0..10.0 K","0..100","x","x","x","x"]
[153,"reheat 2 start temperature","加热器2开始温度","0.0..10.0 K","0..100","x","x","x","x"]
[154,"reheat 2 hysteresis","加热器2延迟","0.0..10.0 K","0..100","x","x","x","x"]
[155,"reheat 3 start temperature","加热器3开始温度","0.0..10.0 K","0..100",null,"x","x","x"]
[156,"reheat 3 hysteresis","加热器3延迟","0.0..10.0 K","0..100",null,"x","x","x"]
[157,"dehumidification start","除湿开始","0..90%","0..90","x","x","x","x"]
[158,"dehumidification hysteresis","除湿延迟","0..90%","0..90","x","x","x","x"]
[159,"humidification start","加湿开始","0..90%","0..90","x","x","x","x"]
[160,"humidification hysteresis","加湿延迟","0..90%","0..90","x","x","x","x"]
[161,"                    - reserved -","预留"]
[162,"                    - reserved -","预留"]
[163,"                    - reserved -","预留"]
[164,"                    - reserved -","预留"]
[165,"                    - reserved -","预留"]
[null," -------------------------------------  d a t a    m o d u l e   4  数据模块4-----------------------------------------"]
[166,"compressor start  (setpoint + val)","压缩机开始(设定点 +数值)","0.0..10.0 K","0..100","x","x","x","x"]
[167,"compressor hysteresis","压缩机延迟","0.0..10.0 K","0..100","x","x","x","x"]
[168,"suction valve start","吸引器阀门开始","0.0..10.0 K","0..100",null,"x","x","x"]
[169,"suction valve proportional band","吸引器阀门比例频率","0.0..10.0 K","0..100",null,"x","x","x"]
[170,"drycooler start temperature","干冷器开始温度","0..45°C","0..45",null,"x","x","x"]
[171,"reheat 1 start temperature","加热器1开始温度","0.0..10.0 K","0..100","x","x","x","x"]
[172,"reheat 1 hysteresis","加热器1延迟","0.0..10.0 K","0..100","x","x","x","x"]
[173,"reheat 2 start temperature","加热器2开始温度","0.0..10.0 K","0..100","x","x","x","x"]
[174,"reheat 2 hysteresis","加热器2延迟","0.0..10.0 K","0..100","x","x","x","x"]
[175,"reheat 3 start temperature","加热器3开始温度","0.0..10.0 K","0..100",null,"x","x","x"]
[176,"reheat 3 hysteresis","加热器3延迟","0.0..10.0 K","0..100",null,"x","x","x"]
[177,"dehumidification start","除湿开始","0..90%","0..90","x","x","x","x"]
[178,"dehumidification hysteresis","除湿延迟","0..90%","0..90","x","x","x","x"]
[179,"humidification start","加湿开始","0..90%","0..90","x","x","x","x"]
[180,"humidification hysteresis","加湿延迟","0..90%","0..90","x","x","x","x"]
[181,"                    - reserved -","预留"]
[182,"                    - reserved -","预留"]
[183,"                    - reserved -","预留"]
[184,"                    - reserved -","预留"]
[185,"                    - reserved -","预留"]
[null," -------------------------------------  d a t a    m o d u l e   5  数据模块5-----------------------------------------"]
[186,"compressor start  (setpoint + val)","压缩机开始(设定点 +数值)","0.0..10.0 K","0..100","x","x","x","x"]
[187,"compressor hysteresis","压缩机延迟","0.0..10.0 K","0..100","x","x","x","x"]
[188,"suction valve start","吸引器阀门开始","0.0..10.0 K","0..100",null,"x","x","x"]
[189,"suction valve proportional band","吸引器阀门比例频率","0.0..10.0 K","0..100",null,"x","x","x"]
[190,"drycooler start temperature","干冷器开始温度","0..45°C","0..45",null,"x","x","x"]
[191,"reheat 1 start temperature","加热器1开始温度","0.0..10.0 K","0..100","x","x","x","x"]
[192,"reheat 1 hysteresis","加热器1延迟","0.0..10.0 K","0..100","x","x","x","x"]
[193,"reheat 2 start temperature","加热器2开始温度","0.0..10.0 K","0..100","x","x","x","x"]
[194,"reheat 2 hysteresis","加热器2延迟","0.0..10.0 K","0..100","x","x","x","x"]
[195,"reheat 3 start temperature","加热器3开始温度","0.0..10.0 K","0..100",null,"x","x","x"]
[196,"reheat 3 hysteresis","加热器3延迟","0.0..10.0 K","0..100",null,"x","x","x"]
[197,"dehumidification start","除湿开始","0..90%","0..90","x","x","x","x"]
[198,"dehumidification hysteresis","除湿延迟","0..90%","0..90","x","x","x","x"]
[199,"humidification start","加湿开始","0..90%","0..90","x","x","x","x"]
[200,"humidification hysteresis","加湿延迟","0..90%","0..90","x","x","x","x"]
[201,"                    - reserved -","预留"]
[202,"                    - reserved -","预留"]
[203,"                    - reserved -","预留"]
[204,"                    - reserved -","预留"]
[205,"                    - reserved -","预留"]
[null," -------------------------------------  d a t a    m o d u l e   6  数据模块6-----------------------------------------"]
[206,"compressor start  (setpoint + val)","压缩机开始(设定点 +数值)","0.0..10.0 K","0..100","x","x","x","x"]
[207,"compressor hysteresis","压缩机延迟","0.0..10.0 K","0..100","x","x","x","x"]
[208,"suction valve start","吸引器阀门开始","0.0..10.0 K","0..100",null,"x","x","x"]
[209,"suction valve proportional band","吸引器阀门比例频率","0.0..10.0 K","0..100",null,"x","x","x"]
[210,"drycooler start temperature","干冷器开始温度","0..45°C","0..45",null,"x","x","x"]
[211,"reheat 1 start temperature","加热器1开始温度","0.0..10.0 K","0..100","x","x","x","x"]
[212,"reheat 1 hysteresis","加热器1延迟","0.0..10.0 K","0..100","x","x","x","x"]
[213,"reheat 2 start temperature","加热器2开始温度","0.0..10.0 K","0..100","x","x","x","x"]
[214,"reheat 2 hysteresis","加热器2延迟","0.0..10.0 K","0..100","x","x","x","x"]
[215,"reheat 3 start temperature","加热器3开始温度","0.0..10.0 K","0..100",null,"x","x","x"]
[216,"reheat 3 hysteresis","加热器3延迟","0.0..10.0 K","0..100",null,"x","x","x"]
[217,"dehumidification start","除湿开始","0..90%","0..90","x","x","x","x"]
[218,"dehumidification hysteresis","除湿延迟","0..90%","0..90","x","x","x","x"]
[219,"humidification start","加湿开始","0..90%","0..90","x","x","x","x"]
[220,"humidification hysteresis","加湿延迟","0..90%","0..90","x","x","x","x"]
[221,"                    - reserved -","预留"]
[222,"                    - reserved -","预留"]
[223,"                    - reserved -","预留"]
[224,"                    - reserved -","预留"]
[225,"                    - reserved -","预留"]
[null," -------------------------------------  g e n e r a l   d a t a   一般数据-----------------------------------------"]
[226,"general status byte 1","一般状态字节1","bit-coded","see table","x","x","x","x"]
[227,"general status byte 2","一般状态字节2","bit-coded","see table","x","x","x","x"]
[228,"error byte 1","错误字节1","bit-coded","see table","x","x","x","x"]
[229,"error byte 2","错误字节2","bit-coded","see table","x","x","x","x"]
[230,"LB checksum","低位校验","0..255",null,"x","x","x","x"]
[231,"HB checksum","高位校验","0..255",null,"x","x","x","x"]
[null,"The 16 bit checksum is the 2's complement of the sum from byte 0 to byte 137."]
[null,"16位校验是2的补数,补数为从字节0到字节137的合计。"]
[]
[]
[]
[]
[]
["Bit #","General Status Byte 1","一般状态字节1","POS","R / W","C1001/2","C4000","C5000","C6000"]
[0,"0 = PC-STOP (monitoring),  1 = on","0=电脑停止(监测)，1=开","0x01","R/W","x","x","x","x"]
[1,"0 = REMOTE STOP (contact),  1 = on","0=远程停止(干接点)，1=开","0x02","R","x","x","x","x"]
[2,"0 = LOCAL STOP (key),  1 = on","0=本地停止(键)，1=开","0x04","R","x","x","x","x"]
[3,"0 = TIMER-STOP (weekly oper.),  1 = on","0=时间计划停止(每周操作)，1=开","0x08","R",null,null,"x","x"]
[4,"not used ","未用","0x10","R"]
[5,"not used ","未用","0x20","R"]
[6,"not used ","未用","0x40","R"]
[7,"not used ","未用","0x80","R"]
[null,"NOTE: only if bits #0 to #3 are set to 1 the unit is in operation."]
[null,"If one of the bits #0,#1,#2,#3 is set to 0 the unit is in STOP condition."]
[null,"注意：如果比特#0-#3设置为1,那么单元在操作"]
[null,"如果比特#0、#1、#2或#3(其中一个)设置为0,那么单元在停止状态"]
[]
["Bit #","General Status Byte 2","一般状态字节2","POS","R / W","C1001/2","C4000","C5000","C6000"]
[0,"not used ","未用","0x01","R"]
[1,"not used ","未用","0x02","R"]
[2,"not used ","未用","0x04","R"]
[3,"not used ","未用","0x08","R"]
[4,"not used ","未用","0x10","R"]
[5,"not used ","未用","0x20","R"]
[6,"not used ","未用","0x40","R"]
[7,"not used ","未用","0x80","R"]
[]
["Bit #","module 1 - 6 digital OUT compressor 2","模块1-6数字输出压缩机2","POS","R / W","C1001/2","C4000","C5000","C6000"]
[0,"modul 1 compressor 2","模块1压缩机2","0x01","R",null,null,"x","x"]
[1,"modul 2 compressor 2","模块2压缩机2","0x02","R",null,null,"x","x"]
[2,"modul 3 compressor 2","模块3压缩机2","0x04","R",null,null,"x","x"]
[3,"modul 4 compressor 2","模块4压缩机2","0x08","R",null,null,"x","x"]
[4,"modul 5 compressor 2","模块5压缩机2","0x10","R",null,null,"x","x"]
[5,"modul 6 compressor 2","模块6压缩机2","0x20","R",null,null,"x","x"]
[6,"not used ","未用","0x40","R",null,null,"x","x"]
[7,"not used ","未用","0x80","R",null,null,"x","x"]
[null,"NOTE: if a bit is set to 1, than the corresponding component is in operation."]
[null,"注意：如果1个比特设置为1,那么相应组件在操作"]
["Bit #","module x digital OUT status byte 1","模块x数字输出状态字节1","POS","R / W","C1001/2","C4000","C5000","C6000"]
[0,"reheat 1","加热器1","0x01","R","x","x","x","x"]
[1,"compressor","压缩机","0x02","R","x","x","x","x"]
[2,"humidification","加湿器","0x04","R","x","x","x","x"]
[3,"dehumidification","除湿器","0x08","R","x","x","x","x"]
[4,"fan","风机","0x10","R","x","x","x","x"]
[5,"drycooler","干冷机","0x20","R",null,"x","x","x"]
[6,"alarm relays #1","警报继电器#1","0x40","R","x","x","x","x"]
[7,"hot gas reheat / reheat 3","热风加热器/加热器3","0x80","R",null,"x","x","x"]
[null,"NOTE: if a bit is set to 1, than the corresponding component is in operation."]
[null,"注意：如果1个比特设置为1,那么相应组件在操作"]
["Bit #","module x digital OUT status byte 2","模块x数字输出状态字节2","POS","R / W","C1001/2","C4000","C5000","C6000"]
[0,"reheat 2","加热器2","0x01","R","x","x","x","x"]
[1,"glycol pump","乙二醇泵","0x02","R",null,"x","x","x"]
[2,"louver (0=closed, 1=open)","通气窗(0=关，1=开)","0x04","R","x","x","x","x"]
[3,"alarm relays #2","警报继电器#2","0x08","R",null,"x","x","x"]
[4,"alarm relays #3","警报继电器#3","0x10","R",null,"x"]
[5,"alarm relays #4","警报继电器#4","0x20","R",null,"x"]
[6,"alarm relays #5","警报继电器#5","0x40","R",null,"x"]
[7,"glycol pump 1 / 2 select","乙二醇泵1/2选择","0x80","R",null,"x","x","x"]
[null,"NOTE: if a bit is set to 1, than the corresponding component is in operation."]
[null,"注意：如果1个比特设置为1,那么相应组件在操作"]
["Bit #","module 1 - 4 digital IN compressor 2","模块1-4数字输入压缩机2","POS","R / W","C1001/2","C4000","C5000","C6000"]
[0,"modul 1 compressor 2 low pressure","模块1压缩机2低压强","0x01","R",null,null,"x","x"]
[1,"modul 1 compressor 2 high pressure","模块1压缩机2高压强","0x02","R",null,null,"x","x"]
[2,"modul 2 compressor 2 low pressure","模块2压缩机2低压强","0x04","R",null,null,"x","x"]
[3,"modul 2 compressor 2 high pressure","模块2压缩机2高压强","0x08","R",null,null,"x","x"]
[4,"modul 3 compressor 2 low pressure","模块3压缩机2低压强","0x10","R",null,null,"x","x"]
[5,"modul 3 compressor 2 high pressure","模块3压缩机2高压强","0x20","R",null,null,"x","x"]
[6,"modul 4 compressor 2 low pressure","模块4压缩机2低压强","0x40","R",null,null,"x","x"]
[7,"modul 4 compressor 2 high pressure","模块4压缩机2高压强","0x80","R",null,null,"x","x"]
[null,"NOTE: if a bit is set to 1, than the corresponding alarm is active."]
[null,"注意：如果1个比特设置为1,那么相应警报正触发。"]
["Bit #","module 5 - 6 digital IN compressor 2","模块5-6数字输入压缩机2","POS","R / W","C1001/2","C4000","C5000","C6000"]
[0,"modul 5 compressor 2 low pressure","模块5压缩机2低压强","0x01","R",null,null,"x","x"]
[1,"modul 5 compressor 2 high pressure","模块5压缩机2高压强","0x02","R",null,null,"x","x"]
[2,"modul 6 compressor 2 low pressure","模块6压缩机2低压强","0x04","R",null,null,"x","x"]
[3,"modul 6 compressor 2 high pressure","模块6压缩机2高压强","0x08","R",null,null,"x","x"]
[4,"not used ","未用","0x10","R"]
[5,"not used ","未用","0x20","R"]
[6,"not used ","未用","0x40","R"]
[7,"not used ","未用","0x80","R"]
[null,"NOTE: if a bit is set to 1, than the corresponding alarm is active."]
[null,"注意：如果1个比特设置为1,那么相应警报正触发。"]
["Bit #","module x digital IN status byte 1","模块x数字输入状态字节1","POS","R / W","C1001/2","C4000","C5000","C6000"]
[0,"compressor low pressure","压缩机低压强","0x01","R","x","x","x","x"]
[1,"compressor high pressure","压缩机高压强","0x02","R","x","x","x","x"]
[2,"reheat 1 failure","加热器1失败","0x04","R","x","x","x","x"]
[3,"humidification failure","加湿器失败","0x08","R","x","x","x","x"]
[4,"air flow failure","空调流动失败","0x10","R","x","x","x","x"]
[5,"filter clogged","过滤器阻塞","0x20","R","x","x","x","x"]
[6,"aux. alarm #1","辅助警报#1","0x40","R","x","x","x","x"]
[7,"reheat 2 failure","加热器2失败","0x80","R","x","x","x","x"]
[null,"NOTE: if a bit is set to 1, than the corresponding alarm is active."]
[null,"注意：如果1个比特设置为1,那么相应警报正触发。"]
["Bit #","module x digital IN status byte 2","模块x数字输入状态字节2","POS","R / W","C1001/2","C4000","C5000","C6000"]
[0,"conductivity too high (< 5µS)","传导率太高 (< 5µS)","0x01","R",null,"x","x","x"]
[1,"ultrasonic failure","超声波失败","0x02","R",null,"x","x","x"]
[2,"glycol pump 1 failure","乙二醇泵1失败","0x04","R",null,"x","x","x"]
[3,"glycol pump 2 failure","乙二醇泵2失败","0x08","R",null,"x","x","x"]
[4,"drycooler failure","干冷机失败","0x10","R",null,"x","x","x"]
[5,"water detector","漏水检测","0x20","R","x","x","x","x"]
[6,"aux. alarm #2","辅助警报#2","0x40","R",null,"x","x","x"]
[7,"aux. alarm #3","辅助警报#3","0x80","R",null,"x","x","x"]
[null,"NOTE: if a bit is set to 1, than the corresponding alarm is active."]
[null,"注意：如果1个比特设置为1,那么相应警报正触发。"]
[]
["Bit #","error byte 1","错误字节1","POS","R / W","C1001/2","C4000","C5000","C6000"]
[0,"return air temp. too high alarm","回风温度太高警报","0x01","R","x","x","x","x"]
[1,"return air humid. too high alarm","回风湿度太高警报","0x02","R","x","x","x","x"]
[2,"supply air temp. too high alarm","进风温度太高警报","0x04","R",null,"x","x","x"]
[3,"supply air humid. too high alarm","进风湿度太高警报","0x08","R",null,"x","x","x"]
[4,"water temp. too high alarm","水温太高警报","0x10","R",null,"x","x","x"]
[5,"return air temp. too low alarm","回风温度太低警报","0x20","R","x","x","x","x"]
[6,"return air humid. too low alarm","回风湿度太低警报","0x40","R","x","x","x","x"]
[7,"supply air temp. too low alarm","进风温度太低警报","0x80","R",null,"x","x","x"]
[null,"NOTE: if a bit is set to 1, than the corresponding alarm is active."]
[null,"注意：如果1个比特设置为1,那么相应警报正触发。"]
["Bit #","error byte 2","错误字节2","POS","R / W","C1001/2","C4000","C5000","C6000"]
[0,"supply air humid. too low alarm","进风湿度太低警报","0x01","R",null,"x","x","x"]
[1,"water temp. too low alarm","水温太低警报","0x02","R",null,"x","x","x"]
[2,"supervisor failure","管理器失败","0x04","R",null,"x","x","x"]
[3,"freeze alarm","冻结警报","0x08","R",null,"x","x","x"]
[4,"fire / smoke detector","火灾/烟雾检测器","0x10","R","x","x","x","x"]
[5,"sensor failure","传感器失败","0x20","R","x","x","x","x"]
[6,"controller failure","控制器失败","0x40","R","x","x","x","x"]
[7,"IO-board transmission failure","IO传输失败","0x80","R",null,"x","x","x"]
[null,"NOTE: if a bit is set to 1, than the corresponding alarm is active."]
[null,"注意：如果1个比特设置为1,那么相应警报正触发。"]