{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["变量dat文件","CSpreadSheetBackup"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":39,"n_cols":76,"rows_kept":39,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","6.7.92.3","Stulz7000_1_UnitSwitchStatus","2号空调 开关状态","1","1","1","1","1013",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","6.7.92.3","Stulz7000_1_UnitTemperature","2号空调 单元温度","101","4","2","4","2340",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.7.92.3","Stulz7000_1_UnitHumidity","2号空调 单元湿度","101","4","2","4","2342",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.7.92.3","Stulz7000_1_UnitSetTemperatureDay","2号空调 白天设置温度","101","4","2","4","2346",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.7.92.3","Stulz7000_1_UnitSetTemperatureNight","2号空调 夜晚设置温度","101","4","2","4","2348",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.7.92.3","Stulz7000_1_UnitSetHumidity","2号空调 设置湿度","101","4","2","4","2352",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.7.92.3","Stulz7000_1_AirFlow1Alarm","2号空调 空气流1故障","1","1","1","1","8500",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["8","6.7.92.3","Stulz7000_1_AirFlow2Alarm","2号空调 空气流2故障","1","1","1","1","8501",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["9","6.7.92.3","Stulz7000_1_AirFlow3Alarm","2号空调 空气流3故障","1","1","1","1","8502",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["10","6.7.92.3","Stulz7000_1_ReturnairTempToohighAlarm","2号空调 回风温度过高报警","1","1","1","1","8508",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["11","6.7.92.3","Stulz7000_1_ReturnairHumidToohighAlarm","2号空调 回风湿度过高报警","1","1","1","1","8509",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["12","6.7.92.3","Stulz7000_1_WaterTempToohighAlarm","2号空调 水温过高报警","1","1","1","1","8512",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["13","6.7.92.3","Stulz7000_1_ReturnairTempToolowAlarm","2号空调 回风温度过低报警","1","1","1","1","8513",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["14","6.7.92.3","Stulz7000_1_ReturnairhumidToolowAlarm","2号空调 回风湿度过低报警","1","1","1","1","8514",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["14","6.7.92.3","Stulz7000_1_WaterTempTooLowAlarm","2号空调 水温过低报警","1","1","1","1","8517",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["15","6.7.92.3","Stulz7000_1_Comp1HpAlarm","2号空调 压缩机1高压报警","1","1","1","1","8560",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["16","6.7.92.3","Stulz7000_1_Comp2HpAlarm","2号空调 压缩机2高压报警","1","1","1","1","8561",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["17","6.7.92.3","Stulz7000_1_Comp1LpAlarm","2号空调 压缩机1低压报警","1","1","1","1","8562",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["18","6.7.92.3","Stulz7000_1_Comp2LpAlarm","2号空调 压缩机2低压报警","1","1","1","1","8563",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["19","6.7.92.3","Stulz7000_1_ElecHeat1Alarm","2号空调 电加热器1故障","1","1","1","1","8564",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["20","6.7.92.3","Stulz7000_1_ElecHeat2Alarm","2号空调 电加热器2故障","1","1","1","1","8565",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["21","6.7.92.3","Stulz7000_1_ElecHeat3Alarm","2号空调 电加热器3故障","1","1","1","1","8566",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["22","6.7.92.3","Stulz7000_1_ElecHeat4Alarm","2号空调 电加热器4故障","1","1","1","1","8567",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["23","6.7.92.3","Stulz7000_1_Drycooler1Alarm","2号空调 干式冷却器1故障","1","1","1","1","8568",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["24","6.7.92.3","Stulz7000_1_Drycooler2Alarm","2号空调 干式冷却器2故障","1","1","1","1","8569",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["25","6.7.92.3","Stulz7000_1_Drycooler3Alarm","2号空调 干式冷却器3故障","1","1","1","1","8570",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["26","6.7.92.3","Stulz7000_1_Drycooler4Alarm","2号空调 干式冷却器4故障","1","1","1","1","8571",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["27","6.7.92.3","Stulz7000_1_GlycolPump1Alarm","2号空调 乙二醇泵1故障","1","1","1","1","8572",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["28","6.7.92.3","Stulz7000_1_GlycolPump2Alarm","2号空调 乙二醇泵2故障","1","1","1","1","8573",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["29","6.7.92.3","Stulz7000_1_GlycolPump3Alarm","2号空调 乙二醇泵3故障","1","1","1","1","8574",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["30","6.7.92.3","Stulz7000_1_GlycolPump4Alarm","2号空调 乙二醇泵4故障","1","1","1","1","8575",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["31","6.7.92.3","Stulz7000_1_Humidification1Alarm","2号空调 加湿器1故障","1","1","1","1","8576",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["32","6.7.92.3","Stulz7000_1_Humidification2Alarm","2号空调 加湿器2故障","1","1","1","1","8577",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["33","6.7.92.3","Stulz7000_1_Humidification3Alarm","2号空调 加湿器3故障","1","1","1","1","8588",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["34","6.7.92.3","Stulz7000_1_FanFilter1Alarm","2号空调 风扇过滤网1故障","1","1","1","1","8589",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["35","6.7.92.3","Stulz7000_1_FanFilter2Alarm","2号空调 风扇过滤网2故障","1","1","1","1","8590",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["36","6.7.92.3","Stulz7000_1_FanFilter3Alarm","2号空调 风扇过滤网3故障","1","1","1","1","8591",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["1","6.7.92.3","Stulz7000_1_Communications","2号空调 通信状态","1000","0","0","1","0","","","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断开,"]

{"sheet":"CSpreadSheetBackup","index":1,"n_rows":39,"n_cols":76,"rows_kept":39,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","6.7.92.3","Stulz7000_1_UnitSwitchStatus","2号空调 开关状态","1","1","1","1","1013",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","6.7.92.3","Stulz7000_1_UnitTemperature","2号空调 单元温度","101","4","2","4","2340",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","6.7.92.3","Stulz7000_1_UnitHumidity","2号空调 单元湿度","101","4","2","4","2342",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","6.7.92.3","Stulz7000_1_UnitSetTemperatureDay","2号空调 白天设置温度","101","4","2","4","2346",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","6.7.92.3","Stulz7000_1_UnitSetTemperatureNight","2号空调 夜晚设置温度","101","4","2","4","2348",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","6.7.92.3","Stulz7000_1_UnitSetHumidity","2号空调 设置湿度","101","4","2","4","2352",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","6.7.92.3","Stulz7000_1_AirFlow1Alarm","2号空调 空气流1故障","1","1","1","1","8500",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["8","6.7.92.3","Stulz7000_1_AirFlow2Alarm","2号空调 空气流2故障","1","1","1","1","8501",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["9","6.7.92.3","Stulz7000_1_AirFlow3Alarm","2号空调 空气流3故障","1","1","1","1","8502",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["10","6.7.92.3","Stulz7000_1_ReturnairTempToohighAlarm","2号空调 回风温度过高报警","1","1","1","1","8508",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["11","6.7.92.3","Stulz7000_1_ReturnairHumidToohighAlarm","2号空调 回风湿度过高报警","1","1","1","1","8509",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["12","6.7.92.3","Stulz7000_1_WaterTempToohighAlarm","2号空调 水温过高报警","1","1","1","1","8512",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["13","6.7.92.3","Stulz7000_1_ReturnairTempToolowAlarm","2号空调 回风温度过低报警","1","1","1","1","8513",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["14","6.7.92.3","Stulz7000_1_ReturnairhumidToolowAlarm","2号空调 回风湿度过低报警","1","1","1","1","8514",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["14","6.7.92.3","Stulz7000_1_WaterTempTooLowAlarm","2号空调 水温过低报警","1","1","1","1","8517",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["15","6.7.92.3","Stulz7000_1_Comp1HpAlarm","2号空调 压缩机1高压报警","1","1","1","1","8560",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["16","6.7.92.3","Stulz7000_1_Comp2HpAlarm","2号空调 压缩机2高压报警","1","1","1","1","8561",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["17","6.7.92.3","Stulz7000_1_Comp1LpAlarm","2号空调 压缩机1低压报警","1","1","1","1","8562",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["18","6.7.92.3","Stulz7000_1_Comp2LpAlarm","2号空调 压缩机2低压报警","1","1","1","1","8563",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["19","6.7.92.3","Stulz7000_1_ElecHeat1Alarm","2号空调 电加热器1故障","1","1","1","1","8564",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["20","6.7.92.3","Stulz7000_1_ElecHeat2Alarm","2号空调 电加热器2故障","1","1","1","1","8565",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["21","6.7.92.3","Stulz7000_1_ElecHeat3Alarm","2号空调 电加热器3故障","1","1","1","1","8566",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["22","6.7.92.3","Stulz7000_1_ElecHeat4Alarm","2号空调 电加热器4故障","1","1","1","1","8567",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["23","6.7.92.3","Stulz7000_1_Drycooler1Alarm","2号空调 干式冷却器1故障","1","1","1","1","8568",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["24","6.7.92.3","Stulz7000_1_Drycooler2Alarm","2号空调 干式冷却器2故障","1","1","1","1","8569",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["25","6.7.92.3","Stulz7000_1_Drycooler3Alarm","2号空调 干式冷却器3故障","1","1","1","1","8570",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["26","6.7.92.3","Stulz7000_1_Drycooler4Alarm","2号空调 干式冷却器4故障","1","1","1","1","8571",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["27","6.7.92.3","Stulz7000_1_GlycolPump1Alarm","2号空调 乙二醇泵1故障","1","1","1","1","8572",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["28","6.7.92.3","Stulz7000_1_GlycolPump2Alarm","2号空调 乙二醇泵2故障","1","1","1","1","8573",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["29","6.7.92.3","Stulz7000_1_GlycolPump3Alarm","2号空调 乙二醇泵3故障","1","1","1","1","8574",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["30","6.7.92.3","Stulz7000_1_GlycolPump4Alarm","2号空调 乙二醇泵4故障","1","1","1","1","8575",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["31","6.7.92.3","Stulz7000_1_Humidification1Alarm","2号空调 加湿器1故障","1","1","1","1","8576",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["32","6.7.92.3","Stulz7000_1_Humidification2Alarm","2号空调 加湿器2故障","1","1","1","1","8577",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["33","6.7.92.3","Stulz7000_1_Humidification3Alarm","2号空调 加湿器3故障","1","1","1","1","8588",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["34","6.7.92.3","Stulz7000_1_FanFilter1Alarm","2号空调 风扇过滤网1故障","1","1","1","1","8589",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["35","6.7.92.3","Stulz7000_1_FanFilter2Alarm","2号空调 风扇过滤网2故障","1","1","1","1","8590",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["36","6.7.92.3","Stulz7000_1_FanFilter3Alarm","2号空调 风扇过滤网3故障","1","1","1","1","8591",null,"type-1","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","0",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","报警"]
["1","6.7.92.3","Stulz7000_1_Communications","2号空调 通信状态","1000","0","0","1","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断开,"]