{"text_format":"3","workbook":"xls","n_sheets":20,"sheets":["Sheet1","１．適用","２．システム構成","２．１システム構成図<1>","２．１システム構成図<2>","２．１システム構成図<3>","２．１システム構成図<4>","２．１システム構成図<5>","２．１システム構成図<6>","３．ハードウェア仕様<1>","４．ソフトウェア仕様","３．ハードウェア仕様<2>","４．１動作概要","４．２上位ユニット通信機能<1>","４．２上位ユニット通信機能<2>","４．２上位ユニット通信機能<3>","４．２上位ユニット通信機能<4>","４．２上位ユニット通信機能<5>","４．２上位ユニット通信機能<6>","４．２上位ユニット通信機能<7>"],"not_rendered":{"images":3,"external_links":1,"defined_names":3,"comments":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":29,"n_cols":5,"rows_kept":29,"merged":[[17,0,17,5],[19,0,19,5]],"flags":["formulas_cached_only"]}
{"$rows_empty":17}
["上海大金空调机远程监控接口"]
[]
["通信协议"]
{"$rows_empty":8}
[{"$nulls":4},"技外联  SZ-02120301"]

{"sheet":"１．適用","index":1,"n_rows":3,"n_cols":9,"rows_kept":3,"flags":["formulas_cached_only"]}
[]
[]
[null,null,"1.","適用",{"$nulls":4},"　  本通信协议适用于上海大金空调有限公司开发的『空调机远程监控接口』(下称：接口)\n　  每块接口最大可对三台空调室内机进行监视和控制，通过同接口相连的上位机(SU：Supervision Unit或监视/控制中心)可以实现远程监视/控制。"]

{"sheet":"２．システム構成","index":2,"n_rows":24,"n_cols":9,"rows_kept":24,"flags":["formulas_cached_only"]}
[]
[]
[null,null,"2.","系统构成"]
[{"$nulls":4},"2.1","系统构成图"]
[{"$nulls":6},"1.","上位机","    上位机定义SU:Supervision Unit或监视/控制中心。为了实现对空调机的监视/控制，对接口发出规定指令。接口接收到的指令向上位机回复指令。"]
[]
[{"$nulls":6},"2.","空调室内机","    接口为了进行监视/控制空调机的系统，1块接口最多可连接3台室内机。\n接口板通过采用室内机同遥控器的通信信号实现监视，并可实现遥控器的控制功能。"]
[]
[]
[{"$nulls":4},"2.2","上位机间通信"]
[{"$nulls":6},"1.","连结方式","    通信方式可采用二种，一种为上位机同接口板直接联接(直接连接方式)另一种为利用公众通信回路，以MODEM为媒介将上位机同接口相连(MODEM方式)。\n直接连接方式/MODEM方式可设定功能进行选择。"]
[]
[{"$nulls":8},"直接连接方式\n接口同上位机保持接续状态，传送指令，回复指令。\n"]
[{"$nulls":8},"MODEM方式\n接口同上位机处于未接续状态，传送指令，回复指令时需先同回线连接。\n"]
[]
[{"$nulls":6},"2.","通信方式","上位机为主轴，接口为从向，采用主从通从通信方式。\n上位机(主机)发送主令，接口(从局)根据指令回复。\n直接连接方式时，通常采用上述方式。\nMODEM方式时，虽然通常采用上述方式，但紧急警告发生时，有必要自动同公众回线连接。\n"]
[]
[{"$nulls":6},"3.","通信规格","各项目自由设定功能选择。详细内容参考软件说明。"]
[{"$nulls":7},"· 通信情报形式","独有规格         /中国邮电电信总局文件(中国电信文换[1999]625基准)规格"]
[{"$nulls":7},"· 通信串联接口","RS-232          ／RS-485"]
[{"$nulls":7},"· 通信速度","2.4Kbps         ／9.6Kbps"]
[{"$nulls":7},"・ 同期方式","调步同期"]
[{"$nulls":7},"・ 字节构成","开始：1字节   数据：8字节   停止：1字节   电池：无"]
[{"$nulls":7},"・ 流量控制","RS/CS流"]

{"sheet":"２．１システム構成図<1>","index":3,"n_rows":60,"n_cols":83,"rows_kept":60,"merged":[[2,5,2,42],[2,47,2,84],[3,5,3,32],[3,37,3,42],[3,47,3,74],[3,79,3,84],[7,2,45,2],[8,16,8,21],[8,37,8,42],[8,58,8,63],[8,79,8,84],[11,59,11,62],[11,80,11,83],[21,58,22,63],[21,79,22,84],[32,59,32,62],[32,80,32,83],[34,17,36,20],[34,59,36,62],[37,21,37,26],[37,40,37,43],[37,63,37,68],[37,82,37,85],[43,6,43,11],[43,16,43,21],[43,26,43,31],[43,37,43,42],[43,48,43,53],[43,58,43,63],[43,68,43,73],[43,79,43,84],[47,5,47,12],[47,15,47,22],[47,25,47,32],[47,36,47,43],[47,47,47,54],[47,57,47,64],[47,67,47,74],[47,78,47,85],[49,2,60,2],[52,29,52,32],[52,43,52,46],[52,57,52,60],[59,29,59,32],[59,43,59,46],[59,57,59,60]],"flags":["formulas_cached_only"]}
[]
[]
[null,null,"通信方式",null,null,"直接接続方式",{"$nulls":41},"ＭＯＤＥＭ方式"]
[null,null,"I／F",null,null,"RS-485",{"$nulls":31},"RS-232",{"$nulls":9},"RS-485",{"$nulls":31},"RS-232"]
[]
[]
[]
[null,null,"上位机·接口间通讯系统"]
[{"$nulls":16},"上位机",{"$nulls":20},"上位机",{"$nulls":20},"上位机",{"$nulls":20},"上位机"]
[]
[]
[{"$nulls":59},"MODEM",{"$nulls":20},"MODEM"]
{"$rows_empty":9}
[{"$nulls":58},"公共线路",{"$nulls":20},"公共线路"]
{"$rows_empty":10}
[{"$nulls":59},"MODEM",{"$nulls":20},"MODEM"]
[]
[{"$nulls":17},"RS232/\nRS485\n转换器",{"$nulls":41},"RS232/\nRS485\n转换器"]
[]
[]
[{"$nulls":21},"RS-485",{"$nulls":18},"RS-232",{"$nulls":22},"RS-485",{"$nulls":18},"RS-232"]
[]
[]
[]
[]
[]
[{"$nulls":6},"接口",{"$nulls":9},"接口",{"$nulls":9},"接口",{"$nulls":10},"接口",{"$nulls":10},"接口",{"$nulls":9},"接口",{"$nulls":9},"接口",{"$nulls":10},"接口"]
[]
[]
[]
[{"$nulls":5},"空调室内机",{"$nulls":9},"空调室内机",{"$nulls":9},"空调室内机",{"$nulls":10},"空调室内机",{"$nulls":10},"空调室内机",{"$nulls":9},"空调室内机",{"$nulls":9},"空调室内机",{"$nulls":10},"空调室内机"]
[]
[null,null,"空调系统"]
[]
[]
[{"$nulls":29},"室内机",{"$nulls":13},"室内机",{"$nulls":13},"室内机"]
[]
[]
[]
[]
[]
[]
[{"$nulls":29},"遥控器",{"$nulls":13},"遥控器",{"$nulls":13},"遥控器"]

{"sheet":"２．１システム構成図<2>","index":4,"n_rows":60,"n_cols":58,"rows_kept":60,"merged":[[2,5,2,32],[3,5,3,32],[7,2,45,2],[37,21,37,26],[43,6,43,11],[43,16,43,21],[43,26,43,31],[47,5,47,12],[47,15,47,22],[47,25,47,32],[49,2,60,2],[52,29,52,32],[52,43,52,46],[52,57,52,60],[59,29,59,32],[59,43,59,46],[59,57,59,60]],"flags":["formulas_cached_only"]}
[]
[]
[null,null,"通信方式",null,null,"单独方式"]
[null,null,"I／F",null,null,"RS-485"]
[]
[]
[]
[null,null,"上位机·接口间通信系统"]
{"$rows_empty":29}
[{"$nulls":21},"RS-485"]
[]
[]
[]
[]
[]
[{"$nulls":6},"接口",{"$nulls":9},"接口",{"$nulls":9},"接口"]
[]
[]
[]
[{"$nulls":5},"空调室内机",{"$nulls":9},"空调室内机",{"$nulls":9},"空调室内机"]
[]
[null,null,"空调系统"]
[]
[]
[{"$nulls":29},"室内机",{"$nulls":13},"室内机",{"$nulls":13},"室内机"]
[]
[]
[]
[]
[]
[]
[{"$nulls":29},"遥控器",{"$nulls":13},"遥控器",{"$nulls":13},"遥控器"]

{"sheet":"２．１システム構成図<3>","index":5,"n_rows":56,"n_cols":63,"rows_kept":56,"merged":[[18,57,27,58],[21,50,23,56],[40,7,56,8],[40,9,41,12],[40,13,41,15],[40,55,41,57],[40,58,41,61],[40,62,56,63],[43,9,44,12],[43,13,44,15],[43,55,44,57],[43,58,44,61],[45,9,46,12],[45,13,46,15],[45,55,46,57],[45,58,46,61],[47,9,48,12],[47,13,48,15],[47,55,48,57],[47,58,48,61],[49,9,50,12],[49,13,50,15],[49,55,50,57],[49,58,50,61],[51,9,52,12],[51,13,52,15],[51,55,52,57],[51,58,52,61],[53,9,54,12],[53,13,54,15],[53,55,54,57],[53,58,54,61],[55,9,56,12],[55,13,56,15],[55,55,56,57],[55,58,56,61]],"flags":["formulas_cached_only"]}
[]
[]
[{"$nulls":3},"直接连接方式—RS-485时连接形态"]
{"$rows_empty":14}
[{"$nulls":15},"RS-232"]
[{"$nulls":57},"RS-485(half duplex)"]
[]
[]
[{"$nulls":50},"RS-232/RS-485\n转换器"]
[]
[]
[]
[]
[{"$nulls":5},"RS-232/RS-485转换器"]
[]
[{"$nulls":6},"RS-232/RS-485转换器需使用下述产品。"]
[]
[{"$nulls":6},"品名：ic485-lp1(ATEN International Co.,Ltd) 或相当品"]
[{"$nulls":6},"设定：DCE/DTE : DCE"]
[{"$nulls":6},"　　　MON/SIM : SIM"]
[{"$nulls":6},"　　　Three position slide switch : T-RTS R-/RTS",{"$nulls":50},"终端电阻"]
[]
[{"$nulls":57},"两端接口的终端电阻置于ON"]
[]
[]
[{"$nulls":5},"连接电线"]
[]
[{"$nulls":7},"to PC(D-sub 9Pin)",null,"Signal",{"$nulls":3},"Pin\nNo.",{"$nulls":41},"Pin\nNo.",null,null,"Signal",{"$nulls":3},"to Converter(D-sub 25Pin)"]
[]
[]
[{"$nulls":9},"TXD",{"$nulls":3},3,{"$nulls":41},2,null,null,"TD"]
[]
[{"$nulls":9},"RXD",{"$nulls":3},2,{"$nulls":41},3,null,null,"RD"]
[]
[{"$nulls":9},"RTS",{"$nulls":3},7,{"$nulls":41},4,null,null,"RTS"]
[]
[{"$nulls":9},"CTS",{"$nulls":3},8,{"$nulls":41},5,null,null,"CTS"]
[]
[{"$nulls":9},"DSR",{"$nulls":3},6,{"$nulls":41},6,null,null,"DSR"]
[]
[{"$nulls":9},"DTR",{"$nulls":3},4,{"$nulls":41},20,null,null,"DTR"]
[]
[{"$nulls":9},"GND",{"$nulls":3},5,{"$nulls":41},7,null,null,"GND"]

{"sheet":"２．１システム構成図<4>","index":6,"n_rows":51,"n_cols":63,"rows_kept":51,"merged":[[10,52,10,54],[33,7,51,8],[33,9,34,12],[33,13,34,15],[33,55,34,57],[33,58,34,61],[33,62,51,63],[36,9,37,12],[36,13,37,15],[36,55,37,57],[36,58,37,61],[38,9,39,12],[38,13,39,15],[38,55,39,57],[38,58,39,61],[40,9,41,12],[40,13,41,15],[40,55,41,57],[40,58,41,61],[42,9,43,12],[42,13,43,15],[42,55,43,57],[42,58,43,61],[44,9,45,12],[44,13,45,15],[44,55,45,57],[44,58,45,61],[46,9,47,12],[46,13,47,15],[46,55,47,57],[46,58,47,61],[48,9,49,12],[48,13,49,15],[48,55,49,57],[48,58,49,61],[50,9,51,12],[50,13,51,15],[50,55,51,57],[50,58,51,61]],"flags":["formulas_cached_only"]}
[]
[]
[{"$nulls":3},"直接连接方式—RS-232方式时的连接形态"]
{"$rows_empty":14}
[{"$nulls":15},"RS-232交叉电线"]
{"$rows_empty":8}
[{"$nulls":51},"・ 一个线路只能连接一台遥控器·室内机。"]
[{"$nulls":51},"・ 不可连接集中遥控器。"]
[]
[]
[]
[{"$nulls":5},"连接电线"]
[]
[{"$nulls":7},"to CrossCable(D-sub 9Pin)",null,"Signal",{"$nulls":3},"Pin\nNo.",{"$nulls":41},"Pin\nNo.",null,null,"Signal",{"$nulls":3},"to Adapter(XH8P)"]
[]
[]
[{"$nulls":9},"GND",{"$nulls":3},5,{"$nulls":41},1,null,null,"GND"]
[]
[{"$nulls":9},"(CD)",{"$nulls":3},1,{"$nulls":41},2,null,null,"(CD)"]
[]
[{"$nulls":9},"ER",{"$nulls":3},4,{"$nulls":41},3,null,null,"ER"]
[]
[{"$nulls":9},"(RI)",{"$nulls":3},9,{"$nulls":41},4,null,null,"(RI)"]
[]
[{"$nulls":9},"RTS",{"$nulls":3},7,{"$nulls":41},5,null,null,"RTS"]
[]
[{"$nulls":9},"TXD",{"$nulls":3},3,{"$nulls":41},6,null,null,"TXD"]
[]
[{"$nulls":9},"CTS",{"$nulls":3},8,{"$nulls":41},7,null,null,"CTS"]
[]
[{"$nulls":9},"RXD",{"$nulls":3},2,{"$nulls":41},8,null,null,"RXD"]

{"sheet":"２．１システム構成図<5>","index":7,"n_rows":82,"n_cols":63,"rows_kept":82,"merged":[[8,47,12,49],[10,52,10,54],[16,49,16,50],[18,57,27,58],[19,49,19,50],[21,50,23,56],[45,7,63,8],[45,9,46,12],[45,13,46,15],[45,55,46,57],[45,58,46,61],[45,62,63,63],[48,9,49,12],[48,13,49,15],[48,55,49,57],[48,58,49,61],[50,9,51,12],[50,13,51,15],[50,55,51,57],[50,58,51,61],[52,9,53,12],[52,13,53,15],[52,55,53,57],[52,58,53,61],[54,9,55,12],[54,13,55,15],[54,55,55,57],[54,58,55,61],[56,9,57,12],[56,13,57,15],[56,55,57,57],[56,58,57,61],[58,9,59,12],[58,13,59,15],[58,55,59,57],[58,58,59,61],[60,9,61,12],[60,13,61,15],[60,55,61,57],[60,58,61,61],[62,9,63,12],[62,13,63,15],[62,55,63,57],[62,58,63,61],[66,27,67,29],[66,30,67,33],[66,34,82,35],[69,27,70,29],[69,30,70,33],[71,27,72,29],[71,30,72,33],[73,27,74,29],[73,30,74,33],[75,27,76,29],[75,30,76,33],[77,27,78,29],[77,30,78,33],[79,27,80,29],[79,30,80,33],[81,27,82,29],[81,30,82,33]],"flags":["formulas_cached_only"]}
[]
[]
[{"$nulls":3},"MODEM方式—RS-485方式时的连接形态"]
[]
[]
[]
[{"$nulls":47}," RS-232"]
[]
[{"$nulls":47},"· CTS\n· RTS\n· CD\n· ER"]
[]
[{"$nulls":52},"· RTS"]
[]
[]
[]
[]
[]
[{"$nulls":49},"RXD"]
[]
[{"$nulls":57},"RS-485(半双工)"]
[{"$nulls":49},"TXD"]
[]
[{"$nulls":50},"RS-232/RS-485\n转换器"]
[]
[]
[]
[]
[{"$nulls":5},"・ MODEM同RS-232/RS-485转换器以及接口连接的电线不能使用标准品，需另行制作。"]
[]
[]
[]
[]
[{"$nulls":5},"RS-232/RS-485转换器"]
[]
[{"$nulls":6},"RS-232/RS-485转换器需使用下述产品。",{"$nulls":52},"终端电阻"]
[]
[{"$nulls":6},"品名：ic485-lp1(ATEN International Co.,Ltd) 或相当品",{"$nulls":52},"两端接口的终端电阻置于ON"]
[{"$nulls":6},"设定：DCE/DTE : DCE"]
[{"$nulls":6},"　　　MON/SIM : SIM"]
[{"$nulls":6},"　　　Three position slide switch : T-RTS R-/RTS"]
[]
[]
[]
[]
[{"$nulls":5},"连接电线"]
[]
[{"$nulls":7},"to MODEM(D-sub 9Pin)",null,"Signal",{"$nulls":3},"Pin\nNo.",{"$nulls":41},"Pin\nNo.",null,null,"Signal",{"$nulls":3},"to Adapter(XH8P)"]
[]
[]
[{"$nulls":9},"GND",{"$nulls":3},5,{"$nulls":41},1,null,null,"GND"]
[]
[{"$nulls":9},"(CD)",{"$nulls":3},1,{"$nulls":41},2,null,null,"(CD)"]
[]
[{"$nulls":9},"ER",{"$nulls":3},4,{"$nulls":41},3,null,null,"ER"]
[]
[{"$nulls":9},"(RI)",{"$nulls":3},9,{"$nulls":41},4,null,null,"(RI)"]
[]
[{"$nulls":9},"RTS",{"$nulls":3},7,{"$nulls":41},5,null,null,"RTS"]
[]
[{"$nulls":9},"TXD",{"$nulls":3},3,{"$nulls":41},6,null,null,"TXD"]
[]
[{"$nulls":9},"CTS",{"$nulls":3},8,{"$nulls":41},7,null,null,"CTS"]
[]
[{"$nulls":9},"RXD",{"$nulls":3},2,{"$nulls":41},8,null,null,"RXD"]
[]
[]
[]
[{"$nulls":27},"Pin\nNo.",null,null,"Signal",{"$nulls":3},"to Converter(D-sub 25Pin)"]
[]
[]
[{"$nulls":27},2,null,null,"TD"]
[]
[{"$nulls":27},3,null,null,"RD"]
[]
[{"$nulls":27},4,null,null,"RTS"]
[]
[{"$nulls":27},5,null,null,"CTS"]
[]
[{"$nulls":27},6,null,null,"DSR"]
[]
[{"$nulls":27},20,null,null,"DTR"]
[]
[{"$nulls":27},7,null,null,"GND"]

{"sheet":"２．１システム構成図<6>","index":8,"n_rows":51,"n_cols":63,"rows_kept":51,"merged":[[10,52,10,54],[33,7,51,8],[33,9,34,12],[33,13,34,15],[33,55,34,57],[33,58,34,61],[33,62,51,63],[36,9,37,12],[36,13,37,15],[36,55,37,57],[36,58,37,61],[38,9,39,12],[38,13,39,15],[38,55,39,57],[38,58,39,61],[40,9,41,12],[40,13,41,15],[40,55,41,57],[40,58,41,61],[42,9,43,12],[42,13,43,15],[42,55,43,57],[42,58,43,61],[44,9,45,12],[44,13,45,15],[44,55,45,57],[44,58,45,61],[46,9,47,12],[46,13,47,15],[46,55,47,57],[46,58,47,61],[48,9,49,12],[48,13,49,15],[48,55,49,57],[48,58,49,61],[50,9,51,12],[50,13,51,15],[50,55,51,57],[50,58,51,61]],"flags":["formulas_cached_only"]}
[]
[]
[{"$nulls":3},"MODEM方式—RS-232方式时的连接形态"]
{"$rows_empty":11}
[{"$nulls":34},"HayesTMACCURATM336 EXT."]
[{"$nulls":34},"SPEAKERPHONE 互换品"]
[]
[{"$nulls":39},"RS232"]
[{"$nulls":39},"直电线"]
{"$rows_empty":7}
[{"$nulls":51},"・ 一个线路只能连接一台遥控器·室内机。"]
[{"$nulls":51},"· 不可连接集中遥控器。"]
[]
[]
[]
[{"$nulls":5},"连接电线"]
[]
[{"$nulls":7},"to StraightCable(D-sub 9Pin)",null,"Signal",{"$nulls":3},"Pin\nNo.",{"$nulls":41},"Pin\nNo.",null,null,"Signal",{"$nulls":3},"to Adapter(XH8P)"]
[]
[]
[{"$nulls":9},"GND",{"$nulls":3},5,{"$nulls":41},1,null,null,"GND"]
[]
[{"$nulls":9},"(CD)",{"$nulls":3},1,{"$nulls":41},2,null,null,"(CD)"]
[]
[{"$nulls":9},"ER",{"$nulls":3},4,{"$nulls":41},3,null,null,"ER"]
[]
[{"$nulls":9},"(RI)",{"$nulls":3},9,{"$nulls":41},4,null,null,"(RI)"]
[]
[{"$nulls":9},"RTS",{"$nulls":3},7,{"$nulls":41},5,null,null,"RTS"]
[]
[{"$nulls":9},"TXD",{"$nulls":3},3,{"$nulls":41},6,null,null,"TXD"]
[]
[{"$nulls":9},"CTS",{"$nulls":3},8,{"$nulls":41},7,null,null,"CTS"]
[]
[{"$nulls":9},"RXD",{"$nulls":3},2,{"$nulls":41},8,null,null,"RXD"]

{"sheet":"３．ハードウェア仕様<1>","index":9,"n_rows":29,"n_cols":9,"rows_kept":29,"flags":["formulas_cached_only"]}
[]
[]
[null,null,"3.","硬件规格"]
[{"$nulls":4},"3.1","硬件构成"]
[{"$nulls":6},"1.","电脑基板(下基板)","100mm X 100mm（双面基板）"]
[]
[{"$nulls":6},"2.","电脑基板(上基板)"]
[]
[{"$nulls":6},"3.","CN1:电源输入端子","XH端子：2P　白"]
[{"$nulls":8},"电源规格　　：DC16V+15%／ー15%"]
[]
[{"$nulls":6},"4.","CN2:MODEM／RS-232连接端子"]
[]
[{"$nulls":6},"5.","CN3:外部强制运转/停止输入端子"]
[]
[{"$nulls":6},"6.","Tes1:RS-485连接端子台"]
[]
[{"$nulls":6},"7.","Tes2:遥控器·线路连接端子台","连接室内机—遥控器传输线路。(无极性)"]
[{"$nulls":8},"　R／C1：遥控器·线路0连接"]
[{"$nulls":8},"　R／C2：遥控器·线路1连接"]
[{"$nulls":8},"　R／C3：遥控器·线路2连接"]
[]
[{"$nulls":6},"8.","BS1:设定状态","接触：利用遥控器的维修模式设定各种模式"]
[]
[{"$nulls":6},"9.","LED-A:微电脑遥控器正常","緑"]
[]
[{"$nulls":6},"10.","LED-1:异常","红"]
[]
[{"$nulls":6},"11.","SS1：RS-485终端ON/OFF"]

{"sheet":"４．ソフトウェア仕様","index":10,"n_rows":41,"n_cols":8,"rows_kept":41,"flags":["formulas_cached_only"]}
[]
[]
[null,null,"4.","软件规格"]
[{"$nulls":4},"4.1","动作概要"]
[{"$nulls":6},"1.","初期设定"]
[{"$nulls":6},"2.","遥控器回路通信"]
[{"$nulls":6},"3.","上位机通信"]
[]
[{"$nulls":4},"4.2","上位机通信功能"]
[{"$nulls":6},"1.","接线方式"]
[{"$nulls":6},"2.","通信方式"]
[{"$nulls":6},"3.","通信规格"]
[{"$nulls":6},"4.","中国邮电协议规格"]
[{"$nulls":6},"5.","独有协议规格"]
[]
[{"$nulls":4},"4.3","空调机监视·控制功能"]
[]
[]
[{"$nulls":4},"4.4","设定功能"]
[{"$nulls":6},"1.","概要"]
[{"$nulls":6},"2.","遥控器表示及操作开关"]
[{"$nulls":6},"3.","遥控器维修模式设定次序"]
[]
[{"$nulls":4},"4.5","成组控制"]
[]
[]
[{"$nulls":4},"4.6","顺次起动"]
[{"$nulls":6},"1.","概要"]
[{"$nulls":6},"2.","顺次起动时间表"]
[]
[{"$nulls":4},"4.7","备用机运转"]
[]
[{"$nulls":4},"4.8","强制运转·停止"]
[{"$nulls":6},"1.","概要"]
[{"$nulls":6},"2.","停止/起动时间"]
[]
[{"$nulls":4},"4.9","自动交替运转"]
[]
[{"$nulls":4},"4.10","时钟"]
[]
[{"$nulls":4},"4.11","发报"]

{"sheet":"３．ハードウェア仕様<2>","index":11,"n_rows":51,"n_cols":52,"rows_kept":51,"merged":[[12,41,12,43],[12,44,12,46],[13,18,13,22],[13,23,13,30],[13,32,13,39],[15,16,15,17],[15,24,15,25],[18,48,23,48],[19,16,19,18],[21,16,22,18],[21,42,21,46],[23,16,23,21],[25,47,25,48],[43,29,43,31],[43,32,43,34],[43,35,43,37],[43,38,43,40],[43,41,43,43],[43,44,43,46],[44,29,44,34],[44,35,44,40],[44,41,44,46]],"flags":["formulas_cached_only"]}
[]
[]
[]
[]
[]
[{"$nulls":9},"5．CN3:外部控制运转/停止输入端子",{"$nulls":31},"4．CN2:MODEM／RS-232连接端子"]
[]
[]
[{"$nulls":9},"3．CN1:电源端子",{"$nulls":33},"6．Tes1:RS-485连接端子台"]
[]
[]
[]
[{"$nulls":41},"A(+)",null,null,"B(-)"]
[{"$nulls":18},"电源 POWER",{"$nulls":4},"ON/OFF运转/停止",{"$nulls":8},"     MODEM   CN2"]
[]
[{"$nulls":16},"CN1",{"$nulls":7},"CN3",{"$nulls":26},"11．SS1:RS-485终端ON/OFF"]
[{"$nulls":41},"Tes1"]
[{"$nulls":5},"10．LED-1:异常",{"$nulls":35},"RS-485"]
[{"$nulls":48},"SS1 OFF<->ON"]
[{"$nulls":16},"LED-A",{"$nulls":6},"LED-1",{"$nulls":19},"终端"]
[{"$nulls":43},"RS-485"]
[{"$nulls":16},"SERV.\n MON. ",{"$nulls":8},"ERROR",{"$nulls":16},"TERMINATION",{"$nulls":8},"8．BS1:设定模式"]
[{"$nulls":26},"异常"]
[{"$nulls":16},"微电脑监控器正常"]
[]
[{"$nulls":47},"BS1"]
[{"$nulls":3},"9．LED-A:微电脑监控器正常"]
{"$rows_empty":16}
[{"$nulls":29},"P1",null,null,"P2",null,null,"P1",null,null,"P2",null,null,"P1",null,null,"P2"]
[{"$nulls":29},"R/C 1",{"$nulls":5},"R/C 2",{"$nulls":5},"R/C 3"]
[]
[]
[]
[{"$nulls":23},"1．下基板",{"$nulls":11},"7．Tes2:遥控器·回路连接端子台"]
[]
[{"$nulls":17},"2．上基板"]

{"sheet":"４．１動作概要","index":12,"n_rows":22,"n_cols":9,"rows_kept":22,"flags":["formulas_cached_only"]}
[]
[]
[null,null,"4.","软件规格"]
[{"$nulls":4},"4.1","动作概要"]
[{"$nulls":6},"1.","初始设定","电源接通后，时刻为00:00。"]
[]
[]
[]
[{"$nulls":6},"2.","遥控回路通讯","监视空调机状态。"]
[{"$nulls":8},"如果利用遥控器进行操作，空调机的运转状态随时改变。"]
[]
[]
[]
[{"$nulls":6},"3.","上位机通讯"]
[{"$nulls":7},"・ 运程通讯","应对上位机的通讯要求，实现远程通讯。"]
[{"$nulls":8},"上位机长时间连接状态下，自动切断通信。"]
[]
[]
[{"$nulls":7},"・ 远程通讯","有事情发生时，根据发生原因向上位机通报，实现远程通讯。"]
[{"$nulls":8},"通报时，如果同上位机无法连接，则自动重拨。"]
[{"$nulls":8},"上位时如果长时间处于通信中的情况下，自动切断，进行发报保护。"]
[{"$nulls":8},"※发报保护情况下无法通报。"]

{"sheet":"４．２上位ユニット通信機能<1>","index":13,"n_rows":24,"n_cols":9,"rows_kept":24,"flags":["formulas_cached_only"]}
[]
[]
[null,null,"4.","软件规格"]
[{"$nulls":4},"4.2","上位机通信功能"]
[{"$nulls":6},"1.","接线方式","　    通信方式有二种、一种为上位机同接口直接连接(直接连接方式)另一种为以公共回路为媒介、使上位机同接口连接(MODEM)方式。\n直接连接方式/MODEM方式可以进行设置选择。"]
[]
[{"$nulls":8},"直接连接方式：\n接口同上位机保持常通状态，可随时发出指令，回复指令。\n"]
[{"$nulls":8},"MODEM方式：\n接口同上位机保持常断状态发生指令，回复时需先连接回路。\n"]
[]
[{"$nulls":6},"2.","通信方式","采用主从通讯方式，上位机为主局，接口为从局。\n上位机(主机)发出指令，接口(从局)针对该指令返信。\n直接连接方式连接时，采用上述方式。\nMODEM连接方式时，通常情况下采用上述方式，\n但有紧急警告发生时，接口自动连接回路发信。"]
[]
[{"$nulls":6},"3.","通信规格","由设定功能选择各项目"]
[{"$nulls":7},"(1)通信情报形式","独有规格　　　　／中国邮电电信总局文件（中国电信交换[1999]625号 基准）规格"]
[{"$nulls":7},"(2)通信接口制式","RS-232　　　　 ／RS-485"]
[{"$nulls":7},"(3)通信速度","2.4Kbps　　　　／9.6Kbps"]
[{"$nulls":7},"(4)同期方式","调步同期"]
[{"$nulls":7},"(4)字节构成","起始：1字节   数据：8字节   停止：1字节   电池：无"]
[{"$nulls":7},"(5)流量控制","RS／CS流"]
[]
[{"$nulls":6},"4.","中国邮电通信协议"]
[]
[{"$nulls":6},"5.","独自通信协议"]
[]
[{"$nulls":6},"6.","接口信息","直接连接方式·独有规格时，接口每隔2秒钟向上位机发送接口信息。\n接口信息、包括各台空调机的累积情况以及各种情况发生的信息。"]

{"sheet":"４．２上位ユニット通信機能<2>","index":14,"n_rows":76,"n_cols":20,"rows_kept":76,"merged":[[3,5,4,5],[3,6,3,7],[4,9,4,12],[7,5,8,5],[7,7,8,7],[9,5,10,5],[9,7,10,7],[11,5,12,5],[11,7,12,7],[13,5,14,5],[13,7,14,7],[15,5,18,5],[15,7,18,7],[16,8,18,8],[19,5,30,5],[31,5,34,5],[41,4,41,11],[41,12,41,19],[44,4,44,7],[44,8,44,19],[45,4,46,7],[45,8,46,19],[48,7,48,8],[48,10,48,11],[48,13,48,14],[53,8,53,9],[54,8,54,9],[55,8,55,9],[63,4,63,7],[63,8,63,11],[63,12,63,15],[63,16,63,19]],"flags":["formulas_cached_only"]}
[]
[null,null,"邮电规格"]
[]
[{"$nulls":5},"符号","命令"]
[{"$nulls":9},"             数值"]
[]
[{"$nulls":5},"SOI",null,"起始码",{"$nulls":3},"7EH"]
[{"$nulls":5},"VER",null,"通信协议\n版本",{"$nulls":3},"'2'"]
[{"$nulls":11},"'0'"]
[{"$nulls":5},"ADR",null,"设备\n地址"]
[]
[{"$nulls":5},"CID1",{"$nulls":5},"'6'"]
[{"$nulls":11},"'0'"]
[{"$nulls":5},"CID2"]
[]
[{"$nulls":5},"LENGTH",null,"指令信息\n的字节数","LCHKSUM"]
[{"$nulls":8},"LENID"]
[]
[]
[{"$nulls":5},"COMMAND\nINFO"]
{"$rows_empty":11}
[{"$nulls":5},"CHKSUM"]
[]
[]
[]
[{"$nulls":5},"EOI",null,"结束吗",{"$nulls":3},"0DH"]
[]
[]
[]
[]
[]
[null,null,"LENGTH数据形式",null,"字节高位",{"$nulls":7},"字节低位"]
[{"$nulls":4},"D15","D14","D13","D12","D11","D10","D9","D8","D7","D6","D5","D4","D3","D2","D1","D0"]
[]
[{"$nulls":4},"LCHKSUM",{"$nulls":3},"LENID"]
[{"$nulls":4},"LENGTH确认和",{"$nulls":3},"INFO中ASCII码的字节数"]
[]
[]
[{"$nulls":3},"・","LCHKSUM= ",null,"(","D11…D8",null,"＋","D7…D4",null,"＋","D3…D0",null,")","的2的补数"]
[]
[null,null,"(例)","INFO的字节数=18时","LENID：D11…D0 =",{"$nulls":3},0,0,0,0,0,0,0,1,0,0,1,0]
[]
[]
[{"$nulls":4},"LCHKSUM：D15…D12=",{"$nulls":3},"D11…D8",null,"=",null,0,0,0,0]
[{"$nulls":8},"D7…D4",{"$nulls":3},0,0,0,1]
[{"$nulls":7},"＋","D3…D0",null,null,"＋",0,0,1,0]
[{"$nulls":9},"2的补数",null,null,0,0,1,1,"2的补数"]
[{"$nulls":12},"="]
[{"$nulls":12},1,1,0,1]
[]
[]
[{"$nulls":4},"D15","D14","D13","D12","D11","D10","D9","D8","D7","D6","D5","D4","D3","D2","D1","D0"]
[{"$nulls":3},"LENGTH= ",1,1,0,1,0,0,0,0,0,0,0,1,0,0,1,0]
[{"$nulls":4},"D",{"$nulls":3},0,{"$nulls":3},1,{"$nulls":3},2]
[]
[]
[]
[]
[]
[null,null,"CHKSUM数据形式",null,"从VER到INFO的合计的2的补数"]
[]
[null,null,"(例)","~1203400456ABCDFEFC72CR('~'=SOI,'CR'=EOI)时"]
[{"$nulls":4}," '1'+'2'+'0'+…+'A'+'B'+…+'F'+'E'的2的补数"]
[{"$nulls":4},"=31H+32H+30H+…+41H+42H+…+46H+45H的2的补数"]
[{"$nulls":4},"=038EH的2的补数"]
[{"$nulls":4},"=FC72H"]

{"sheet":"４．２上位ユニット通信機能<3>","index":15,"n_rows":27,"n_cols":8,"rows_kept":27,"merged":[[6,5,8,5],[9,5,15,5],[9,7,15,7]],"flags":["formulas_cached_only"]}
[]
[null,null,"独有规格"]
[]
[{"$nulls":5},"符号","指令","数值"]
[]
[{"$nulls":5},"STX","起始码","02H"]
[{"$nulls":5},"识别部"]
[]
[]
[{"$nulls":5},"数据部",null,"…"]
[]
[]
[]
[]
[]
[]
[{"$nulls":5},"ETX","结束吗","03H"]
[{"$nulls":5},"BCC"]
[]
[]
[]
[]
[null,null,"识别部","'0'～'9'、'A'～'F'的ASCII码(30H～39H、41H～46H)"]
[]
[null,null,"数据部","'0'～'9'、'A'～'F'的ASCII码(30H～39H、41H～46H)"]
[]
[null,null,"BCC","从STX到ETX的一个字节的每一排他论理和"]

{"sheet":"４．２上位ユニット通信機能<4>","index":16,"n_rows":36,"n_cols":8,"rows_kept":36,"merged":[[6,5,9,5],[10,5,16,5],[10,7,16,7],[25,4,25,5],[26,4,26,5],[27,4,27,5],[28,4,28,5],[29,4,29,5]],"flags":["formulas_cached_only"]}
[]
[null,null,"接口信息"]
[]
[{"$nulls":5},"符号","指令","数值"]
[]
[{"$nulls":5},"STX","开始码","02H"]
[{"$nulls":5},"识别部",null,"'A'"]
[{"$nulls":7},"'T'"]
[{"$nulls":7},"'x'"]
[{"$nulls":7},"'!'"]
[{"$nulls":5},"数据部",null,"…"]
[]
[]
[]
[]
[]
[]
[{"$nulls":5},"ETX","结束吗","03H"]
[{"$nulls":5},"BCC"]
[]
[]
[]
[]
[null,null,"识别部","'Atx!' 但是'x'为、'0'、'1'、'2'、'3'中的其中一个。"]
[]
[{"$nulls":3},"机能","识别部",null,"备注"]
[{"$nulls":3},"LINE1空调累积情报通知","AT0!"]
[{"$nulls":3},"LINE2空调累积情报通知","AT1!"]
[{"$nulls":3},"LINE3空调累积情报通知","AT2!"]
[{"$nulls":3},"事件通知","AT3!"]
[]
[{"$nulls":3},"当某LINE未连结空调机，或看某LINE的空调机内机同遥控器间存在通信异常时，空调机的累积情报通知不发信。"]
[]
[null,null,"数据部","'0'～'9'、'A'～'F'的ASCII码(30H～39H、41H～46H)"]
[]
[null,null,"BCC","从STX到ETX的1个字节的每一排他的论理和。"]

{"sheet":"４．２上位ユニット通信機能<5>","index":17,"n_rows":70,"n_cols":6,"rows_kept":70,"merged":[[30,1,31,1],[30,2,31,2],[30,3,30,5]],"flags":["formulas_cached_only"]}
[]
[]
[null,"指令·通信一览表",{"$nulls":3},"：未对应"]
[]
[]
[null,null,"CID2",null,null,"RTN"]
[null," 获取模拟量量化后数据(浮点数)","41H",null,"正常","00H"]
[null," 获取模拟量量化后数据(定点数)","42H",null,"VER错","01H"]
[null," 获取开关输入状态","43H",null,"CHK SUM错","02H"]
[null," 获取告警状态","44H",null,"LCHK SUM错","03H"]
[null," 遥控","45H",null,"CID2错","04H"]
[null," 获取系统参数(浮点数)","46H",null,"命令格式无效","05H"]
[null," 获取系统参数(定点数)","47H",null,"无效数据","06H"]
[null," 设定系统参数(浮点数)","48H",null," 用户自定义","E0H…EFH"]
[null," 设定系统参数(定点数)","49H"]
[null," 获取系统历史数据(浮点数)*","4AH"]
[null," 获取系统历史数据(定点数)*","4BH"]
[null," 获取历史告警*","4CH"]
[null," 获取监测模块时间*","4DH"]
[null," 设定监测模块时间*","4EH"]
[null," 获取通信协议版本号","4FH"]
[null," 获取设备地址","50H"]
[null," 获取设备(监测模块)，厂家信息","51H"]
[null," (到目前为止功能)","E0H"]
[null," 用户自定义","E1H…EFH"]
[]
[]
["   "]
[]
[]
[null,"功　　能","内    容","识别部"]
[{"$nulls":3},0,1,2]
[null,"回路切断要求",null,0,0,0]
[null,"RAM读出",null,0,"E",0]
[null,"RAM记入",null,0,"F",0]
[null,"登录","接口ID确认",1,0,0]
[null,null,"PASSWORD确认",1,1,0]
[null,"接口设定","PASSWORD设定",2,1,0]
[null,null,"中心ーTEL No.",2,2,0]
[null,null,"接口ID",2,3,0]
[null,null,"现在时刻",2,4,0]
[null,null,"定时发报时刻",2,5,0]
[null,null,"连通为此的拨号次数",2,8,0]
[null,null,"重拨次数",2,"A",0]
[null,null,"自动备机有无",2,"B",0]
[null,null,"自动交替运转时间",2,"C",0]
[null,null,"最低运转保证台数",2,"D",0]
[null,null,"发报设定",2,"E",0]
[null,"空调设置状态确认","室内机管理台数",3,0,0]
[null,null,"UNIT No.",3,1,0]
[null,null,"限制情报",3,2,0]
[null,"空调数据收集","累积情报",4,0,0]
[null,null,"发报原因",4,1,0]
[null,"空调数据初始化",null,5,0,0]
[null,"空调·控制","运转",6,0,0]
[null,null,"过滤网清洗信号重置",6,1,0]
[null,null,"运转模式",6,2,0]
[null,null,"设定温度",6,3,0]
[null,null,"风量",6,4,0]
[null,"接口设定读出","中心ーTEL No.",7,2,0]
[null,null,"接口ID",7,3,0]
[null,null,"现在时刻",7,4,0]
[null,null,"定时发报时刻",7,5,0]
[null,null,"连通为止的拨号次数",7,8,0]
[null,null,"重拨次数",7,"A",0]
[null,null,"自动备机有无",7,"B",0]
[null,null,"自动交替运转时间",7,"C",0]
[null,null,"最低运转保证台数",7,"D",0]
[null,null,"发报设定",7,"E",0]
[null,"否定",null,"F","*",0]

{"sheet":"４．２上位ユニット通信機能<6>","index":18,"n_rows":541,"n_cols":19,"rows_kept":541,"merged":[[2,4,2,6],[2,11,2,18],[4,2,5,18],[7,2,8,2],[7,4,7,7],[7,9,8,9],[7,11,8,11],[7,13,7,16],[7,18,8,18],[8,4,8,5],[8,13,8,14],[11,2,12,2],[11,4,12,4],[11,11,12,11],[11,13,12,13],[13,2,14,2],[13,4,14,4],[13,11,14,11],[13,13,14,13],[15,2,16,2],[15,4,16,4],[15,11,16,11],[15,13,16,13],[17,2,18,2],[17,4,18,4],[17,11,18,11],[17,13,18,13],[19,2,22,2],[19,11,22,11],[20,4,22,4],[20,13,22,13],[23,2,26,2],[23,11,74,11],[23,13,24,13],[25,13,74,13],[25,14,28,14],[29,14,32,14],[33,14,36,14],[37,14,40,14],[41,14,44,14],[45,14,48,14],[49,14,52,14],[53,14,56,14],[57,14,60,14],[61,14,64,14],[65,14,68,14],[69,14,72,14],[73,14,74,14],[75,11,78,11],[87,4,87,6],[87,11,87,18],[89,2,90,18],[92,2,93,2],[92,4,92,7],[92,9,93,9],[92,11,93,11],[92,13,92,16],[92,18,93,18],[93,4,93,5],[93,13,93,14],[96,2,97,2],[96,4,97,4],[96,11,97,11],[96,13,97,13],[98,2,99,2],[98,4,99,4],[98,11,99,11],[98,13,99,13],[100,2,101,2],[100,4,101,4],[100,11,101,11],[100,13,101,13],[102,2,103,2],[102,4,103,4],[102,11,103,11],[102,13,103,13],[104,2,107,2],[104,11,107,11],[105,4,107,4],[105,13,107,13],[108,2,111,2],[108,11,131,11],[108,13,109,13],[110,13,131,13],[110,14,111,14],[112,14,113,14],[112,15,113,15],[114,14,115,14],[116,14,117,14],[118,14,119,14],[120,14,121,14],[122,14,123,14],[124,14,125,14],[126,14,127,14],[128,14,129,14],[130,14,131,14],[132,11,135,11],[143,4,143,6],[143,11,143,18],[145,2,146,18],[148,2,149,2],[148,4,148,7],[148,9,149,9],[148,11,149,11],[148,13,148,16],[148,18,149,18],[149,4,149,5],[149,13,149,14],[152,2,153,2],[152,4,153,4],[152,11,153,11],[152,13,153,13],[154,2,155,2],[154,4,155,4],[154,11,155,11],[154,13,155,13],[156,2,157,2],[156,4,157,4],[156,11,157,11],[156,13,157,13],[158,2,159,2],[158,4,159,4],[158,11,159,11],[158,13,159,13],[160,2,163,2],[160,11,163,11],[161,4,163,4],[161,13,163,13],[164,2,167,2],[164,11,191,11],[164,13,165,13],[166,13,191,13],[166,14,167,14],[168,14,169,14],[170,14,171,14],[172,14,173,14],[174,14,175,14],[176,14,177,14],[178,14,179,14],[180,14,181,14],[182,14,183,14],[184,14,185,14],[186,14,187,14],[188,14,189,14],[188,15,189,15],[190,14,191,14],[190,15,191,15],[192,11,195,11],[203,4,203,6],[203,11,203,18],[205,2,206,18],[208,2,209,2],[208,4,208,7],[208,9,209,9],[208,11,209,11],[208,13,208,16],[208,18,209,18],[209,4,209,5],[209,13,209,14],[212,2,213,2],[212,4,213,4],[212,11,213,11],[212,13,213,13],[214,2,215,2],[214,4,215,4],[214,11,215,11],[214,13,215,13],[216,2,217,2],[216,4,217,4],[216,11,217,11],[216,13,217,13],[218,2,219,2],[218,4,219,4],[218,11,219,11],[218,13,219,13],[220,2,223,2],[220,11,223,11],[221,4,223,4],[221,13,223,13],[224,2,225,2],[224,4,225,4],[224,6,225,6],[224,11,227,11],[226,2,229,2],[239,4,239,6],[239,11,239,18],[241,2,242,18],[244,2,245,2],[244,4,244,7],[244,9,245,9],[244,11,245,11],[244,13,244,16],[244,18,245,18],[245,4,245,5],[245,13,245,14],[248,2,249,2],[248,4,249,4],[248,11,249,11],[248,13,249,13],[250,2,251,2],[250,4,251,4],[250,11,251,11],[250,13,251,13],[252,2,253,2],[252,4,253,4],[252,11,253,11],[252,13,253,13],[254,2,255,2],[254,4,255,4],[254,11,255,11],[254,13,255,13],[256,2,259,2],[256,11,259,11],[257,4,259,4],[257,13,259,13],[260,2,263,2],[260,11,285,11],[260,13,285,13],[260,14,263,14],[264,14,267,14],[268,14,271,14],[270,15,271,15],[272,14,275,14],[274,15,275,15],[276,14,279,14],[280,14,283,14],[284,14,285,14],[284,15,285,15],[286,11,289,11],[297,4,297,6],[297,11,297,18],[299,2,300,18],[302,2,303,2],[302,4,302,7],[302,9,303,9],[302,11,303,11],[302,13,302,16],[302,18,303,18],[303,4,303,5],[303,13,303,14],[306,2,307,2],[306,4,307,4],[306,11,307,11],[306,13,307,13],[308,2,309,2],[308,4,309,4],[308,11,309,11],[308,13,309,13],[310,2,311,2],[310,4,311,4],[310,11,311,11],[310,13,311,13],[312,2,313,2],[312,4,313,4],[312,11,313,11],[312,13,313,13],[314,2,317,2],[314,11,317,11],[315,4,317,4],[315,13,317,13],[318,2,323,2],[318,4,319,4],[318,5,319,5],[318,11,321,11],[320,4,323,4],[321,6,322,6],[324,2,327,2],[332,2,332,4],[347,4,347,6],[347,11,347,18],[349,2,350,18],[352,2,353,2],[352,4,352,7],[352,9,353,9],[352,11,353,11],[352,13,352,16],[352,18,353,18],[353,4,353,5],[353,13,353,14],[356,2,357,2],[356,4,357,4],[356,11,357,11],[356,13,357,13],[358,2,359,2],[358,4,359,4],[358,11,359,11],[358,13,359,13],[360,2,361,2],[360,4,361,4],[360,11,361,11],[360,13,361,13],[362,2,363,2],[362,4,363,4],[362,11,363,11],[362,13,363,13],[364,2,367,2],[364,11,367,11],[365,4,367,4],[365,13,367,13],[368,2,371,2],[368,11,371,11],[379,4,379,6],[379,11,379,18],[381,2,382,18],[384,2,385,2],[384,4,384,7],[384,9,385,9],[384,11,385,11],[384,13,384,16],[384,18,385,18],[385,4,385,5],[385,13,385,14],[388,2,389,2],[388,4,389,4],[388,11,389,11],[388,13,389,13],[390,2,391,2],[390,4,391,4],[390,11,391,11],[390,13,391,13],[392,2,393,2],[392,4,393,4],[392,11,393,11],[392,13,393,13],[394,2,395,2],[394,4,395,4],[394,11,395,11],[394,13,395,13],[396,2,399,2],[396,11,399,11],[397,4,399,4],[397,13,399,13],[400,2,403,2],[400,11,403,11],[411,4,411,6],[411,11,411,18],[413,2,414,18],[416,2,417,2],[416,4,416,7],[416,9,417,9],[416,11,417,11],[416,13,416,16],[416,18,417,18],[417,4,417,5],[417,13,417,14],[420,2,421,2],[420,4,421,4],[420,11,421,11],[420,13,421,13],[422,2,423,2],[422,4,423,4],[422,11,423,11],[422,13,423,13],[424,2,425,2],[424,4,425,4],[424,11,425,11],[424,13,425,13],[426,2,427,2],[426,4,427,4],[426,11,427,11],[426,13,427,13],[428,2,431,2],[428,11,431,11],[429,4,431,4],[429,13,431,13],[432,2,435,2],[432,11,495,11],[432,13,451,13],[432,15,433,15],[434,15,435,15],[436,15,437,15],[438,15,439,15],[440,15,441,15],[442,15,443,15],[444,15,445,15],[446,15,447,15],[448,15,449,15],[450,15,451,15],[452,13,455,13],[452,15,453,15],[454,15,455,15],[456,13,495,13],[456,15,457,15],[458,15,459,15],[460,15,461,15],[462,15,463,15],[464,15,465,15],[466,15,467,15],[468,15,469,15],[470,15,471,15],[472,15,473,15],[474,15,475,15],[476,15,477,15],[478,15,479,15],[480,15,481,15],[482,15,483,15],[484,15,485,15],[486,15,487,15],[488,15,489,15],[490,15,491,15],[492,15,493,15],[494,15,495,15],[496,11,499,11],[503,4,503,6],[503,11,503,18],[505,2,506,18],[508,2,509,2],[508,4,508,7],[508,9,509,9],[508,11,509,11],[508,13,508,16],[508,18,509,18],[509,4,509,5],[509,13,509,14],[512,2,513,2],[512,4,513,4],[512,11,513,11],[512,13,513,13],[514,2,515,2],[514,4,515,4],[514,11,515,11],[514,13,515,13],[516,2,517,2],[516,4,517,4],[516,11,517,11],[516,13,517,13],[518,2,519,2],[518,4,519,4],[518,11,519,11],[518,13,519,13],[520,2,523,2],[520,11,523,11],[521,4,523,4],[521,13,523,13],[524,2,535,2],[524,4,526,4],[524,5,535,5],[524,11,535,11],[524,13,526,13],[524,14,535,14],[527,4,535,4],[527,13,535,13],[536,2,539,2],[536,11,539,11]],"flags":["formulas_cached_only"]}
[]
[]
[null,null,"CID2=42H",null," 获得系统模拟量量化后数据(定点数)",{"$nulls":6},"中国邮电电信总局文件（中国电信交换[1999]625号 基准）规格"]
[]
[null,null,"收集装置的代表数据。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"SOI",{"$nulls":4},"7EH",null,"0",null,"SOI",{"$nulls":4},"7EH",null,"0"]
[null,null,"VER",{"$nulls":3},"高BYTE","'2'",null,"1",null,"VER",{"$nulls":3},"高BYTE","'2'",null,"1"]
[{"$nulls":6},"低BYTE","'0'",null,"2",{"$nulls":5},"低BYTE","'0'",null,"2"]
[null,null,"ADR",{"$nulls":3},"高BYTE","*",null,"3",null,"ADR",{"$nulls":3},"高BYTE","*",null,"3"]
[{"$nulls":6},"低BYTE","*",null,"4",{"$nulls":5},"低BYTE","*",null,"4"]
[null,null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5",null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5"]
[{"$nulls":6},"低BYTE","'0'",null,"6",{"$nulls":5},"低BYTE","'0'",null,"6"]
[null,null,"CID2",{"$nulls":3},"高BYTE","'4'",null,"7",null,"RTN",{"$nulls":3},"高BYTE","*",null,"7"]
[{"$nulls":6},"低BYTE","'2'",null,"8",{"$nulls":5},"低BYTE","*",null,"8"]
[null,null,"LENGTH",null,"LCHKSUM",null,null,"'0'",null,"9",null,"LENGTH",null,"LCHKSUM",null,null,"'9'",null,"9"]
[{"$nulls":4},"LENID",null,null,"'0'",null,"10",{"$nulls":3},"LENID",null,null,"'0'",null,"10"]
[{"$nulls":6},"=0","'0'",null,"11",{"$nulls":5},"=52","'3'",null,"11"]
[{"$nulls":7},"'0'",null,"12",{"$nulls":6},"'4'",null,"12"]
[null,null,"CHKSUM",{"$nulls":3},"高BYTE","*",null,"13",null,"DATA\nINFO",null,"DATA\nFLAG",null,null,"*",null,"13"]
[{"$nulls":7},"*",null,"14",{"$nulls":6},"*",null,"14"]
[{"$nulls":7},"*",null,"15",{"$nulls":3},"DATAI","主机工作线/相电压AB/A",null,"20H",null,"15"]
[{"$nulls":6},"低BYTE","*",null,"16",{"$nulls":5},"（无相应数据）","20H",null,"16"]
[null,null,"EOI",{"$nulls":4},"0DH",null,"17",{"$nulls":6},"20H",null,"17"]
[{"$nulls":16},"20H",null,"18"]
[{"$nulls":14},"主机工作线/相电压BC/B",null,"20H",null,"19"]
[{"$nulls":15},"（无相应数据）","20H",null,"20"]
[{"$nulls":16},"20H",null,"21"]
[{"$nulls":16},"20H",null,"22"]
[{"$nulls":14},"主机工作线/相电压CA/C",null,"20H",null,"23"]
[{"$nulls":15},"（无相应数据）","20H",null,"24"]
[{"$nulls":16},"20H",null,"25"]
[{"$nulls":16},"20H",null,"26"]
[{"$nulls":14},"主机工作电流A相",null,"20H",null,"27"]
[{"$nulls":15},"（无相应数据）","20H",null,"28"]
[{"$nulls":16},"20H",null,"29"]
[{"$nulls":16},"20H",null,"30"]
[{"$nulls":14},"主机工作电流B相",null,"20H",null,"31"]
[{"$nulls":15},"（无相应数据）","20H",null,"32"]
[{"$nulls":16},"20H",null,"33"]
[{"$nulls":16},"20H",null,"34"]
[{"$nulls":14},"主机工作电流C相",null,"20H",null,"35"]
[{"$nulls":15},"（无相应数据）","20H",null,"36"]
[{"$nulls":16},"20H",null,"37"]
[{"$nulls":16},"20H",null,"38"]
[{"$nulls":14},"送风温度",null,"20H",null,"39"]
[{"$nulls":15},"（无相应数据）","20H",null,"40"]
[{"$nulls":16},"20H",null,"41"]
[{"$nulls":16},"20H",null,"42"]
[{"$nulls":14},"回风温度","高BYTE","*",null,"43"]
[{"$nulls":15},"吸い込み温度（゜C）","*",null,"44"]
[{"$nulls":15},"            X100","*",null,"45"]
[{"$nulls":15},"低BYTE","*",null,"46"]
[{"$nulls":14},"送风湿度",null,"20H",null,"47"]
[{"$nulls":15},"（无相应数据）","20H",null,"48"]
[{"$nulls":16},"20H",null,"49"]
[{"$nulls":16},"20H",null,"50"]
[{"$nulls":14},"回风湿度",null,"20H",null,"51"]
[{"$nulls":15},"（无相应数据）","20H",null,"52"]
[{"$nulls":16},"20H",null,"53"]
[{"$nulls":16},"20H",null,"54"]
[{"$nulls":14},"压缩机吸气压力",null,"20H",null,"55"]
[{"$nulls":15},"（无相应数据）","20H",null,"56"]
[{"$nulls":16},"20H",null,"57"]
[{"$nulls":16},"20H",null,"58"]
[{"$nulls":14},"压缩机排气压力",null,"20H",null,"59"]
[{"$nulls":15},"（无相应数据）","20H",null,"60"]
[{"$nulls":16},"20H",null,"61"]
[{"$nulls":16},"20H",null,"62"]
[{"$nulls":14},"用户自定义遥测数量P","（无相应数据）","'0'",null,"63"]
[{"$nulls":16},"'0'",null,"64"]
[{"$nulls":11},"CHKSUM",{"$nulls":3},"高BYTE","*",null,"65"]
[{"$nulls":16},"*",null,"66"]
[{"$nulls":16},"*",null,"67"]
[{"$nulls":15},"低BYTE","*",null,"68"]
[{"$nulls":11},"EOI",{"$nulls":4},"0DH",null,"69"]
{"$rows_empty":7}
[null,null,"CID2=43H",null," 获取开关输入状态",{"$nulls":6},"中国邮电电信总局文件（中国电信交換[1999]625号 基准）规格"]
[]
[null,null,"收集运转状态数据。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"SOI",{"$nulls":4},"7EH",null,"0",null,"SOI",{"$nulls":4},"7EH",null,"0"]
[null,null,"VER",{"$nulls":3},"高BYTE","'2'",null,"1",null,"VER",{"$nulls":3},"高BYTE","'2'",null,"1"]
[{"$nulls":6},"低BYTE","'0'",null,"2",{"$nulls":5},"低BYTE","'0'",null,"2"]
[null,null,"ADR",{"$nulls":3},"高BYTE","*",null,"3",null,"ADR",{"$nulls":3},"高BYTE","*",null,"3"]
[{"$nulls":6},"低BYTE","*",null,"4",{"$nulls":5},"低BYTE","*",null,"4"]
[null,null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5",null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5"]
[{"$nulls":6},"低BYTE","'0'",null,"6",{"$nulls":5},"低BYTE","'0'",null,"6"]
[null,null,"CID2",{"$nulls":3},"高BYTE","'4'",null,"7",null,"RTN",{"$nulls":3},"高BYTE","*",null,"7"]
[{"$nulls":6},"低BYTE","'3'",null,"8",{"$nulls":5},"低BYTE","*",null,"8"]
[null,null,"LENGTH",null,"LCHKSUM",null,null,"'0'",null,"9",null,"LENGTH",null,"LCHKSUM",null,null,"'7'",null,"9"]
[{"$nulls":4},"LENID",null,null,"'0'",null,"10",{"$nulls":3},"LENID",null,null,"'0'",null,"10"]
[{"$nulls":6},"=0","'0'",null,"11",{"$nulls":5},"=24","'1'",null,"11"]
[{"$nulls":7},"'0'",null,"12",{"$nulls":6},"'8'",null,"12"]
[null,null,"CHKSUM",{"$nulls":3},"高BYTE",null,null,"13",null,"DATA\nINFO",null,"DATA\nFLAG",null,null,"*",null,"13"]
[{"$nulls":9},"14",{"$nulls":6},"*",null,"14"]
[{"$nulls":9},"15",{"$nulls":3},"RUNSTATE","空调状态","00H:停止","*",null,"15"]
[{"$nulls":6},"低BYTE",null,null,"16",{"$nulls":5},"01H:运转","*",null,"16"]
[null,null,"EOI",{"$nulls":4},"0DH",null,"17",{"$nulls":4},"用户自定义状态数量P","=9","'0'",null,"17"]
[{"$nulls":16},"'9'",null,"18"]
[{"$nulls":14},"加湿器状态","00H:停止","*",null,"19"]
[{"$nulls":15},"01H:运转","*",null,"20"]
[{"$nulls":14},"电加热器状态","00H:停止","*",null,"21"]
[{"$nulls":15},"01H:运转","*",null,"22"]
[{"$nulls":14},"风扇状态","00H:停止","*",null,"23"]
[{"$nulls":15},"01H:运转","*",null,"24"]
[{"$nulls":14},"压缩机状态","00H:停止","*",null,"25"]
[{"$nulls":15},"01H:运转","*",null,"26"]
[{"$nulls":14},"过滤网状态","00H:OFF","*",null,"27"]
[{"$nulls":15},"01H:ON","*",null,"28"]
[{"$nulls":14},"注意报状态","00H:OFF","*",null,"29"]
[{"$nulls":15},"01H:ON","*",null,"30"]
[{"$nulls":14},"警报状态","00H:OFF","*",null,"31"]
[{"$nulls":15},"01H:ON","*",null,"32"]
[{"$nulls":14},"异常状态","00H:OFF","*",null,"33"]
[{"$nulls":15},"01H:ON","*",null,"34"]
[{"$nulls":14},"运转状态","00H:送风 ","*",null,"35"]
[{"$nulls":15},"01H:制热  02H:制冷","*",null,"36"]
[{"$nulls":11},"CHKSUM",{"$nulls":3},"高BYTE","*",null,"37"]
[{"$nulls":16},"*",null,"38"]
[{"$nulls":16},"*",null,"39"]
[{"$nulls":15},"低BYTE","*",null,"40"]
[{"$nulls":11},"EOI",{"$nulls":4},"0DH",null,"41"]
[]
[]
[]
[]
[]
[]
[null,null,"CID2=44H",null," 获取告警状态",{"$nulls":6},"中国邮电电信总局文件（中国电信交換[1999]625号 基准）规格"]
[]
[null,null,"收集警告状态数据。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"SOI",{"$nulls":4},"7EH",null,"0",null,"SOI",{"$nulls":4},"7EH",null,"0"]
[null,null,"VER",{"$nulls":3},"高BYTE","'2'",null,"1",null,"VER",{"$nulls":3},"高BYTE","'2'",null,"1"]
[{"$nulls":6},"低BYTE","'0'",null,"2",{"$nulls":5},"低BYTE","'0'",null,"2"]
[null,null,"ADR",{"$nulls":3},"高BYTE","*",null,"3",null,"ADR",{"$nulls":3},"高BYTE","*",null,"3"]
[{"$nulls":6},"低BYTE","*",null,"4",{"$nulls":5},"低BYTE","*",null,"4"]
[null,null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5",null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5"]
[{"$nulls":6},"低BYTE","'0'",null,"6",{"$nulls":5},"低BYTE","'0'",null,"6"]
[null,null,"CID2",{"$nulls":3},"高BYTE","'4'",null,"7",null,"RTN",{"$nulls":3},"高BYTE","*",null,"7"]
[{"$nulls":6},"低BYTE","'4'",null,"8",{"$nulls":5},"低BYTE","*",null,"8"]
[null,null,"LENGTH",null,"LCHKSUM",null,null,"'0'",null,"9",null,"LENGTH",null,"LCHKSUM",null,null,"'3'",null,"9"]
[{"$nulls":4},"LENID",null,null,"'0'",null,"10",{"$nulls":3},"LENID",null,null,"'0'",null,"10"]
[{"$nulls":6},"=0","'0'",null,"11",{"$nulls":5},"=28","'1'",null,"11"]
[{"$nulls":7},"'0'",null,"12",{"$nulls":6},"'C'",null,"12"]
[null,null,"CHKSUM",{"$nulls":3},"高BYTE",null,null,"13",null,"DATA\nINFO",null,"DATA\nFLAG",null,null,"*",null,"13"]
[{"$nulls":9},"14",{"$nulls":6},"*",null,"14"]
[{"$nulls":9},"15",{"$nulls":3},"WARNSTATE","主机工作线/相电压AB/A","（无相应数据）","20H",null,"15"]
[{"$nulls":6},"低BYTE",null,null,"16",{"$nulls":6},"20H",null,"16"]
[null,null,"EOI",{"$nulls":4},"0DH",null,"17",{"$nulls":4},"主机工作线/相电压BC/B","（无相应数据）","20H",null,"17"]
[{"$nulls":16},"20H",null,"18"]
[{"$nulls":14},"主机工作线/相电压CA/C","（无相应数据）","20H",null,"19"]
[{"$nulls":16},"20H",null,"20"]
[{"$nulls":14},"主机工作相电流A","（无相应数据）","20H",null,"21"]
[{"$nulls":16},"20H",null,"22"]
[{"$nulls":14},"主机工作相电流B","（无相应数据）","20H",null,"23"]
[{"$nulls":16},"20H",null,"24"]
[{"$nulls":14},"主机工作相电流C","（无相应数据）","20H",null,"25"]
[{"$nulls":16},"20H",null,"26"]
[{"$nulls":14},"回风温度","00H:正常　F0H:故障","*",null,"27"]
[{"$nulls":15},"01H:下限以下　02H:上限以上","*",null,"28"]
[{"$nulls":14},"回风湿度","（无相应数据）","20H",null,"29"]
[{"$nulls":16},"20H",null,"30"]
[{"$nulls":14},"过滤器","（无相应数据）","20H",null,"31"]
[{"$nulls":16},"20H",null,"32"]
[{"$nulls":14},"压缩机","（无相应数据）","20H",null,"33"]
[{"$nulls":16},"20H",null,"34"]
[{"$nulls":14},"风机","（无相应数据）","20H",null,"35"]
[{"$nulls":16},"20H",null,"36"]
[{"$nulls":14},"用户自定义告警数量P","=1","'0'",null,"37"]
[{"$nulls":16},"'1'",null,"38"]
[{"$nulls":14},"异常代码","（参考故障诊断用代码表）","*",null,"39"]
[{"$nulls":16},"*",null,"40"]
[{"$nulls":11},"CHKSUM",{"$nulls":3},"高BYTE","*",null,"41"]
[{"$nulls":16},"*",null,"42"]
[{"$nulls":16},"*",null,"43"]
[{"$nulls":15},"低BYTE","*",null,"44"]
[{"$nulls":11},"EOI",{"$nulls":4},"0DH",null,"45"]
[]
[]
[]
[]
[]
[]
[null,null,"CID2=45H",null,"遥控",{"$nulls":6},"中国邮电电信总局文件（中国电信交換[1999]625号 基准）规格"]
[]
[null,null,"远程控制运转/停止操作"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"SOI",{"$nulls":4},"7EH",null,"0",null,"SOI",{"$nulls":4},"7EH",null,"0"]
[null,null,"VER",{"$nulls":3},"高BYTE","'2'",null,"1",null,"VER",{"$nulls":3},"高BYTE","'2'",null,"1"]
[{"$nulls":6},"低BYTE","'0'",null,"2",{"$nulls":5},"低BYTE","'0'",null,"2"]
[null,null,"ADR",{"$nulls":3},"高BYTE","*",null,"3",null,"ADR",{"$nulls":3},"高BYTE","*",null,"3"]
[{"$nulls":6},"低BYTE","*",null,"4",{"$nulls":5},"低BYTE","*",null,"4"]
[null,null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5",null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5"]
[{"$nulls":6},"低BYTE","'0'",null,"6",{"$nulls":5},"低BYTE","'0'",null,"6"]
[null,null,"CID2",{"$nulls":3},"高BYTE","'4'",null,"7",null,"RTN",{"$nulls":3},"高BYTE","*",null,"7"]
[{"$nulls":6},"低BYTE","'5'",null,"8",{"$nulls":5},"低BYTE","*",null,"8"]
[null,null,"LENGTH",null,"LCHKSUM",null,null,"'E'",null,"9",null,"LENGTH",null,"LCHKSUM",null,null,"'0'",null,"9"]
[{"$nulls":4},"LENID",null,null,"'0'",null,"10",{"$nulls":3},"LENID",null,null,"'0'",null,"10"]
[{"$nulls":6},"=2","'0'",null,"11",{"$nulls":5},"=0","'0'",null,"11"]
[{"$nulls":7},"'2'",null,"12",{"$nulls":6},"'0'",null,"12"]
[null,null,"COMMAND\nINFO",null,"COMMAND\nTYPE",null,"空调操作","*",null,"13",null,"CHKSUM",{"$nulls":3},"高BYTE","*",null,"13"]
[{"$nulls":7},"*",null,"14",{"$nulls":6},"*",null,"14"]
[null,null,"CHKSUM",{"$nulls":3},"高BYTE","*",null,"15",{"$nulls":6},"*",null,"15"]
[{"$nulls":7},"*",null,"16",{"$nulls":5},"低BYTE","*",null,"16"]
[{"$nulls":7},"*",null,"17",null,"EOI",{"$nulls":4},"0DH",null,"17"]
[{"$nulls":6},"低BYTE","*",null,"18"]
[null,null,"EOI",{"$nulls":4},"0DH",null,"19"]
[]
[null,null,"空调操作 = 10H:运转 / 11H:顺次起动运转 / 1FH:停止"]
[]
[]
[]
[]
[]
[]
[null,null,"CID2=47H",null," 获取参数(定点数)",{"$nulls":6},"中国邮电电信总局文件（中国电信交換[1999]625号 基准）规格"]
[]
[null,null,"取得设定参数。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"SOI",{"$nulls":4},"7EH",null,"0",null,"SOI",{"$nulls":4},"7EH",null,"0"]
[null,null,"VER",{"$nulls":3},"高BYTE","'2'",null,"1",null,"VER",{"$nulls":3},"高BYTE","'2'",null,"1"]
[{"$nulls":6},"低BYTE","'0'",null,"2",{"$nulls":5},"低BYTE","'0'",null,"2"]
[null,null,"ADR",{"$nulls":3},"高BYTE","*",null,"3",null,"ADR",{"$nulls":3},"高BYTE","*",null,"3"]
[{"$nulls":6},"低BYTE","*",null,"4",{"$nulls":5},"低BYTE","*",null,"4"]
[null,null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5",null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5"]
[{"$nulls":6},"低BYTE","'0'",null,"6",{"$nulls":5},"低BYTE","'0'",null,"6"]
[null,null,"CID2",{"$nulls":3},"高BYTE","'4'",null,"7",null,"RTN",{"$nulls":3},"高BYTE","*",null,"7"]
[{"$nulls":6},"低BYTE","'７'",null,"8",{"$nulls":5},"低BYTE","*",null,"8"]
[null,null,"LENGTH",null,"LCHKSUM",null,null,"'0'",null,"9",null,"LENGTH",null,"LCHKSUM",null,null,"'5'",null,"9"]
[{"$nulls":4},"LENID",null,null,"'0'",null,"10",{"$nulls":3},"LENID",null,null,"'0'",null,"10"]
[{"$nulls":6},"=0","'0'",null,"11",{"$nulls":5},"=26","'1'",null,"11"]
[{"$nulls":7},"'0'",null,"12",{"$nulls":6},"'A'",null,"12"]
[null,null,"CHKSUM",{"$nulls":3},"高BYTE","*",null,"13",null,"DATA\nINFO",null,"DATAI","空调开机温度",null,"*",null,"13"]
[{"$nulls":7},"*",null,"14",{"$nulls":6},"*",null,"14"]
[{"$nulls":7},"*",null,"15",{"$nulls":6},"*",null,"15"]
[{"$nulls":6},"低BYTE","*",null,"16",{"$nulls":6},"*",null,"16"]
[null,null,"EOI",{"$nulls":4},"0DH",null,"17",{"$nulls":4},"空调关机温度",null,"*",null,"17"]
[{"$nulls":16},"*",null,"18"]
[{"$nulls":16},"*",null,"19"]
[{"$nulls":16},"*",null,"20"]
[{"$nulls":14},"回风温度上限",null,"*",null,"21"]
[{"$nulls":16},"*",null,"22"]
[{"$nulls":16},"*",null,"23"]
[{"$nulls":16},"*",null,"24"]
[{"$nulls":14},"回风温度下限",null,"*",null,"25"]
[{"$nulls":16},"*",null,"26"]
[{"$nulls":16},"*",null,"27"]
[{"$nulls":16},"*",null,"28"]
[{"$nulls":14},"回风湿度上限",null,"*",null,"29"]
[{"$nulls":16},"*",null,"30"]
[{"$nulls":16},"*",null,"31"]
[{"$nulls":16},"*",null,"32"]
[{"$nulls":14},"回风湿度下限",null,"*",null,"33"]
[{"$nulls":16},"*",null,"34"]
[{"$nulls":16},"*",null,"35"]
[{"$nulls":16},"*",null,"36"]
[{"$nulls":14},"用户自定义告警数量P","=0","'0'",null,"37"]
[{"$nulls":16},"'0'",null,"38"]
[{"$nulls":11},"CHKSUM",{"$nulls":3},"高BYTE","*",null,"39"]
[{"$nulls":16},"*",null,"40"]
[{"$nulls":16},"*",null,"41"]
[{"$nulls":15},"低BYTE","*",null,"42"]
[{"$nulls":11},"EOI",{"$nulls":4},"0DH",null,"43"]
[]
[]
[]
[]
[]
[]
[null,null,"CID2=49H",null,"设定参数(定点数)",{"$nulls":6},"中国邮电电信总局文件（中国电信交換[1999]625号 基准）规格"]
[]
[null,null,"设定参数。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"SOI",{"$nulls":4},"7EH",null,"0",null,"SOI",{"$nulls":4},"7EH",null,"0"]
[null,null,"VER",{"$nulls":3},"高BYTE","'2'",null,"1",null,"VER",{"$nulls":3},"高BYTE","'2'",null,"1"]
[{"$nulls":6},"低BYTE","'0'",null,"2",{"$nulls":5},"低BYTE","'0'",null,"2"]
[null,null,"ADR",{"$nulls":3},"高BYTE","*",null,"3",null,"ADR",{"$nulls":3},"高BYTE","*",null,"3"]
[{"$nulls":6},"低BYTE","*",null,"4",{"$nulls":5},"低BYTE","*",null,"4"]
[null,null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5",null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5"]
[{"$nulls":6},"低BYTE","'0'",null,"6",{"$nulls":5},"低BYTE","'0'",null,"6"]
[null,null,"CID2",{"$nulls":3},"高BYTE","'4'",null,"7",null,"RTN",{"$nulls":3},"高BYTE","*",null,"7"]
[{"$nulls":6},"低BYTE","'9'",null,"8",{"$nulls":5},"低BYTE","*",null,"8"]
[null,null,"LENGTH",null,"LCHKSUM",null,null,"'A'",null,"9",null,"LENGTH",null,"LCHKSUM",null,null,"'0'",null,"9"]
[{"$nulls":4},"LENID",null,null,"'0'",null,"10",{"$nulls":3},"LENID",null,null,"'0'",null,"10"]
[{"$nulls":6},"=6","'0'",null,"11",{"$nulls":5},"=0","'0'",null,"11"]
[{"$nulls":7},"'6'",null,"12",{"$nulls":6},"'0'",null,"12"]
[null,null,"COMMAND\nINFO",null,"COMMAND\nTYPE","指定设定参数","高BYTE","*",null,"13",null,"CHKSUM",{"$nulls":3},"高BYTE","*",null,"13"]
[{"$nulls":6},"低BYTE","*",null,"14",{"$nulls":6},"*",null,"14"]
[{"$nulls":4},"DATAI","表4．9．1参照","高BYTE","*",null,"15",{"$nulls":6},"*",null,"15"]
[{"$nulls":6},"设定值","*",null,"16",{"$nulls":5},"低BYTE","*",null,"16"]
[{"$nulls":7},"*",null,"17",null,"EOI",{"$nulls":4},"0DH",null,"17"]
[{"$nulls":6},"低BYTE","*",null,"18"]
[null,null,"CHKSUM",{"$nulls":3},"高BYTE","*",null,"19"]
[{"$nulls":7},"*",null,"20"]
[{"$nulls":7},"*",null,"21"]
[{"$nulls":6},"低BYTE","*",null,"22"]
[null,null,"EOI",{"$nulls":4},"0DH",null,"23"]
[]
[]
[]
[null,null,"表4．9．1",null,null,"COMMAND TYPE","内　　容"]
[]
[{"$nulls":5},"80H","空调开机温度"]
[{"$nulls":5},"81H","空调关机温度"]
[{"$nulls":5},"82H","回风温度上限"]
[{"$nulls":5},"83H","回风温度下限"]
[{"$nulls":5},"84H","回风湿度上限"]
[{"$nulls":5},"85H","回风湿度下限"]
[{"$nulls":5},"E0H…EFH","用户自定义"]
[]
[]
[]
[]
[]
[]
[null,null,"CID2=4FH",null," 获取通信协议版本号",{"$nulls":6},"中国邮电电信总局文件（中国电信交換[1999]625号 基准）规格"]
[]
[null,null,"取得通信协议版本情报。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"SOI",{"$nulls":4},"7EH",null,"0",null,"SOI",{"$nulls":4},"7EH",null,"0"]
[null,null,"VER",{"$nulls":3},"高BYTE","*",null,"1",null,"VER",{"$nulls":3},"高BYTE","'2'",null,"1"]
[{"$nulls":6},"低BYTE","*",null,"2",{"$nulls":5},"低BYTE","'0'",null,"2"]
[null,null,"ADR",{"$nulls":3},"高BYTE","*",null,"3",null,"ADR",{"$nulls":3},"高BYTE","*",null,"3"]
[{"$nulls":6},"低BYTE","*",null,"4",{"$nulls":5},"低BYTE","*",null,"4"]
[null,null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5",null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5"]
[{"$nulls":6},"低BYTE","'0'",null,"6",{"$nulls":5},"低BYTE","'0'",null,"6"]
[null,null,"CID2",{"$nulls":3},"高BYTE","'4'",null,"7",null,"RTN",{"$nulls":3},"高BYTE","*",null,"7"]
[{"$nulls":6},"低BYTE","'F'",null,"8",{"$nulls":5},"低BYTE","*",null,"8"]
[null,null,"LENGTH",null,"LCHKSUM",null,null,"'0'",null,"9",null,"LENGTH",null,"LCHKSUM",null,null,"'0'",null,"9"]
[{"$nulls":4},"LENID",null,null,"'0'",null,"10",{"$nulls":3},"LENID",null,null,"'0'",null,"10"]
[{"$nulls":6},"=0","'0'",null,"11",{"$nulls":5},"=0","'0'",null,"11"]
[{"$nulls":7},"'0'",null,"12",{"$nulls":6},"'0'",null,"12"]
[null,null,"CHKSUM",{"$nulls":3},"高BYTE","*",null,"13",null,"CHKSUM",{"$nulls":3},"高BYTE","*",null,"13"]
[{"$nulls":7},"*",null,"14",{"$nulls":6},"*",null,"14"]
[{"$nulls":7},"*",null,"15",{"$nulls":6},"*",null,"15"]
[{"$nulls":6},"低BYTE","*",null,"16",{"$nulls":5},"低BYTE","*",null,"16"]
[null,null,"EOI",{"$nulls":4},"0DH",null,"17",null,"EOI",{"$nulls":4},"0DH",null,"17"]
[]
[]
[]
[]
[]
[]
[null,null,"CID2=50H",null," 获取设备地址",{"$nulls":6},"中国邮电电信总局文件（中国电信交換[1999]625号 基准）规格"]
[]
[null,null,"取得SM地址情报。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"SOI",{"$nulls":4},"7EH",null,"0",null,"SOI",{"$nulls":4},"7EH",null,"0"]
[null,null,"VER",{"$nulls":3},"高BYTE","*",null,"1",null,"VER",{"$nulls":3},"高BYTE","'2'",null,"1"]
[{"$nulls":6},"低BYTE","*",null,"2",{"$nulls":5},"低BYTE","'0'",null,"2"]
[null,null,"ADR",{"$nulls":3},"高BYTE","*",null,"3",null,"ADR",{"$nulls":3},"高BYTE","*",null,"3"]
[{"$nulls":6},"低BYTE","*",null,"4",{"$nulls":5},"低BYTE","*",null,"4"]
[null,null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5",null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5"]
[{"$nulls":6},"低BYTE","'0'",null,"6",{"$nulls":5},"低BYTE","'0'",null,"6"]
[null,null,"CID2",{"$nulls":3},"高BYTE","'5'",null,"7",null,"RTN",{"$nulls":3},"高BYTE","*",null,"7"]
[{"$nulls":6},"低BYTE","'0'",null,"8",{"$nulls":5},"低BYTE","*",null,"8"]
[null,null,"LENGTH",null,"LCHKSUM",null,null,"'0'",null,"9",null,"LENGTH",null,"LCHKSUM",null,null,"'0'",null,"9"]
[{"$nulls":4},"LENID",null,null,"'0'",null,"10",{"$nulls":3},"LENID",null,null,"'0'",null,"10"]
[{"$nulls":6},"=0","'0'",null,"11",{"$nulls":5},"=0","'0'",null,"11"]
[{"$nulls":7},"'0'",null,"12",{"$nulls":6},"'0'",null,"12"]
[null,null,"CHKSUM",{"$nulls":3},"高BYTE","*",null,"13",null,"CHKSUM",{"$nulls":3},"高BYTE","*",null,"13"]
[{"$nulls":7},"*",null,"14",{"$nulls":6},"*",null,"14"]
[{"$nulls":7},"*",null,"15",{"$nulls":6},"*",null,"15"]
[{"$nulls":6},"低BYTE","*",null,"16",{"$nulls":5},"低BYTE","*",null,"16"]
[null,null,"EOI",{"$nulls":4},"0DH",null,"17",null,"EOI",{"$nulls":4},"0DH",null,"17"]
[]
[]
[]
[]
[]
[]
[null,null,"CID2=51H",null," 获取设备(监测模块)，厂家信息",{"$nulls":6},"中国邮电电信总局文件（中国电信交換[1999]625号 基准）规格"]
[]
[null,null,"取得设备(SM)情报、厂家情报 "]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"SOI",{"$nulls":4},"7EH",null,"0",null,"SOI",{"$nulls":4},"7EH",null,"0"]
[null,null,"VER",{"$nulls":3},"高BYTE","'2'",null,"1",null,"VER",{"$nulls":3},"高BYTE","'2'",null,"1"]
[{"$nulls":6},"低BYTE","'0'",null,"2",{"$nulls":5},"低BYTE","'0'",null,"2"]
[null,null,"ADR",{"$nulls":3},"高BYTE","*",null,"3",null,"ADR",{"$nulls":3},"高BYTE","*",null,"3"]
[{"$nulls":6},"低BYTE","*",null,"4",{"$nulls":5},"低BYTE","*",null,"4"]
[null,null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5",null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5"]
[{"$nulls":6},"低BYTE","'0'",null,"6",{"$nulls":5},"低BYTE","'0'",null,"6"]
[null,null,"CID2",{"$nulls":3},"高BYTE","'5'",null,"7",null,"RTN",{"$nulls":3},"高BYTE","*",null,"7"]
[{"$nulls":6},"低BYTE","'1'",null,"8",{"$nulls":5},"低BYTE","*",null,"8"]
[null,null,"LENGTH",null,"LCHKSUM",null,null,"'0'",null,"9",null,"LENGTH",null,"LCHKSUM",null,null,"'C'",null,"9"]
[{"$nulls":4},"LENID",null,null,"'0'",null,"10",{"$nulls":3},"LENID",null,null,"'0'",null,"10"]
[{"$nulls":6},"=0","'0'",null,"11",{"$nulls":5},"=64","'4'",null,"11"]
[{"$nulls":7},"'0'",null,"12",{"$nulls":6},"'0'",null,"12"]
[null,null,"CHKSUM",{"$nulls":3},"高BYTE","*",null,"13",null,"DATA\nINFO",null,"采集器名称",null,"'D'","'4'",null,"13"]
[{"$nulls":7},"*",null,"14",{"$nulls":6},"'4'",null,"14"]
[{"$nulls":7},"*",null,"15",{"$nulls":5},"'I'","'4'",null,"15"]
[{"$nulls":6},"低BYTE","*",null,"16",{"$nulls":6},"'9'",null,"16"]
[null,null,"EOI",{"$nulls":4},"0DH",null,"17",{"$nulls":5},"'S'","'5'",null,"17"]
[{"$nulls":16},"'3'",null,"18"]
[{"$nulls":15},"'2'","'3'",null,"19"]
[{"$nulls":16},"'2'",null,"20"]
[{"$nulls":15},"'0'","'3'",null,"21"]
[{"$nulls":16},"'0'",null,"22"]
[{"$nulls":15},"'0'","'3'",null,"23"]
[{"$nulls":16},"'0'",null,"24"]
[{"$nulls":15},"'1'","'3'",null,"25"]
[{"$nulls":16},"'1'",null,"26"]
[{"$nulls":15},"' '","'2'",null,"27"]
[{"$nulls":16},"'0'",null,"28"]
[{"$nulls":15},"' '","'2'",null,"29"]
[{"$nulls":16},"'0'",null,"30"]
[{"$nulls":15},"' '","'2'",null,"31"]
[{"$nulls":16},"'0'",null,"32"]
[{"$nulls":13},"厂家软件\n版本",null,"'V'","'5'",null,"33"]
[{"$nulls":16},"'6'",null,"34"]
[{"$nulls":15},"'1'","'3'",null,"35"]
[{"$nulls":16},"'1'",null,"36"]
[{"$nulls":13},"厂家名称",null,"'S'","'5'",null,"37"]
[{"$nulls":16},"'3'",null,"38"]
[{"$nulls":15},"'H'","'4'",null,"39"]
[{"$nulls":16},"'8'",null,"40"]
[{"$nulls":15},"'A'","'4'",null,"41"]
[{"$nulls":16},"'1'",null,"42"]
[{"$nulls":15},"'N'","'4'",null,"43"]
[{"$nulls":16},"'E'",null,"44"]
[{"$nulls":15},"'G'","'4'",null,"45"]
[{"$nulls":16},"'7'",null,"46"]
[{"$nulls":15},"'H'","'4'",null,"47"]
[{"$nulls":16},"'8'",null,"48"]
[{"$nulls":15},"'A'","'4'",null,"49"]
[{"$nulls":16},"'1'",null,"50"]
[{"$nulls":15},"'I'","'4'",null,"51"]
[{"$nulls":16},"'9'",null,"52"]
[{"$nulls":15},"' '","'2'",null,"53"]
[{"$nulls":16},"'0'",null,"54"]
[{"$nulls":15},"'D'","'4'",null,"55"]
[{"$nulls":16},"'4'",null,"56"]
[{"$nulls":15},"'A'","'4'",null,"57"]
[{"$nulls":16},"'1'",null,"58"]
[{"$nulls":15},"'I'","'4'",null,"59"]
[{"$nulls":16},"'9'",null,"60"]
[{"$nulls":15},"'K'","'4'",null,"61"]
[{"$nulls":16},"'B'",null,"62"]
[{"$nulls":15},"'I'","'4'",null,"63"]
[{"$nulls":16},"'9'",null,"64"]
[{"$nulls":15},"'N'","'4'",null,"65"]
[{"$nulls":16},"'E'",null,"66"]
[{"$nulls":15},"' '","'2'",null,"67"]
[{"$nulls":16},"'0'",null,"68"]
[{"$nulls":15},"' '","'2'",null,"69"]
[{"$nulls":16},"'0'",null,"70"]
[{"$nulls":15},"' '","'2'",null,"71"]
[{"$nulls":16},"'0'",null,"72"]
[{"$nulls":15},"' '","'2'",null,"73"]
[{"$nulls":16},"'0'",null,"74"]
[{"$nulls":15},"' '","'2'",null,"75"]
[{"$nulls":16},"'0'",null,"76"]
[{"$nulls":11},"CHKSUM",{"$nulls":3},"高BYTE","*",null,"77"]
[{"$nulls":16},"*",null,"78"]
[{"$nulls":16},"*",null,"79"]
[{"$nulls":15},"低BYTE","*",null,"80"]
[{"$nulls":11},"EOI",{"$nulls":4},"0DH",null,"81"]
[]
[]
[null,null,"CID2=E0H",{"$nulls":8},"中国邮电电信总局文件（中国电信交換[1999]625号 基准）规格"]
[]
[]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"SOI",{"$nulls":4},"7EH",null,"0",null,"SOI",{"$nulls":4},"7EH",null,"0"]
[null,null,"VER",{"$nulls":3},"高BYTE","'2'",null,"1",null,"VER",{"$nulls":3},"高BYTE","'2'",null,"1"]
[{"$nulls":6},"低BYTE","'0'",null,"2",{"$nulls":5},"低BYTE","'0'",null,"2"]
[null,null,"ADR",{"$nulls":3},"高BYTE","*",null,"3",null,"ADR",{"$nulls":3},"高BYTE","*",null,"3"]
[{"$nulls":6},"低BYTE","*",null,"4",{"$nulls":5},"低BYTE","*",null,"4"]
[null,null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5",null,"CID1",{"$nulls":3},"高BYTE","'6'",null,"5"]
[{"$nulls":6},"低BYTE","'0'",null,"6",{"$nulls":5},"低BYTE","'0'",null,"6"]
[null,null,"CID2",{"$nulls":3},"高BYTE","'E'",null,"7",null,"RTN",{"$nulls":3},"高BYTE","*",null,"7"]
[{"$nulls":6},"低BYTE","'0'",null,"8",{"$nulls":5},"低BYTE","*",null,"8"]
[null,null,"LENGTH",null,"LCHKSUM",null,null,"*",null,"9",null,"LENGTH",null,"LCHKSUM",null,null,"*",null,"9"]
[{"$nulls":4},"LENID",null,null,"*",null,"10",{"$nulls":3},"LENID",null,null,"*",null,"10"]
[{"$nulls":6},"INFO长度","*",null,"11",{"$nulls":6},"*",null,"11"]
[{"$nulls":7},"*",null,"12",{"$nulls":6},"*",null,"12"]
[null,null,"COMMAND\nINFO",null,"识别部","指令·回复一览表\n（独有规格）\n的情报",null,"*",null,"13",null,"DATA\nINFO",null,"识别部","指令·回复一览表\n（独有规格）\n的情报",null,"*",null,"13"]
[{"$nulls":7},"*",null,"14",{"$nulls":6},"*",null,"14"]
[{"$nulls":7},"*",null,"15",{"$nulls":6},"*",null,"15"]
[{"$nulls":4},"数据部",null,null,"*",null,"16",{"$nulls":3},"数据部",null,null,"*",null,"16"]
[{"$nulls":7},"*",null,"17",{"$nulls":6},"*",null,"17"]
{"$rows_empty":7}
[null,null,"CHKSUM",{"$nulls":3},"高BYTE","*",{"$nulls":3},"CHKSUM",{"$nulls":3},"高BYTE","*"]
[{"$nulls":7},"*",{"$nulls":8},"*"]
[{"$nulls":7},"*",{"$nulls":8},"*"]
[{"$nulls":6},"低BYTE","*",{"$nulls":7},"低BYTE","*"]
[null,null,"EOI",{"$nulls":4},"0DH",null,"x",null,"EOI",{"$nulls":4},"0DH",null,"y"]

{"sheet":"４．２上位ユニット通信機能<7>","index":19,"n_rows":1439,"n_cols":19,"rows_kept":1439,"merged":[[2,4,2,6],[2,11,2,18],[4,2,5,18],[7,2,8,2],[7,4,7,7],[7,9,8,9],[7,11,8,11],[7,13,7,16],[7,18,8,18],[8,4,8,5],[8,13,8,14],[11,2,13,2],[11,11,13,11],[22,4,22,6],[22,11,22,18],[24,2,25,18],[27,2,28,2],[27,4,27,7],[27,9,28,9],[27,11,28,11],[27,13,27,16],[27,18,28,18],[28,4,28,5],[28,13,28,14],[31,2,33,2],[31,11,33,11],[34,2,37,2],[34,4,37,4],[34,5,37,5],[34,11,49,11],[34,13,49,13],[34,14,35,14],[36,14,37,14],[38,14,39,14],[40,14,41,14],[42,14,43,14],[44,14,45,14],[46,14,47,14],[48,14,49,14],[58,4,58,6],[58,11,58,18],[60,2,61,18],[63,2,64,2],[63,4,63,7],[63,9,64,9],[63,11,64,11],[63,13,63,16],[63,18,64,18],[64,4,64,5],[64,13,64,14],[67,2,69,2],[67,11,69,11],[70,2,75,2],[70,4,73,4],[70,5,73,5],[74,4,75,4],[74,5,75,5],[84,4,84,6],[84,11,84,18],[86,2,87,18],[89,2,90,2],[89,4,89,7],[89,9,90,9],[89,11,90,11],[89,13,89,16],[89,18,90,18],[90,4,90,5],[90,13,90,14],[93,2,95,2],[93,11,95,11],[96,11,111,11],[96,13,111,13],[124,4,124,6],[124,11,124,18],[126,2,127,18],[129,2,130,2],[129,4,129,7],[129,9,130,9],[129,11,130,11],[129,13,129,16],[129,18,130,18],[130,4,130,5],[130,13,130,14],[133,2,135,2],[133,11,135,11],[136,2,143,2],[136,4,143,4],[164,4,164,6],[164,11,164,18],[166,2,167,18],[169,2,170,2],[169,4,169,7],[169,9,170,9],[169,11,170,11],[169,13,169,16],[169,18,170,18],[170,4,170,5],[170,13,170,14],[173,2,175,2],[173,11,175,11],[176,2,183,2],[176,4,183,4],[197,4,197,6],[197,11,197,18],[199,2,200,18],[202,2,203,2],[202,4,202,7],[202,9,203,9],[202,11,203,11],[202,13,202,16],[202,18,203,18],[203,4,203,5],[203,13,203,14],[206,2,208,2],[206,11,208,11],[209,2,238,2],[209,4,238,4],[266,18,267,18],[269,2,298,2],[269,3,269,4],[270,3,270,4],[271,3,271,4],[272,3,272,4],[273,3,273,4],[274,3,274,4],[275,3,275,4],[276,3,276,4],[277,3,277,4],[278,3,278,4],[279,3,279,4],[280,3,280,4],[281,3,281,4],[282,3,282,4],[283,3,283,4],[284,3,284,4],[285,3,285,4],[286,3,286,4],[287,3,287,4],[288,3,288,4],[289,3,289,4],[290,3,290,4],[291,3,291,4],[292,3,292,4],[293,3,293,4],[294,3,294,4],[295,3,295,4],[296,3,296,4],[297,3,297,4],[298,3,298,4],[313,2,342,2],[313,3,313,4],[314,3,314,4],[315,3,315,4],[315,6,316,11],[316,3,316,4],[317,3,317,4],[318,3,318,4],[319,3,319,4],[320,3,320,4],[321,3,321,4],[322,3,322,4],[323,3,323,4],[324,3,324,4],[325,3,325,4],[326,3,326,4],[327,3,327,4],[328,3,328,4],[328,6,329,14],[329,3,329,4],[330,3,330,4],[331,3,331,4],[332,3,332,4],[333,3,333,4],[334,3,334,4],[335,3,335,4],[336,3,336,4],[337,3,337,4],[338,3,338,4],[339,3,339,4],[340,3,340,4],[341,3,341,4],[342,3,342,4],[349,4,349,6],[349,11,349,18],[351,2,352,18],[354,2,355,2],[354,4,354,7],[354,9,355,9],[354,11,355,11],[354,13,354,16],[354,18,355,18],[355,4,355,5],[355,13,355,14],[358,2,360,2],[358,11,360,11],[361,2,376,2],[361,4,376,4],[381,2,396,2],[381,3,381,4],[382,3,382,4],[383,3,383,4],[384,3,384,4],[385,3,385,4],[386,3,386,4],[387,3,387,4],[388,3,388,4],[389,3,389,4],[390,3,390,4],[391,3,391,4],[392,3,392,4],[393,3,393,4],[394,3,394,4],[395,3,395,4],[396,3,396,4],[406,4,406,6],[406,11,406,18],[408,2,409,18],[411,2,412,2],[411,4,411,7],[411,9,412,9],[411,11,412,11],[411,13,411,16],[411,18,412,18],[412,4,412,5],[412,13,412,14],[415,2,417,2],[415,11,417,11],[418,2,421,2],[418,4,421,4],[418,5,419,5],[420,5,421,5],[426,2,429,2],[426,3,426,4],[427,3,427,4],[428,3,428,4],[429,3,429,4],[441,4,441,6],[441,11,441,18],[443,2,444,18],[446,2,447,2],[446,4,446,7],[446,9,447,9],[446,11,447,11],[446,13,446,16],[446,18,447,18],[447,4,447,5],[447,13,447,14],[450,2,452,2],[450,11,452,11],[453,2,456,2],[453,4,456,4],[453,5,454,5],[455,5,456,5],[461,2,464,2],[461,3,461,4],[462,3,462,4],[463,3,463,4],[464,3,464,4],[476,4,476,6],[476,11,476,18],[478,2,479,18],[481,2,482,2],[481,4,481,7],[481,9,482,9],[481,11,482,11],[481,13,481,16],[481,18,482,18],[482,4,482,5],[482,13,482,14],[485,2,487,2],[485,11,487,11],[502,4,502,6],[502,11,502,18],[504,2,505,18],[507,2,508,2],[507,4,507,7],[507,9,508,9],[507,11,508,11],[507,13,507,16],[507,18,508,18],[508,4,508,5],[508,13,508,14],[511,2,513,2],[511,11,513,11],[514,2,515,2],[514,4,515,4],[514,5,515,5],[522,2,523,2],[522,3,522,4],[523,3,523,4],[533,4,533,6],[533,11,533,18],[535,2,536,18],[538,2,539,2],[538,4,538,7],[538,9,539,9],[538,11,539,11],[538,13,538,16],[538,18,539,18],[539,4,539,5],[539,13,539,14],[542,2,544,2],[542,11,544,11],[559,4,559,6],[559,11,559,18],[561,2,562,18],[564,2,565,2],[564,4,564,7],[564,9,565,9],[564,11,565,11],[564,13,564,16],[564,18,565,18],[565,4,565,5],[565,13,565,14],[568,2,570,2],[568,11,570,11],[571,2,572,2],[571,4,572,4],[571,5,572,5],[580,2,581,2],[580,3,580,4],[581,3,581,4],[591,4,591,6],[591,11,591,18],[593,2,594,18],[596,2,597,2],[596,4,596,7],[596,9,597,9],[596,11,597,11],[596,13,596,16],[596,18,597,18],[597,4,597,5],[597,13,597,14],[600,2,602,2],[600,11,602,11],[617,4,617,6],[617,11,617,18],[619,2,620,18],[622,2,623,2],[622,4,622,7],[622,9,623,9],[622,11,623,11],[622,13,622,16],[622,18,623,18],[623,4,623,5],[623,13,623,14],[626,2,628,2],[626,11,628,11],[629,2,630,2],[650,4,650,6],[650,11,650,18],[652,2,653,18],[655,2,656,2],[655,4,655,7],[655,9,656,9],[655,11,656,11],[655,13,655,16],[655,18,656,18],[656,4,656,5],[656,13,656,14],[659,2,661,2],[659,11,661,11],[662,11,667,11],[662,13,663,13],[662,14,663,14],[664,13,665,13],[664,14,665,14],[666,13,667,13],[666,14,667,14],[672,11,677,11],[672,12,672,13],[672,15,673,15],[673,12,673,13],[674,12,674,13],[674,15,675,15],[675,12,675,13],[676,12,676,13],[676,15,677,15],[677,12,677,13],[684,4,684,6],[684,11,684,18],[686,2,687,18],[689,2,690,2],[689,4,689,7],[689,9,690,9],[689,11,690,11],[689,13,689,16],[689,18,690,18],[690,4,690,5],[690,13,690,14],[693,2,695,2],[693,11,695,11],[696,11,697,11],[696,13,697,13],[696,14,697,14],[705,3,705,4],[705,11,706,11],[705,12,705,13],[706,12,706,13],[713,4,713,6],[713,11,713,18],[715,2,716,18],[718,2,719,2],[718,4,718,7],[718,9,719,9],[718,11,719,11],[718,13,718,16],[718,18,719,18],[719,4,719,5],[719,13,719,14],[722,2,724,2],[722,11,724,11],[725,11,739,11],[730,13,731,13],[730,14,731,14],[732,13,733,13],[732,14,733,14],[734,13,735,13],[734,14,735,14],[736,13,737,13],[736,14,737,14],[769,4,769,6],[769,11,769,18],[771,2,772,18],[774,2,775,2],[774,4,774,7],[774,9,775,9],[774,11,775,11],[774,13,774,16],[774,18,775,18],[775,4,775,5],[775,13,775,14],[778,2,780,2],[778,11,780,11],[781,2,783,2],[781,11,806,11],[782,4,783,4],[782,5,783,5],[785,13,786,13],[787,13,790,13],[787,14,790,14],[791,13,794,13],[791,14,794,14],[795,13,798,13],[795,14,798,14],[799,13,801,13],[799,14,801,14],[802,13,804,13],[802,14,804,14],[840,4,840,6],[840,11,840,18],[842,2,843,18],[845,2,846,2],[845,4,845,7],[845,9,846,9],[845,11,846,11],[845,13,845,16],[845,18,846,18],[846,4,846,5],[846,13,846,14],[849,2,851,2],[849,11,851,11],[852,11,855,11],[877,11,880,11],[877,12,877,13],[878,12,878,13],[879,12,879,13],[880,12,880,13],[890,4,890,6],[890,11,890,18],[892,2,893,18],[895,2,896,2],[895,4,895,7],[895,9,896,9],[895,11,896,11],[895,13,895,16],[895,18,896,18],[896,4,896,5],[896,13,896,14],[899,2,901,2],[899,11,901,11],[910,4,910,6],[910,11,910,18],[912,2,913,18],[915,2,916,2],[915,4,915,7],[915,9,916,9],[915,11,916,11],[915,13,915,16],[915,18,916,18],[916,4,916,5],[916,13,916,14],[919,2,921,2],[919,11,921,11],[922,2,923,2],[936,4,936,7],[936,11,936,18],[938,2,939,18],[941,2,942,2],[941,4,941,7],[941,9,942,9],[941,11,942,11],[941,13,941,16],[941,18,942,18],[942,4,942,5],[942,13,942,14],[945,2,947,2],[945,11,947,11],[960,4,960,6],[960,11,960,18],[962,2,963,18],[965,2,966,2],[965,4,965,7],[965,9,966,9],[965,11,966,11],[965,13,965,16],[965,18,966,18],[966,4,966,5],[966,13,966,14],[969,2,971,2],[969,11,971,11],[972,2,973,2],[993,4,993,6],[993,11,993,18],[995,2,996,18],[998,2,999,2],[998,4,998,7],[998,9,999,9],[998,11,999,11],[998,13,998,16],[998,18,999,18],[999,4,999,5],[999,13,999,14],[1002,2,1004,2],[1002,11,1004,11],[1005,2,1011,2],[1006,4,1008,4],[1006,5,1008,5],[1009,4,1011,4],[1009,5,1011,5],[1028,4,1028,6],[1028,11,1028,18],[1030,2,1031,18],[1033,2,1034,2],[1033,4,1033,7],[1033,9,1034,9],[1033,11,1034,11],[1033,13,1033,16],[1033,18,1034,18],[1034,4,1034,5],[1034,13,1034,14],[1037,2,1039,2],[1037,11,1039,11],[1040,2,1044,2],[1065,4,1065,6],[1065,11,1065,18],[1067,2,1068,18],[1070,2,1071,2],[1070,4,1070,7],[1070,9,1071,9],[1070,11,1071,11],[1070,13,1070,16],[1070,18,1071,18],[1071,4,1071,5],[1071,13,1071,14],[1074,2,1076,2],[1074,11,1076,11],[1077,11,1106,11],[1077,13,1106,13],[1115,4,1115,6],[1115,11,1115,18],[1117,2,1118,18],[1120,2,1121,2],[1120,4,1120,7],[1120,9,1121,9],[1120,11,1121,11],[1120,13,1120,16],[1120,18,1121,18],[1121,4,1121,5],[1121,13,1121,14],[1124,2,1126,2],[1124,11,1126,11],[1127,11,1142,11],[1127,13,1142,13],[1147,11,1162,11],[1147,12,1147,13],[1148,12,1148,13],[1149,12,1149,13],[1150,12,1150,13],[1151,12,1151,13],[1152,12,1152,13],[1153,12,1153,13],[1154,12,1154,13],[1155,12,1155,13],[1156,12,1156,13],[1157,12,1157,13],[1158,12,1158,13],[1159,12,1159,13],[1160,12,1160,13],[1161,12,1161,13],[1162,12,1162,13],[1169,4,1169,6],[1169,11,1169,18],[1171,2,1172,18],[1174,2,1175,2],[1174,4,1174,7],[1174,9,1175,9],[1174,11,1175,11],[1174,13,1174,16],[1174,18,1175,18],[1175,4,1175,5],[1175,13,1175,14],[1178,2,1180,2],[1178,11,1180,11],[1181,11,1184,11],[1181,13,1184,13],[1181,14,1182,14],[1183,14,1184,14],[1189,11,1192,11],[1189,12,1189,13],[1190,12,1190,13],[1191,12,1191,13],[1192,12,1192,13],[1199,4,1199,6],[1199,11,1199,18],[1201,2,1202,18],[1204,2,1205,2],[1204,4,1204,7],[1204,9,1205,9],[1204,11,1205,11],[1204,13,1204,16],[1204,18,1205,18],[1205,4,1205,5],[1205,13,1205,14],[1208,2,1210,2],[1208,11,1210,11],[1211,11,1214,11],[1211,13,1214,13],[1211,14,1212,14],[1213,14,1214,14],[1219,11,1222,11],[1219,12,1219,13],[1220,12,1220,13],[1221,12,1221,13],[1222,12,1222,13],[1229,4,1229,6],[1229,11,1229,18],[1231,2,1232,18],[1234,2,1235,2],[1234,4,1234,7],[1234,9,1235,9],[1234,11,1235,11],[1234,13,1234,16],[1234,18,1235,18],[1235,4,1235,5],[1235,13,1235,14],[1238,2,1240,2],[1238,11,1240,11],[1252,4,1252,6],[1252,11,1252,18],[1254,2,1255,18],[1257,2,1258,2],[1257,4,1257,7],[1257,9,1258,9],[1257,11,1258,11],[1257,13,1257,16],[1257,18,1258,18],[1258,4,1258,5],[1258,13,1258,14],[1261,2,1263,2],[1261,11,1263,11],[1264,11,1265,11],[1264,13,1265,13],[1264,14,1265,14],[1272,11,1273,11],[1272,12,1272,13],[1273,12,1273,13],[1280,4,1280,6],[1280,11,1280,18],[1282,2,1283,18],[1285,2,1286,2],[1285,4,1285,7],[1285,9,1286,9],[1285,11,1286,11],[1285,13,1285,16],[1285,18,1286,18],[1286,4,1286,5],[1286,13,1286,14],[1289,2,1291,2],[1289,11,1291,11],[1303,4,1303,6],[1303,11,1303,18],[1305,2,1306,18],[1308,2,1309,2],[1308,4,1308,7],[1308,9,1309,9],[1308,11,1309,11],[1308,13,1308,16],[1308,18,1309,18],[1309,4,1309,5],[1309,13,1309,14],[1312,2,1314,2],[1312,11,1314,11],[1315,11,1316,11],[1315,13,1316,13],[1315,14,1316,14],[1324,11,1325,11],[1324,12,1324,13],[1325,12,1325,13],[1332,4,1332,6],[1332,11,1332,18],[1334,2,1335,18],[1337,2,1338,2],[1337,4,1337,7],[1337,9,1338,9],[1337,11,1338,11],[1337,13,1337,16],[1337,18,1338,18],[1338,4,1338,5],[1338,13,1338,14],[1341,2,1343,2],[1341,11,1343,11],[1355,4,1355,6],[1355,11,1355,18],[1357,2,1358,18],[1360,2,1361,2],[1360,4,1360,7],[1360,9,1361,9],[1360,11,1361,11],[1360,13,1360,16],[1360,18,1361,18],[1361,4,1361,5],[1361,13,1361,14],[1364,2,1366,2],[1364,11,1366,11],[1367,11,1368,11],[1385,4,1385,6],[1385,11,1385,18],[1387,2,1388,18],[1390,11,1391,11],[1390,13,1390,16],[1390,18,1391,18],[1391,13,1391,14],[1394,11,1396,11],[1405,4,1405,6],[1405,11,1405,18],[1407,2,1408,18],[1410,11,1411,11],[1410,13,1410,16],[1410,18,1411,18],[1411,13,1411,14],[1414,11,1416,11],[1425,4,1425,6],[1425,11,1425,18],[1427,2,1428,18],[1430,11,1431,11],[1430,13,1430,16],[1430,18,1431,18],[1431,13,1431,14],[1434,11,1436,11]],"flags":["formulas_cached_only"]}
[]
[]
[null,null,"000",null,"回线切断要求",{"$nulls":6},"独有规格"]
[]
[null,null,"要求接口切断回线通信。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'0'",null,"1",null,"识别部",{"$nulls":4},"'0'",null,"1"]
[{"$nulls":7},"'0'",null,"2",{"$nulls":6},"'0'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"ETX",{"$nulls":4},"03H",null,"4",null,"ETX",{"$nulls":4},"03H",null,"4"]
[null,null,"BCC",{"$nulls":4},"*",null,"5",null,"BCC",{"$nulls":4},"*",null,"5"]
[]
[]
[]
[]
[]
[]
[null,null,"0E0",null,"RAM读出",{"$nulls":6},"独有规格"]
[]
[null,null,"读出接口RAM中数据。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'0'",null,"1",null,"识别部",{"$nulls":4},"'0'",null,"1"]
[{"$nulls":7},"'E'",null,"2",{"$nulls":6},"'E'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,null,"读出先头RAM地址","高位        16^3","*",null,"4",null,"数据部",null,"RAM读出数据","第1字节数据","高位        16^1","*",null,"4"]
[{"$nulls":6},"　　        16^2","*",null,"5",{"$nulls":5},"低位        16^0","*",null,"5"]
[{"$nulls":6},"　　        16^1","*",null,"6",{"$nulls":4},"第2字节数据","高位        16^1","*",null,"6"]
[{"$nulls":6},"低位        16^0","*",null,"7",{"$nulls":5},"低位        16^0","*",null,"7"]
[null,null,"ETX",{"$nulls":4},"03H",null,"8",{"$nulls":4},"第3字节数据","高位        16^1","*",null,"8"]
[null,null,"BCC",{"$nulls":4},"*",null,"9",{"$nulls":5},"低位        16^0","*",null,"9"]
[{"$nulls":14},"第4字节数据","高位        16^1","*",null,"10"]
[{"$nulls":15},"低位        16^0","*",null,"11"]
[{"$nulls":14},"第5字节数据","高位        16^1","*",null,"12"]
[{"$nulls":15},"低位        16^0","*",null,"13"]
[{"$nulls":14},"第6字节数据","高位        16^1","*",null,"14"]
[{"$nulls":15},"低位        16^0","*",null,"15"]
[{"$nulls":14},"第7字节数据","高位        16^1","*",null,"16"]
[{"$nulls":15},"低位        16^0","*",null,"17"]
[{"$nulls":14},"第8字节数据","高位        16^1","*",null,"18"]
[{"$nulls":15},"低位        16^0","*",null,"19"]
[{"$nulls":11},"ETX",{"$nulls":4},"03H",null,"20"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"21"]
[]
[]
[]
[]
[]
[]
[null,null,"0F0",null,"RAM记入",{"$nulls":6},"独有规格"]
[]
[null,null,"接口RAM数据记入。记入数据为1个BYTE单位。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'0'",null,"1",null,"识别部",{"$nulls":4},"'0'",null,"1"]
[{"$nulls":7},"'F'",null,"2",{"$nulls":6},"'F'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,null,"记入RAM地址","高位        16^3","*",null,"4",null,"ETX",{"$nulls":4},"03H",null,"4"]
[{"$nulls":6},"　　        16^2","*",null,"5",null,"BCC",{"$nulls":4},"*",null,"5"]
[{"$nulls":6},"　　        16^1","*",null,"6"]
[{"$nulls":6},"低位        16^0","*",null,"7"]
[{"$nulls":5},"记入数据","高位        16^1","*",null,"8"]
[{"$nulls":6},"低位        16^0","*",null,"9"]
[null,null,"ETX",{"$nulls":4},"03H",null,"10"]
[null,null,"BCC",{"$nulls":4},"*",null,"11"]
[]
[]
[]
[]
[]
[]
[null,null,"100",null,"登录：接口ID确认",{"$nulls":6},"独有规格"]
[]
[null,null,"确认接口ID。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'1'",null,"1",null,"识别部",{"$nulls":4},"'1'",null,"1"]
[{"$nulls":7},"'0'",null,"2",{"$nulls":6},"'0'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"ETX",{"$nulls":4},"03H",null,"4",null,"数据部",null,"接口ID","第1行","初期值 'F'","*",null,"4"]
[null,null,"BCC",{"$nulls":4},"*",null,"5",{"$nulls":4},"第2行","初期值 'F'","*",null,"5"]
[{"$nulls":14},"第3行","初期值 'F'","*",null,"6"]
[{"$nulls":14},"第4行","初期值 'F'","*",null,"7"]
[{"$nulls":14},"第5行","初期值 'F'","*",null,"8"]
[{"$nulls":14},"第6行","初期值 'F'","*",null,"9"]
[{"$nulls":14},"第7行","初期值 'F'","*",null,"10"]
[{"$nulls":14},"第8行","初期值 'F'","*",null,"11"]
[{"$nulls":14},"第9行","初期值 'F'","*",null,"12"]
[{"$nulls":14},"第10行","初期值 'F'","*",null,"13"]
[{"$nulls":14},"第11行","初期值 'F'","*",null,"14"]
[{"$nulls":14},"第12行","初期值 'F'","*",null,"15"]
[{"$nulls":14},"第13行","初期值 'F'","*",null,"16"]
[{"$nulls":14},"第14行","初期值 'F'","*",null,"17"]
[{"$nulls":14},"第15行","初期值 'F'","*",null,"18"]
[{"$nulls":14},"第16行","初期值 'F'","*",null,"19"]
[{"$nulls":11},"ETX",{"$nulls":4},"03H",null,"20"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"21"]
[]
[{"$nulls":4},"・ 接口ID是为了上位机能识别多台接口时每个接口所持有的信息。"]
[]
[null,null,"[备注]"]
[null,null,"・ 上位机有信息发出时，为了能明确该信息是针对那个接口，此时利用该指令指定某一接口。"]
[]
[]
[]
[]
[]
[null,null,"110",null,"登录：PASSWORD确认",{"$nulls":6},"独有规格"]
[]
[null,null,"在登录接口时需对PASSWORD进行确认。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'1'",null,"1",null,"识别部",{"$nulls":4},"'1'",null,"1"]
[{"$nulls":7},"'1'",null,"2",{"$nulls":6},"'1'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,"PASSWORD","第1行",null,"*",null,"4",null,"数据部",null,null,"回复码",null,"*",null,"4"]
[{"$nulls":5},"第2行",null,"*",null,"5",null,"ETX",{"$nulls":4},"03H",null,"5"]
[{"$nulls":5},"第3行",null,"*",null,"6",null,"BCC",{"$nulls":4},"*",null,"6"]
[{"$nulls":5},"第4行",null,"*",null,"7"]
[{"$nulls":5},"第5行",null,"*",null,"8"]
[{"$nulls":5},"第6行",null,"*",null,"9"]
[{"$nulls":5},"第7行",null,"*",null,"10"]
[{"$nulls":5},"第8行",null,"*",null,"11"]
[null,null,"ETX",{"$nulls":4},"03H",null,"12"]
[null,null,"BCC",{"$nulls":4},"*",null,"13"]
[]
[{"$nulls":11},"回复码 = 0 : 必须项目未设定(登录成功)"]
[{"$nulls":11},"　　　 = 1 :  PASSWORD正常(登录成功)"]
[{"$nulls":11},"　　　 = 2 : PASSWORD异常(登录失败)"]
[]
[null,null,"[备注]"]
[null,null,"・ 上位机登录成功之前，接口仅接受下述指令"]
[null,null,"　　　　①切断要求"]
[null,null,"　　　　②登录：接口ID确认"]
[null,null,"　　　　③登录：PASSWORD确认"]
[null,null,"　上位机发出上述以后的指令时，接口发出实行不可能回复(F30)。"]
[null,null,"　接口在必须项目未设定时，不进行PASSWORD确认，回复码=0回复。"]
[]
[]
[]
[]
[]
[]
[null,null,"210",null,"接口设定：PASSWORD",{"$nulls":6},"独有规格"]
[]
[null,null,"将上位机决定的PASSWORD。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'2'",null,"1",null,"识别部",{"$nulls":4},"'2'",null,"1"]
[{"$nulls":7},"'1'",null,"2",{"$nulls":6},"'1'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,"PASSWORD","第1行",null,"*",null,"4",null,"ETX",{"$nulls":4},"03H",null,"4"]
[{"$nulls":5},"第2行",null,"*",null,"5",null,"BCC",{"$nulls":4},"*",null,"5"]
[{"$nulls":5},"第3行",null,"*",null,"6"]
[{"$nulls":5},"第4行",null,"*",null,"7"]
[{"$nulls":5},"第5行",null,"*",null,"8"]
[{"$nulls":5},"第6行",null,"*",null,"9"]
[{"$nulls":5},"第7行",null,"*",null,"10"]
[{"$nulls":5},"第8行",null,"*",null,"11"]
[null,null,"ETX",{"$nulls":4},"03H",null,"12"]
[null,null,"BCC",{"$nulls":4},"*",null,"13"]
[]
[null,null,"[备注]"]
[null,null,"・ 设定必须项目"]
[null,null,"· 为防止遗忘密码，请对密码好好保存。"]
[null,null,"   遗忘密码，将无法登录接口。"]
[]
[]
[]
[]
[]
[]
[null,null,"220",null,"接口设定：上位机TEL No.",{"$nulls":6},"独有规格"]
[]
[null,null,"向接口设定上位机TEL No.。"]
[]
[]
[null,null,"符号",{"$nulls":8},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'2'",null,"1",null,"识别部",{"$nulls":4},"'2'",null,"1"]
[{"$nulls":7},"'2'",null,"2",{"$nulls":6},"'2'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,"上位机TEL No.情报",null,null,"*",null,"4",null,"ETX",{"$nulls":4},"03H",null,"4"]
[{"$nulls":7},"*",null,"5",null,"BCC",{"$nulls":4},"*",null,"5"]
[{"$nulls":7},"*",null,"6"]
[{"$nulls":7},"*",null,"7"]
[{"$nulls":7},"*",null,"8"]
[{"$nulls":7},"*",null,"9"]
[{"$nulls":7},"*",null,"10"]
[{"$nulls":7},"*",null,"11"]
[{"$nulls":7},"*",null,"12"]
[{"$nulls":7},"*",null,"13"]
[{"$nulls":7},"*",null,"14"]
[{"$nulls":7},"*",null,"15"]
[{"$nulls":7},"*",null,"16"]
[{"$nulls":7},"*",null,"17"]
[{"$nulls":7},"*",null,"18"]
[{"$nulls":7},"*",null,"19"]
[{"$nulls":7},"*",null,"20"]
[{"$nulls":7},"*",null,"21"]
[{"$nulls":7},"*",null,"22"]
[{"$nulls":7},"*",null,"23"]
[{"$nulls":7},"*",null,"24"]
[{"$nulls":7},"*",null,"25"]
[{"$nulls":7},"*",null,"26"]
[{"$nulls":7},"*",null,"27"]
[{"$nulls":7},"*",null,"28"]
[{"$nulls":7},"*",null,"29"]
[{"$nulls":7},"*",null,"30"]
[{"$nulls":7},"*",null,"31"]
[{"$nulls":7},"*",null,"32"]
[{"$nulls":7},"*",null,"33"]
[null,null,"ETX",{"$nulls":4},"03H",null,"34"]
[null,null,"BCC",{"$nulls":4},"*",null,"35"]
[]
[null,null,"数据部设定信息"]
[null,null,"[0～9] : 电话号码"]
[null,null,"[An]   : n×2秒钟内拨号完成(n=1～F)"]
[null,null,"[B]    : PB信号选择"]
[null,null,"[C]    : DP信号选择"]
[null,null,"[F]    : 无效数据"]
[]
[null,null,"[备注]"]
[null,null,"· 设定必须项目"]
[null,null,"· [An]中n因PBx的机种设定不同而有所区别，实际使用时请根据PBX的适合值进行设定。"]
[null,null,"· [An]在指令中可能会设定几次，n的合计不要超过25(19H)"]
[null,null,"· 未使用区域必须设定为“F”。"]
[null,null,"· 有效数据申请勿设定“F”。"]
[]
[]
[]
[]
[]
[]
[null,null,"(例1)上位机·接口都同外线连接"]
[]
[{"$nulls":4},"接口侧TEL回路",null,"：PB"]
[{"$nulls":4},"上位机TEL No.",null,"：021-5442-1118"]
[]
[]
[]
[]
[null,null,"数据部",4,null,"'B'","　　　根据接口侧电话回路，设定PB信"]
[{"$nulls":3},5,null,"'0'"]
[{"$nulls":3},6,null,"'2'"]
[{"$nulls":3},7,null,"'1'"]
[{"$nulls":3},8,null,"'6'"]
[{"$nulls":3},9,null,"'4'"]
[{"$nulls":3},10,null,"'8'","　　　设定上位机TEL No."]
[{"$nulls":3},11,null,"'9'"]
[{"$nulls":3},12,null,"'1'"]
[{"$nulls":3},13,null,"'1'"]
[{"$nulls":3},14,null,"'1'"]
[{"$nulls":3},15,null,"'8'"]
[{"$nulls":3},16,null,"'F'"]
[{"$nulls":3},17,null,"'F'"]
[{"$nulls":3},18,null,"'F'"]
[{"$nulls":3},19,null,"'F'"]
[{"$nulls":3},20,null,"'F'"]
[{"$nulls":3},21,null,"'F'"]
[{"$nulls":3},22,null,"'F'"]
[{"$nulls":3},23,null,"'F'"]
[{"$nulls":3},24,null,"'F'","　　　未使用区域设定为'F'"]
[{"$nulls":3},25,null,"'F'"]
[{"$nulls":3},26,null,"'F'"]
[{"$nulls":3},27,null,"'F'"]
[{"$nulls":3},28,null,"'F'"]
[{"$nulls":3},29,null,"'F'"]
[{"$nulls":3},30,null,"'F'"]
[{"$nulls":3},31,null,"'F'"]
[{"$nulls":3},32,null,"'F'"]
[{"$nulls":3},33,null,"'F'"]
[]
[]
[]
[]
[]
[]
[null,null,"(例2)上位机·接口都同内线连接"]
[{"$nulls":4},"接口侧PBX",null,"：DP"]
[{"$nulls":4},"接口侧PBX外线发信号码",null,"：9"]
[{"$nulls":4},"上位机侧PBX",null,"：PB"]
[{"$nulls":4},"上位机TEL No.",null,"：021-5442-1118"]
[{"$nulls":4},"上位机内信号码",null,"：221"]
[]
[]
[null,null,"数据部",4,null,"'C'","　　　根据接口侧PBX设定DP信号选择"]
[{"$nulls":3},5,null,"'9'","　　　设定9为接外线"]
[{"$nulls":3},6,null,"'A'","　　　设定外线接通时间为2秒×3=6秒等待"]
[{"$nulls":3},7,null,"'3'"]
[{"$nulls":3},8,null,"'0'"]
[{"$nulls":3},9,null,"'2'"]
[{"$nulls":3},10,null,"'1'"]
[{"$nulls":3},11,null,"'6'"]
[{"$nulls":3},12,null,"'4'"]
[{"$nulls":3},13,null,"'8'","　　　设定上位机TEL No."]
[{"$nulls":3},14,null,"'9'"]
[{"$nulls":3},15,null,"'1'"]
[{"$nulls":3},16,null,"'1'"]
[{"$nulls":3},17,null,"'1'"]
[{"$nulls":3},18,null,"'8'"]
[{"$nulls":3},19,null,"'A'","　　　设定上位机外线接通为止时间为2秒×5=10秒等待"]
[{"$nulls":3},20,null,"'5'"]
[{"$nulls":3},21,null,"'B'","　　　根据上位机侧PBX设计PB信号选择"]
[{"$nulls":3},22,null,"'2'"]
[{"$nulls":3},23,null,"'2'","　　　设定上位机内线号码"]
[{"$nulls":3},24,null,"'1'"]
[{"$nulls":3},25,null,"'F'"]
[{"$nulls":3},26,null,"'F'"]
[{"$nulls":3},27,null,"'F'"]
[{"$nulls":3},28,null,"'F'"]
[{"$nulls":3},29,null,"'F'","　　　未使用区域设定为'F'"]
[{"$nulls":3},30,null,"'F'"]
[{"$nulls":3},31,null,"'F'"]
[{"$nulls":3},32,null,"'F'"]
[{"$nulls":3},33,null,"'F'"]
[]
[]
[]
[]
[]
[]
[null,null,"230",null,"接口设定：接口ID",{"$nulls":6},"独有规格"]
[]
[null,null,"设定接口ID。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'2'",null,"1",null,"识别部",{"$nulls":4},"'2'",null,"1"]
[{"$nulls":7},"'3'",null,"2",{"$nulls":6},"'3'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,"接口ID","第1行",null,"*",null,"4",null,"ETX",{"$nulls":4},"03H",null,"4"]
[{"$nulls":5},"第2行",null,"*",null,"5",null,"BCC",{"$nulls":4},"*",null,"5"]
[{"$nulls":5},"第3行",null,"*",null,"6"]
[{"$nulls":5},"第4行",null,"*",null,"7"]
[{"$nulls":5},"第5行",null,"*",null,"8"]
[{"$nulls":5},"第6行",null,"*",null,"9"]
[{"$nulls":5},"第7行",null,"*",null,"10"]
[{"$nulls":5},"第8行",null,"*",null,"11"]
[{"$nulls":5},"第9行",null,"*",null,"12"]
[{"$nulls":5},"第10行",null,"*",null,"13"]
[{"$nulls":5},"第11行",null,"*",null,"14"]
[{"$nulls":5},"第12行",null,"*",null,"15"]
[{"$nulls":5},"第13行",null,"*",null,"16"]
[{"$nulls":5},"第14行",null,"*",null,"17"]
[{"$nulls":5},"第15行",null,"*",null,"18"]
[{"$nulls":5},"第16行",null,"*",null,"19"]
[null,null,"ETX",{"$nulls":4},"03H",null,"20"]
[null,null,"BCC",{"$nulls":4},"*",null,"21"]
[]
[null,null,"(例)指定为087-879-3131"]
[null,null,"数据部",4,null,"'0'"]
[{"$nulls":3},5,null,"'8'"]
[{"$nulls":3},6,null,"'7'"]
[{"$nulls":3},7,null,"'8'"]
[{"$nulls":3},8,null,"'7'"]
[{"$nulls":3},9,null,"'9'"]
[{"$nulls":3},10,null,"'3'"]
[{"$nulls":3},11,null,"'1'"]
[{"$nulls":3},12,null,"'3'"]
[{"$nulls":3},13,null,"'1'"]
[{"$nulls":3},14,null,"'F'"]
[{"$nulls":3},15,null,"'F'"]
[{"$nulls":3},16,null,"'F'","　　　剩余区域记入为'F'"]
[{"$nulls":3},17,null,"'F'"]
[{"$nulls":3},18,null,"'F'"]
[{"$nulls":3},19,null,"'F'"]
[]
[null,null,"[备注]"]
[null,null,"・ 必须设定项目"]
[]
[]
[]
[]
[]
[]
[null,null,"240",null,"接口设定：现在时刻",{"$nulls":6},"独有规格"]
[]
[null,null,"对接口设定现在时刻。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'2'",null,"1",null,"识别部",{"$nulls":4},"'2'",null,"1"]
[{"$nulls":7},"'4'",null,"2",{"$nulls":6},"'4'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,"现在时刻","时","高位        10^1","*",null,"4",null,"ETX",{"$nulls":4},"03H",null,"4"]
[{"$nulls":6},"低位        10^0","*",null,"5",null,"BCC",{"$nulls":4},"*",null,"5"]
[{"$nulls":5},"分","高位        10^1","*",null,"6"]
[{"$nulls":6},"低位        10^0","*",null,"7"]
[null,null,"ETX",{"$nulls":4},"03H",null,"8"]
[null,null,"BCC",{"$nulls":4},"*",null,"9"]
[]
[null,null,"(例)设定为18点35分"]
[null,null,"数据部",4,null,"'1'"]
[{"$nulls":3},5,null,"'8'"]
[{"$nulls":3},6,null,"'3'"]
[{"$nulls":3},7,null,"'5'"]
[]
[null,null,"[备注]"]
[null,null,"・ 按24小时制设定。"]
[null,null,"・ 接通电源时为00点00分。"]
[null,null,"・ 为对时间进行修正，请在每次电话连接时实行本指令。"]
[]
[]
[]
[]
[]
[]
[null,null,"250",null,"接口设定：定时发报时间",{"$nulls":6},"独有规格"]
[]
[null,null,"对接口设定定时发表时间。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'2'",null,"1",null,"识别部",{"$nulls":4},"'2'",null,"1"]
[{"$nulls":7},"'5'",null,"2",{"$nulls":6},"'5'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,"定时发报\n时刻","时","高位        10^1","*",null,"4",null,"ETX",{"$nulls":4},"03H",null,"4"]
[{"$nulls":6},"低位        10^0","*",null,"5",null,"BCC",{"$nulls":4},"*",null,"5"]
[{"$nulls":5},"分","高位        10^1","*",null,"6"]
[{"$nulls":6},"低位        10^0","*",null,"7"]
[null,null,"ETX",{"$nulls":4},"03H",null,"8"]
[null,null,"BCC",{"$nulls":4},"*",null,"9"]
[]
[null,null,"(例)设定为22点40分"]
[null,null,"数据部",4,null,"'2'"]
[{"$nulls":3},5,null,"'2'"]
[{"$nulls":3},6,null,"'4'"]
[{"$nulls":3},7,null,"'0'"]
[]
[null,null,"[备注]"]
[null,null,"・ 按24小时制设定"]
[null,null,"・ 初始值    定时发报时间：02点00分"]
{"$rows_empty":7}
[null,null,"280",null,"接口设定：接通为止拨号次数",{"$nulls":6},"独有规格"]
[]
[null,null,"对接口进行接通为止的拨号次数设定。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'2'",null,"1",null,"识别部",{"$nulls":4},"'2'",null,"1"]
[{"$nulls":7},"'8'",null,"2",{"$nulls":6},"'8'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,null,"接通为止拨号次数",null,"*",null,"4",null,"ETX",{"$nulls":4},"03H",null,"4"]
[null,null,"ETX",{"$nulls":4},"03H",null,"5",null,"BCC",{"$nulls":4},"*",null,"5"]
[null,null,"BCC",{"$nulls":4},"*",null,"6"]
[]
[null,null,"接通为止拨号次数=1～F(1～15回)"]
[]
[null,null,"[备注]"]
[null,null,"・ 初始值    接通为止拨号次数=2(2回)"]
[]
[]
[]
[]
[]
[]
[null,null,"2A0",null,"接口设定：重拨次数",{"$nulls":6},"独有规格"]
[]
[null,null,"对接口设定接通为止的重拨次数。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'2'",null,"1",null,"识别部",{"$nulls":4},"'2'",null,"1"]
[{"$nulls":7},"'A'",null,"2",{"$nulls":6},"'A'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,null,"重拨次数","高位        16^1","*",null,"4",null,"ETX",{"$nulls":4},"03H",null,"4"]
[{"$nulls":6},"低位        16^0","*",null,"5",null,"BCC",{"$nulls":4},"*",null,"5"]
[null,null,"ETX",{"$nulls":4},"03H",null,"6"]
[null,null,"BCC",{"$nulls":4},"*",null,"7"]
[]
[null,null,"重拨次数=00H～63H(0～99回)"]
[]
[null,null,"(例)设定为10回"]
[null,null,"数据部",4,null,"'0'"]
[{"$nulls":3},5,null,"'A'"]
[]
[null,null,"[备注]"]
[null,null,"・ 初始值    重拨次数=10H(16回)"]
[]
[]
[]
[]
[]
[]
[null,null,"2B0",null,"接口设定：自动备机有无",{"$nulls":6},"独有规格"]
[]
[null,null,"对接口设定自动备机有无。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据处置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'2'",null,"1",null,"识别部",{"$nulls":4},"'2'",null,"1"]
[{"$nulls":7},"'B'",null,"2",{"$nulls":6},"'B'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,null,"自动备机有无",null,"*",null,"4",null,"ETX",{"$nulls":4},"03H",null,"4"]
[null,null,"ETX",{"$nulls":4},"03H",null,"5",null,"BCC",{"$nulls":4},"*",null,"5"]
[null,null,"BCC",{"$nulls":4},"*",null,"6"]
[]
[null,null,"自动备机有无 = 0:无 / 1:有"]
[]
[null,null,"[备注]"]
[null,null,"・ 初始值    自动备机有无=1(有)"]
[]
[]
[]
[]
[]
[]
[null,null,"2C0",null,"接口设定：自动交替运转时间",{"$nulls":6},"独有规格"]
[]
[null,null,"自动交替运转时间接口设定。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'2'",null,"1",null,"识别部",{"$nulls":4},"'2'",null,"1"]
[{"$nulls":7},"'C'",null,"2",{"$nulls":6},"'C'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,null,"自动交替转换时间","高位        16^1","*",null,"4",null,"ETX",{"$nulls":4},"03H",null,"4"]
[{"$nulls":6},"低位        16^0","*",null,"5",null,"BCC",{"$nulls":4},"*",null,"5"]
[null,null,"ETX",{"$nulls":4},"03H",null,"6"]
[null,null,"BCC",{"$nulls":4},"*",null,"7"]
[]
[null,null,"自动交替运转时间 = 00H      : 自动交替运转功能无"]
[null,null,"　　　　　　　　 = 01H～63H : 1小时～99小时"]
[]
[null,null,"(例)设定为99小时"]
[null,null,"数据部",4,null,"'6'"]
[{"$nulls":3},5,null,"'3'"]
[]
[null,null,"[备注]"]
[null,null,"・ 初始值    自动交替运转时间=00H(自动交替运转功能无)"]
[]
[]
[]
[]
[]
[]
[null,null,"2D0",null,"接口设定：最低运转保证台数",{"$nulls":6},"独有规格"]
[]
[null,null,"自动交替运转时设定最低运转保证台数。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'2'",null,"1",null,"识别部",{"$nulls":4},"'2'",null,"1"]
[{"$nulls":7},"'D'",null,"2",{"$nulls":6},"'D'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,null,"最低运转保证台数",null,"*",null,"4",null,"ETX",{"$nulls":4},"03H",null,"4"]
[null,null,"ETX",{"$nulls":4},"03H",null,"5",null,"BCC",{"$nulls":4},"*",null,"5"]
[null,null,"BCC",{"$nulls":4},"*",null,"6"]
[]
[null,null,"最低运转保证台数 = 1～2 : 1～2台"]
[]
[null,null,"[备注]"]
[null,null,"・ 初始值    最低运转保证台数=1(1台)"]
[]
[]
[]
[]
[]
[]
[null,null,"2E0",null,"接口设定：发报设定",{"$nulls":6},"独有规格"]
[]
[null,null,"根据需要对接口设定发报的许可/禁止设定。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'2'",null,"1",null,"识别部",{"$nulls":4},"'2'",null,"1"]
[{"$nulls":7},"'E'",null,"2",{"$nulls":6},"'E'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",{"$nulls":4},"*",null,"4",null,"ETX",{"$nulls":4},"03H",null,"4"]
[{"$nulls":7},"*",null,"5",null,"BCC",{"$nulls":4},"*",null,"5"]
[null,null,"ETX",{"$nulls":4},"03H",null,"6"]
[null,null,"BCC",{"$nulls":4},"*",null,"7"]
[]
[null,null,"A～B = 未使用(0固定)"]
[null,null,"C = 0:运转模式变化发报禁止　 / 1:运转模式变化发表许可"]
[null,null,"D = 0:后接续异常发报禁止　　 / 1:后接续异常发表许可"]
[null,null,"E = 0:通信异常发报禁止　　　 / 1:通信异常发表许可"]
[null,null,"F = 0:过滤网信号发报禁止     / 1:过滤网信号发表许可"]
[null,null,"G = 0:异常发报禁止　　　　　 / 1:异常发表许可"]
[null,null,"H = 0:定时发报禁止　　　　　 / 1:定时发表许可"]
[]
[null,null,"[备注]"]
[null,null,"・ 初始值    全为0(禁止)"]
[]
[]
[]
[]
[]
[]
[null,null,"300",null,"空调设置模式确认：室内机管理台数",{"$nulls":6},"独有规格"]
[]
[null,null,"从接口读出各遥控器回路所连接的室内机台数。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'3'",null,"1",null,"识别部",{"$nulls":4},"'3'",null,"1"]
[{"$nulls":7},"'0'",null,"2",{"$nulls":6},"'0'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"ETX",{"$nulls":4},"03H",null,"4",null,"数据部",null,null,"LINE0的\n室内机连接台数","高位        16^1","*",null,"4"]
[null,null,"BCC",{"$nulls":4},"*",null,"5",{"$nulls":5},"低位        16^0","*",null,"5"]
[{"$nulls":14},"LINE1的\n室内机连接台数","高位        16^1","*",null,"6"]
[{"$nulls":15},"低位        16^0","*",null,"7"]
[{"$nulls":14},"LINE2的\n室内机连接台数","高位        16^1","*",null,"8"]
[{"$nulls":15},"低位        16^0","*",null,"9"]
[{"$nulls":11},"ETX",{"$nulls":4},"03H",null,"10"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"11"]
[]
[{"$nulls":11},"(例)"]
[{"$nulls":11},"数据部",4,null,"'0'","　　　LINE0=1台"]
[{"$nulls":12},5,null,"'1'"]
[{"$nulls":12},6,null,"'0'","　　　LINE1=1台"]
[{"$nulls":12},7,null,"'1'"]
[{"$nulls":12},8,null,"'0'","　　　LINE2=0台"]
[{"$nulls":12},9,null,"'0'"]
[]
[]
[]
[]
[]
[]
[null,null,"310",null,"空调设置状态确认：Unit No.",{"$nulls":6},"独有规格"]
[]
[null,null,"从接口读出任意室内机的Unit No.。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'3'",null,"1",null,"识别部",{"$nulls":4},"'3'",null,"1"]
[{"$nulls":7},"'1'",null,"2",{"$nulls":6},"'1'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,null,"LINE No.",null,"*",null,"4",null,"数据部",null,null,"Unit No.","高位        16^1","*",null,"4"]
[null,null,"ETX",{"$nulls":4},"03H",null,"5",{"$nulls":5},"低位        16^0","*",null,"5"]
[null,null,"BCC",{"$nulls":4},"*",null,"6",null,"ETX",{"$nulls":4},"03H",null,"6"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"7"]
[]
[null,null,"LINE No. = 0～2",{"$nulls":8},"Unit No. = 00H～10H"]
[{"$nulls":11},"无室内机时为FFH"]
[]
[null,null,"(例)LINE2指定",{"$nulls":8},"(例)LINE2为00H"]
[null,null,"数据部",4,null,"'2'",{"$nulls":5},"数据部",4,null,"'0'"]
[{"$nulls":12},5,null,"'0'"]
[]
[]
[]
[]
[]
[]
[null,null,"320",null,"设置状态确认：限制情报",{"$nulls":6},"独有规格"]
[]
[null,null,"从接口读出任意回路的限制情报。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'3'",null,"1",null,"识别部",{"$nulls":4},"'3'",null,"1"]
[{"$nulls":7},"'2'",null,"2",{"$nulls":6},"'2'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,null,"LINE No.",null,"*",null,"4",null,"数据部",null,null,"RCC",null,"*",null,"4"]
[null,null,"ETX",{"$nulls":4},"03H",null,"5",{"$nulls":6},"*",null,"5"]
[null,null,"BCC",{"$nulls":4},"*",null,"6",{"$nulls":6},"*",null,"6"]
[{"$nulls":16},"*",null,"7"]
[{"$nulls":16},"*",null,"8"]
[{"$nulls":14},"制冷设定温度上限","高位        16^1","*",null,"9"]
[{"$nulls":15},"低位        16^0","*",null,"10"]
[{"$nulls":14},"制冷设定温度下限","高位        16^1","*",null,"11"]
[{"$nulls":15},"低位        16^0","*",null,"12"]
[{"$nulls":14},"制热设定温度上限","高位        16^1","*",null,"13"]
[{"$nulls":15},"低位        16^0","*",null,"14"]
[{"$nulls":14},"制热设定温度下限","高位        16^1","*",null,"15"]
[{"$nulls":15},"低位        16^0","*",null,"16"]
[{"$nulls":14},"风扇1风量控制段数",null,"*",null,"17"]
[{"$nulls":14},"风扇2风量控制段数",null,"*",null,"18"]
[{"$nulls":11},"ETX",{"$nulls":4},"03H",null,"19"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"20"]
[]
[null,null,"LINE No. = 0～2",{"$nulls":8},"RCC：遥控器控制码　　　　 = 0:A TYPE  2:C TYPE  6:D TYPE"]
[{"$nulls":11},"A  ：风扇自动有无　　　　 = 0:无 / 1:有"]
[{"$nulls":11},"B  ：制热设定有无　　　　 = 0:无 / 1:有"]
[{"$nulls":11},"C  ：制冷设定有无　　　　 = 0:无 / 1:有"]
[{"$nulls":11},"D  ：送风设定有无　　　　 = 0:无 / 1:有"]
[{"$nulls":11},"E  ：风扇2有无   　　　　 = 0:无 / 1:有"]
[{"$nulls":11},"F  ：风扇1有无　　　 　     = 0:无 / 1:有"]
[{"$nulls":11},"G  ：设定温度有无　　　　 = 0:无 / 1:有"]
[{"$nulls":11},"H  ：除湿有无　　　　　   = 0:无 / 1:有"]
[{"$nulls":11},"I  ：运转状态自动设定　   = 0:无 / 1:有"]
[{"$nulls":11},"J  ：集尘器有无　　　　　 = 0:无 / 1:有"]
[{"$nulls":11},"K  ：全热交有无　　　　　 = 0:无 / 1:有"]
[{"$nulls":11},"L  ：20NE全热交连动有无   = 0:无 / 1:有"]
[{"$nulls":11},"M  ：20NE集尘机有无　　   = 0:无 / 1:有"]
[{"$nulls":11},"N  ：20NE全热交有无　　   = 0:无 / 1:有"]
[{"$nulls":11},"O,P：未使用"]
[]
[{"$nulls":11},"风扇1，2风量控制系数　  = 0:风量控制无"]
[{"$nulls":11},"　　　   　　　　　　 　= 2:风量2速控制"]
[{"$nulls":11},"　　　   　　　　　　　 = 3:风量3速控制"]
[]
[]
[]
[]
[]
[]
[null,null,"400",null,"空调·参数收集：存满信息",{"$nulls":6},"独有规格"]
[]
[null,null,"读出任意室内机的累积信息。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'4'",null,"1",null,"识别部",{"$nulls":4},"'4'",null,"1"]
[{"$nulls":7},"'0'",null,"2",{"$nulls":6},"'0'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,null,"LINE No.",null,"*",null,"4",null,"数码部",{"$nulls":4},"*",null,"4"]
[{"$nulls":5},"Unit No.","高位        16^1","*",null,"5",{"$nulls":6},"*",null,"5"]
[{"$nulls":6},"低位        16^0","*",null,"6",{"$nulls":6},"*",null,"6"]
[null,null,"ETX",{"$nulls":4},"03H",null,"7",{"$nulls":4},"运转模式",null,"*",null,"7"]
[null,null,"BCC",{"$nulls":4},"*",null,"8",{"$nulls":3},"异常\n代码","区分码",null,"*",null,"8"]
[{"$nulls":14},"内容代码",null,"*",null,"9"]
{"$rows_empty":12}
[{"$nulls":14},"设定温度","高位        10^2","*",null,"22"]
[{"$nulls":15},"　　        10^1","*",null,"23"]
[{"$nulls":15},"低位        10^0","*",null,"24"]
[{"$nulls":14},"回风温度","高位        10^2","*",null,"25"]
[{"$nulls":15},"　　        10^1","*",null,"26"]
[{"$nulls":15},"低位        10^0","*",null,"27"]
[{"$nulls":14},"风扇1风量",null,"*",null,"28"]
[{"$nulls":14},"风扇2风量",null,"*",null,"29"]
[{"$nulls":11},"ETX",{"$nulls":4},"03H",null,"30"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"31"]
[]
[null,null,"LINE No. = 0～2",{"$nulls":8},"A：未使用"]
[null,null,"Unit No. = 何でも良い",{"$nulls":8},"B：加温器状态　　　　 = 0:OFF / 1:ON"]
[{"$nulls":11},"C：电加热状态　　　　 = 0:OFF / 1:ON"]
[{"$nulls":11},"D：风扇状态　　　  　 = 0:OFF / 1:ON"]
[{"$nulls":11},"E：未使用"]
[{"$nulls":11},"F：未使用"]
[{"$nulls":11},"G：压缩机状态　　　　 = 0:OFF / 1:ON"]
[{"$nulls":11},"H：运转状态　　　　　 = 0:OFF / 1:ON"]
[{"$nulls":11},"I：过滤网状态　　　　 = 0:OFF / 1:ON"]
[{"$nulls":11},"J：注意报状态　　　　 = 0:复归 / 1:发生"]
[{"$nulls":11},"K：警报状态　　　　　 = 0:复归 / 1:发生"]
[{"$nulls":11},"L：异常状态　　　　　 = 0:复归 / 1:发生"]
[]
[{"$nulls":11},"运转模式　　　　　 = 0:送风 / 1:制热 / 2:制冷"]
[{"$nulls":11},"设定温度　　　　　 = 000～127(0℃～127℃)"]
[{"$nulls":11},"回风温度　　　　　 = 000～127(0℃～127℃)"]
[{"$nulls":11},"风扇1，2风量　　 　= 0～5"]
{"$rows_empty":13}
[null,null,"410",null,"空调·参数收集：发报原因",{"$nulls":6},"独有规格"]
[]
[null,null,"从接口读出发报原因。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'4'",null,"1",null,"识别部",{"$nulls":4},"'4'",null,"1"]
[{"$nulls":7},"'1'",null,"2",{"$nulls":6},"'1'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"ETX",{"$nulls":4},"03H",null,"4",null,"数据部",{"$nulls":4},"*",null,"4"]
[null,null,"BCC",{"$nulls":4},"*",null,"5",{"$nulls":6},"*",null,"5"]
[{"$nulls":16},"*",null,"6"]
[{"$nulls":16},"*",null,"7"]
[{"$nulls":11},"ETX",{"$nulls":4},"03H",null,"8"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"9"]
[]
[{"$nulls":11},"A = 未使用(0固定)"]
[{"$nulls":11},"B = 0:- / 1:其它接口发报(RS-485时)"]
[{"$nulls":11},"C = 0:- / 1:运转状态变化发报"]
[{"$nulls":11},"D = 0:- / 1:后续异常发报"]
[{"$nulls":11},"E = 0:- / 1:通信异常发报"]
[{"$nulls":11},"F = 0:- / 1:过滤网异常发报"]
[{"$nulls":11},"G = 0:- / 1:异常发报"]
[{"$nulls":11},"H = 0:- / 1:定时发报"]
[{"$nulls":11},"I = 未使用(0固定)"]
[{"$nulls":11},"J = 0:- / 1:LINE2通信异常"]
[{"$nulls":11},"K = 0:- / 1:LINE1通信异常"]
[{"$nulls":11},"L = 0:- / 1:LINE0通信异常"]
[{"$nulls":11},"M = 未使用(0固定)"]
[{"$nulls":11},"N = 0:- / 1:LINE2后接续异常"]
[{"$nulls":11},"O = 0:- / 1:LINE1后接续异常"]
[{"$nulls":11},"P = 0:- / 1:LINE0后接续异常"]
[]
[{"$nulls":11},"(例)"]
[{"$nulls":11},"数据部",4,null,"'0'"]
[{"$nulls":12},5,null,"'8'"]
[{"$nulls":12},6,null,"'1'"]
[{"$nulls":12},7,null,"'0'"]
[{"$nulls":11},"　－数据的含义－"]
[{"$nulls":11},"・ 通信异常发报"]
[{"$nulls":11},"・ LINE0通讯异常"]
[]
[]
[]
[]
[]
[]
[null,null,"500",null,"空调·数据初始化",{"$nulls":6},"独有规格"]
[]
[null,null,"接口内部存储数据的初始化。\n希望从室内机的最初存储数据开始实行时发行。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'5'",null,"1",null,"识别部",{"$nulls":4},"'5'",null,"1"]
[{"$nulls":7},"'0'",null,"2",{"$nulls":6},"'0'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"ETX",{"$nulls":4},"03H",null,"4",null,"ETX",{"$nulls":4},"03H",null,"4"]
[null,null,"BCC",{"$nulls":4},"*",null,"5",null,"BCC",{"$nulls":4},"*",null,"5"]
[]
[]
[]
[]
[]
[]
[null,null,"600",null,"空调·控制    运转",{"$nulls":6},"独有规格"]
[]
[null,null,"对接口的任意LINE运转·停止指令。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'6'",null,"1",null,"识别部",{"$nulls":4},"'6'",null,"1"]
[{"$nulls":7},"'0'",null,"2",{"$nulls":6},"'0'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,null,"LINE No.",null,"*",null,"4",null,"ETX",{"$nulls":4},"03H",null,"4"]
[{"$nulls":5},"状态",null,"*",null,"5",null,"BCC",{"$nulls":4},"*",null,"5"]
[null,null,"ETX",{"$nulls":4},"03H",null,"6"]
[null,null,"BCC",{"$nulls":4},"*",null,"7"]
[]
[null,null,"LINE No.　= 0～2"]
[null,null,"状态　    = 0:停止 / 1:运转 / 3:顺次起动运转"]
{"$rows_empty":7}
[null,null,"610",null,"空调·控制    过滤网清洗重置",{"$nulls":6},"独有规格"]
[]
[null,null,"对接口的任意LINE发出过滤清洗重置指令。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'6'",null,"1",null,"识别部",{"$nulls":4},"'6'",null,"1"]
[{"$nulls":7},"'1'",null,"2",{"$nulls":6},"'1'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,null,"LINE No.",null,"*",null,"4",null,"ETX",{"$nulls":4},"03H",null,"4"]
[null,null,"ETX",{"$nulls":4},"03H",null,"5",null,"BCC",{"$nulls":4},"*",null,"5"]
[null,null,"BCC",{"$nulls":4},"*",null,"6"]
[]
[null,null,"LINE No. = 0～2"]
{"$rows_empty":7}
[null,null,"620",null,"空调·控制    运转模式",{"$nulls":6},"独有规格"]
[]
[null,null,"改变接口任意LINE的运转模式。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'6'",null,"1",null,"识别部",{"$nulls":4},"'6'",null,"1"]
[{"$nulls":7},"'2'",null,"2",{"$nulls":6},"'2'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,null,"LINE No.",null,"*",null,"4",null,"ETX",{"$nulls":4},"03H",null,"4"]
[{"$nulls":5},"运转模式",null,"*",null,"5",null,"BCC",{"$nulls":4},"*",null,"5"]
[null,null,"ETX",{"$nulls":4},"03H",null,"6"]
[null,null,"BCC",{"$nulls":4},"*",null,"7"]
[]
[null,null,"LINE No. = 0～2"]
[null,null,"运转模式 = 0:送风"]
[null,null,"            = 1:制热"]
[null,null,"                  = 2:制冷"]
[null,null,"                  = 3:自动"]
[null,null,"                  = 4:换气清净"]
[null,null,"                  = 7:除湿"]
[]
[null,null,"[备注]"]
[null,null,"・ 参考限制情报：不要设定系统无法实现的运转模式。"]
[]
[]
[]
[]
[]
[]
[null,null,"630",null,"空调·控制    设定温度",{"$nulls":6},"独有规格"]
[]
[null,null,"改变接口任意LINE的设定温度。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'6'",null,"1",null,"识别部",{"$nulls":4},"'6'",null,"1"]
[{"$nulls":7},"'3'",null,"2",{"$nulls":6},"'3'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,null,"LINE No.",null,"*",null,"4",null,"ETX",{"$nulls":4},"03H",null,"4"]
[{"$nulls":5},"制冷设定温度","高位        10^2","*",null,"5",null,"BCC",{"$nulls":4},"*",null,"5"]
[{"$nulls":6},"　　        10^1","*",null,"6"]
[{"$nulls":6},"低位        10^0","*",null,"7"]
[{"$nulls":5},"制热设定温度","高位        10^2","*",null,"8"]
[{"$nulls":6},"　　        10^1","*",null,"9"]
[{"$nulls":6},"低位        10^0","*",null,"10"]
[null,null,"ETX",{"$nulls":4},"03H",null,"11"]
[null,null,"BCC",{"$nulls":4},"*",null,"12"]
[]
[null,null,"LINE No.     = 0～2"]
[null,null,"制冷设定温度 = 000～127 : 0℃～127℃"]
[null,null,"制热设定温度 = 000～127 : 0℃～127℃"]
[]
[null,null,"[备注]"]
[null,null,"・ 参考限止信息的设定温度上限，不要设定为系统无法实现的设定温度。"]
[null,null,"・ 每次仅能设定制冷时的温度或制热时的温度。请在每个状态下都设定一次温度。"]
[]
[]
[]
[]
[]
[]
[null,null,"640",null,"空调·控制    风量",{"$nulls":6},"独有规格"]
[]
[null,null,"改变接口任意LINE的风量。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'6'",null,"1",null,"识别部",{"$nulls":4},"'6'",null,"1"]
[{"$nulls":7},"'4'",null,"2",{"$nulls":6},"'4'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"数据部",null,null,"LINE No.",null,"*",null,"4",null,"ETX",{"$nulls":4},"03H",null,"4"]
[{"$nulls":5},"制冷风扇1风量",null,"*",null,"5",null,"BCC",{"$nulls":4},"*",null,"5"]
[{"$nulls":5},"制冷风扇2风量",null,"*",null,"6"]
[{"$nulls":5},"制热风扇1风量",null,"*",null,"7"]
[{"$nulls":5},"制热风扇2风量",null,"*",null,"8"]
[null,null,"ETX",{"$nulls":4},"03H",null,"9"]
[null,null,"BCC",{"$nulls":4},"*",null,"10"]
[]
[null,null,"LINE No.  = 0～2"]
[null,null,"各风量　　= 0:自动"]
[null,null,"　　　　　= 1:风量1"]
[null,null,"　　　　　= 2:风量2"]
[null,null,"　　　　　= 3:风量3"]
[null,null,"　　　　　= 4:风量4"]
[null,null,"　　　　　= 5:风量5"]
[]
[null,null,"[备注]"]
[null,null,"・ 参考限制信息：不要设定系统无法实现的风量。"]
[null,null,"・ 制冷风扇1、制冷风扇2、制热风扇1、制热风扇2、只能进行个别设定。请设定一次。"]
[]
[]
[]
[]
[]
[]
[null,null,"720",null,"读出接口设定：上位机Unit No.",{"$nulls":6},"独有规格"]
[]
[null,null,"读出同接口相连的上位机的TEL No.。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'7'",null,"1",null,"识别部",{"$nulls":4},"'7'",null,"1"]
[{"$nulls":7},"'2'",null,"2",{"$nulls":6},"'2'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"ETX",{"$nulls":4},"03H",null,"4",null,"数据部",null,"上位机TEL No.信息",null,null,"*",null,"4"]
[null,null,"BCC",{"$nulls":4},"*",null,"5",{"$nulls":6},"*",null,"5"]
[{"$nulls":16},"*",null,"6"]
[{"$nulls":16},"*",null,"7"]
[{"$nulls":16},"*",null,"8"]
[{"$nulls":16},"*",null,"9"]
[{"$nulls":16},"*",null,"10"]
[{"$nulls":16},"*",null,"11"]
[{"$nulls":16},"*",null,"12"]
[{"$nulls":16},"*",null,"13"]
[{"$nulls":16},"*",null,"14"]
[{"$nulls":16},"*",null,"15"]
[{"$nulls":16},"*",null,"16"]
[{"$nulls":16},"*",null,"17"]
[{"$nulls":16},"*",null,"18"]
[{"$nulls":16},"*",null,"19"]
[{"$nulls":16},"*",null,"20"]
[{"$nulls":16},"*",null,"21"]
[{"$nulls":16},"*",null,"22"]
[{"$nulls":16},"*",null,"23"]
[{"$nulls":16},"*",null,"24"]
[{"$nulls":16},"*",null,"25"]
[{"$nulls":16},"*",null,"26"]
[{"$nulls":16},"*",null,"27"]
[{"$nulls":16},"*",null,"28"]
[{"$nulls":16},"*",null,"29"]
[{"$nulls":16},"*",null,"30"]
[{"$nulls":16},"*",null,"31"]
[{"$nulls":16},"*",null,"32"]
[{"$nulls":16},"*",null,"33"]
[{"$nulls":11},"ETX",{"$nulls":4},"03H",null,"34"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"35"]
[]
[]
[]
[]
[]
[]
[null,null,"730",null,"读出接口设定：接口ID",{"$nulls":6},"独有规格"]
[]
[null,null,"读出接口设定的ID。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'7'",null,"1",null,"识别部",{"$nulls":4},"'7'",null,"1"]
[{"$nulls":7},"'3'",null,"2",{"$nulls":6},"'3'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"ETX",{"$nulls":4},"03H",null,"4",null,"数据部",null,"接口ID","第1行",null,"*",null,"4"]
[null,null,"BCC",{"$nulls":4},"*",null,"5",{"$nulls":4},"第2行",null,"*",null,"5"]
[{"$nulls":14},"第3行",null,"*",null,"6"]
[{"$nulls":14},"第4行",null,"*",null,"7"]
[{"$nulls":14},"第5行",null,"*",null,"8"]
[{"$nulls":14},"第6行",null,"*",null,"9"]
[{"$nulls":14},"第7行",null,"*",null,"10"]
[{"$nulls":14},"第8行",null,"*",null,"11"]
[{"$nulls":14},"第9行",null,"*",null,"12"]
[{"$nulls":14},"第10行",null,"*",null,"13"]
[{"$nulls":14},"第11行",null,"*",null,"14"]
[{"$nulls":14},"第12行",null,"*",null,"15"]
[{"$nulls":14},"第13行",null,"*",null,"16"]
[{"$nulls":14},"第14行",null,"*",null,"17"]
[{"$nulls":14},"第15行",null,"*",null,"18"]
[{"$nulls":14},"第16行",null,"*",null,"19"]
[{"$nulls":11},"ETX",{"$nulls":4},"03H",null,"20"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"21"]
[]
[{"$nulls":11},"(例)读出087-879-3131号码"]
[{"$nulls":11},"数据部",4,null,"'0'"]
[{"$nulls":12},5,null,"'8'"]
[{"$nulls":12},6,null,"'7'"]
[{"$nulls":12},7,null,"'8'"]
[{"$nulls":12},8,null,"'7'"]
[{"$nulls":12},9,null,"'9'"]
[{"$nulls":12},10,null,"'3'"]
[{"$nulls":12},11,null,"'1'"]
[{"$nulls":12},12,null,"'3'"]
[{"$nulls":12},13,null,"'1'"]
[{"$nulls":12},14,null,"'F'"]
[{"$nulls":12},15,null,"'F'"]
[{"$nulls":12},16,null,"'F'","　　　未使用区域为'F'"]
[{"$nulls":12},17,null,"'F'"]
[{"$nulls":12},18,null,"'F'"]
[{"$nulls":12},19,null,"'F'"]
[]
[]
[]
[]
[]
[]
[null,null,"740",null,"读出接口设定：现在时刻",{"$nulls":6},"独有规格"]
[]
[null,null,"读出接口累计的现在时刻。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'7'",null,"1",null,"识别部",{"$nulls":4},"'7'",null,"1"]
[{"$nulls":7},"'4'",null,"2",{"$nulls":6},"'4'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"ETX",{"$nulls":4},"03H",null,"4",null,"数据部",null,"现在时刻","时","高位        10^1","*",null,"4"]
[null,null,"BCC",{"$nulls":4},"*",null,"5",{"$nulls":5},"低位        10^0","*",null,"5"]
[{"$nulls":14},"分","高位        10^1","*",null,"6"]
[{"$nulls":15},"低位        10^0","*",null,"7"]
[{"$nulls":11},"ETX",{"$nulls":4},"03H",null,"8"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"9"]
[]
[{"$nulls":11},"(例)读出18点35分"]
[{"$nulls":11},"数据部",4,null,"'1'"]
[{"$nulls":12},5,null,"'8'"]
[{"$nulls":12},6,null,"'3'"]
[{"$nulls":12},7,null,"'5'"]
[]
[]
[]
[]
[]
[]
[null,null,"750",null,"读出接口设定：定时发报时刻",{"$nulls":6},"独有规格"]
[]
[null,null,"读出接口设定的定时发表时刻。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'7'",null,"1",null,"识别部",{"$nulls":4},"'7'",null,"1"]
[{"$nulls":7},"'5'",null,"2",{"$nulls":6},"'5'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"ETX",{"$nulls":4},"03H",null,"4",null,"数据部",null,"定时发表\n时刻","时","高位        10^1","*",null,"4"]
[null,null,"BCC",{"$nulls":4},"*",null,"5",{"$nulls":5},"低位        10^0","*",null,"5"]
[{"$nulls":14},"分","高位        10^1","*",null,"6"]
[{"$nulls":15},"低位        10^0","*",null,"7"]
[{"$nulls":11},"ETX",{"$nulls":4},"03H",null,"8"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"9"]
[]
[{"$nulls":11},"(例)读出22点40分"]
[{"$nulls":11},"数据部",4,null,"'2'"]
[{"$nulls":12},5,null,"'2'"]
[{"$nulls":12},6,null,"'4'"]
[{"$nulls":12},7,null,"'0'"]
[]
[]
[]
[]
[]
[]
[null,null,"780",null,"读出接口设定：接通为止的响应次数",{"$nulls":6},"独有规格"]
[]
[null,null,"读出接口设定的连通为止的响应次数。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'7'",null,"1",null,"识别部",{"$nulls":4},"'7'",null,"1"]
[{"$nulls":7},"'8'",null,"2",{"$nulls":6},"'8'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"ETX",{"$nulls":4},"03H",null,"4",null,"数据部",null,null,"连通为止的响铃次数",null,"*",null,"4"]
[null,null,"BCC",{"$nulls":4},"*",null,"5",null,"ETX",{"$nulls":4},"03H",null,"5"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"6"]
[]
[{"$nulls":11},"连通为止的响铃次数=1～F(1～15回)"]
[]
[]
[]
[]
[]
[]
[null,null,"7A0",null,"读出接口设定：重拨次数",{"$nulls":6},"独有规格"]
[]
[null,null,"读出接口设定的连通为止的重拨为止。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'7'",null,"1",null,"识别部",{"$nulls":4},"'7'",null,"1"]
[{"$nulls":7},"'A'",null,"2",{"$nulls":6},"'A'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"ETX",{"$nulls":4},"03H",null,"4",null,"数据部",null,null,"重拨次数","高位        16^1","*",null,"4"]
[null,null,"BCC",{"$nulls":4},"*",null,"5",{"$nulls":5},"低位        16^0","*",null,"5"]
[{"$nulls":11},"ETX",{"$nulls":4},"03H",null,"6"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"7"]
[]
[{"$nulls":11},"重拨次数=00H～63H(0～99回)"]
[]
[{"$nulls":11},"(例)读出10回"]
[{"$nulls":11},"数据部",4,null,"'0'"]
[{"$nulls":12},5,null,"'A'"]
[]
[]
[]
[]
[]
[]
[null,null,"7B0",null,"读出接口设定：自动备机有无",{"$nulls":6},"独有规格"]
[]
[null,null,"读出接口设定的自动备机功能有无。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'7'",null,"1",null,"识别部",{"$nulls":4},"'7'",null,"1"]
[{"$nulls":7},"'B'",null,"2",{"$nulls":6},"'B'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"ETX",{"$nulls":4},"03H",null,"4",null,"数据部",null,null,"自动备机有无",null,"*",null,"4"]
[null,null,"BCC",{"$nulls":4},"*",null,"5",null,"ETX",{"$nulls":4},"03H",null,"5"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"6"]
[]
[{"$nulls":11},"自动备机有无 = 0:无 / 1:有"]
[]
[]
[]
[]
[]
[]
[null,null,"7C0",null,"读出接口设定：自动交替运转时间",{"$nulls":6},"独有规格"]
[]
[null,null,"读出接口设定的自动交替运转时间。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'7'",null,"1",null,"识别部",{"$nulls":4},"'7'",null,"1"]
[{"$nulls":7},"'C'",null,"2",{"$nulls":6},"'C'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"ETX",{"$nulls":4},"03H",null,"4",null,"数据部",null,null,"自动交替运转时间","高位        16^1","*",null,"4"]
[null,null,"BCC",{"$nulls":4},"*",null,"5",{"$nulls":5},"低位        16^0","*",null,"5"]
[{"$nulls":11},"ETX",{"$nulls":4},"03H",null,"6"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"7"]
[]
[{"$nulls":11},"自动交替运转时间 = 00H      : 自动交替运转功能无"]
[{"$nulls":11},"　　　　　　　　 = 01H～63H : 1小时～99小时"]
[]
[{"$nulls":11},"(例)读出99小时"]
[{"$nulls":11},"数据部",4,null,"'6'"]
[{"$nulls":12},5,null,"'3'"]
[]
[]
[]
[]
[]
[]
[null,null,"7D0",null,"读出接口设定：最低运转保证台数",{"$nulls":6},"独有规格"]
[]
[null,null,"读出接口设定的最低运转保证台数。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'7'",null,"1",null,"识别部",{"$nulls":4},"'7'",null,"1"]
[{"$nulls":7},"'D'",null,"2",{"$nulls":6},"'D'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"ETX",{"$nulls":4},"03H",null,"4",null,"数据部",null,null,"最低运转保证台数",null,"*",null,"4"]
[null,null,"BCC",{"$nulls":4},"*",null,"5",null,"ETX",{"$nulls":4},"03H",null,"5"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"6"]
[]
[{"$nulls":11},"最低运转保证台数 = 1～2 : 1～2台"]
[]
[]
[]
[]
[]
[]
[null,null,"7E0",null,"读出接口设定：发报设定",{"$nulls":6},"独有规格"]
[]
[null,null,"读出接口设定的各种情况下的发报有无。"]
[]
[]
[null,null,"符号",null,"指令",{"$nulls":6},"符号",null,"回复"]
[{"$nulls":4},"名　称",null,"数据位置","数值",{"$nulls":5},"名　称",null,"数据位置","数值"]
[]
[null,null,"STX",{"$nulls":4},"02H",null,"0",null,"STX",{"$nulls":4},"02H",null,"0"]
[null,null,"识别部",{"$nulls":4},"'7'",null,"1",null,"识别部",{"$nulls":4},"'7'",null,"1"]
[{"$nulls":7},"'E'",null,"2",{"$nulls":6},"'E'",null,"2"]
[{"$nulls":7},"'0'",null,"3",{"$nulls":6},"'0'",null,"3"]
[null,null,"ETX",{"$nulls":4},"03H",null,"4",null,"数据部",{"$nulls":4},"*",null,"4"]
[null,null,"BCC",{"$nulls":4},"*",null,"5",{"$nulls":6},"*",null,"5"]
[{"$nulls":11},"ETX",{"$nulls":4},"03H",null,"6"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"7"]
[]
[{"$nulls":11},"A～B = 未使用(0固定)"]
[{"$nulls":11},"C = 0:运转状态变化发报禁止　 / 1:运转状态变化发表许可"]
[{"$nulls":11},"D = 0:后接续异常发报禁止　　 / 1:后接续异常发表许可"]
[{"$nulls":11},"E = 0:通信异常发报禁止　　　 / 1:通信异常发表许可"]
[{"$nulls":11},"F = 0:过滤网清洗发报禁止　　 / 1:过滤网清洗发表许可"]
[{"$nulls":11},"G = 0:异常发报禁止　　　　　 / 1:异常发表许可"]
[{"$nulls":11},"H = 0:定时发报禁止　　　　　 / 1:定时发表许可"]
[]
[]
[]
[]
[]
[]
[null,null,"F10",null,"否定回答：BCC异常",{"$nulls":6},"独有规格"]
[]
[null,null,"告知上位机的指令为BCC异常。\n(仅为回复)"]
[]
[{"$nulls":4}," "]
[{"$nulls":11},"符号",null,"回复"]
[{"$nulls":13},"名　称",null,"数据位置","数值"]
[]
[{"$nulls":11},"STX",{"$nulls":4},"02H",null,"0"]
[{"$nulls":11},"识别部",{"$nulls":4},"'F'",null,"1"]
[{"$nulls":16},"'1'",null,"2"]
[{"$nulls":16},"'0'",null,"3"]
[{"$nulls":11},"ETX",{"$nulls":4},"03H",null,"4"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"5"]
[]
[]
[]
[]
[]
[]
[null,null,"F20",null,"否定回答：未定义",{"$nulls":6},"独有规格"]
[]
[null,null,"告知上位机的指令为未定义。\n(仅为回复)"]
[]
[{"$nulls":4}," "]
[{"$nulls":11},"符号",null,"回复"]
[{"$nulls":13},"名　称",null,"数据位置","数值"]
[]
[{"$nulls":11},"STX",{"$nulls":4},"02H",null,"0"]
[{"$nulls":11},"识别部",{"$nulls":4},"'F'",null,"1"]
[{"$nulls":16},"'2'",null,"2"]
[{"$nulls":16},"'0'",null,"3"]
[{"$nulls":11},"ETX",{"$nulls":4},"03H",null,"4"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"5"]
[]
[]
[]
[]
[]
[]
[null,null,"F30",null,"否定回答：实行不可能",{"$nulls":6},"独有规格"]
[]
[null,null,"告知上位机的指令为实行不可能。\n(仅为回复)"]
[]
[{"$nulls":4}," "]
[{"$nulls":11},"符号",null,"回复"]
[{"$nulls":13},"名　称",null,"数据位置","数值"]
[]
[{"$nulls":11},"STX",{"$nulls":4},"02H",null,"0"]
[{"$nulls":11},"识别部",{"$nulls":4},"'F'",null,"1"]
[{"$nulls":16},"'3'",null,"2"]
[{"$nulls":16},"'0'",null,"3"]
[{"$nulls":11},"ETX",{"$nulls":4},"03H",null,"4"]
[{"$nulls":11},"BCC",{"$nulls":4},"*",null,"5"]