{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["变量dat文件","CSpreadSheetBackup"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":190,"n_cols":76,"rows_kept":190,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","14.1.188.1","sts1_systemStatus","1号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","2","1,2,","警告,报警,"]
["2","14.1.188.1","sts1_systemSourcePhaseDiff","1号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.1","sts1_systemLoadRatio","1号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.1","sts1_source1Voltage","1号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.1","sts1_source1Frequency","1号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.1","sts1_source112VAuxVoltage","1号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.1","sts1_source15VAuxVoltage","1号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.1","sts1_source2Voltage","1号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.1","sts1_source2Frequency","1号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.1","sts1_source212VAuxVoltage","1号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.1","sts1_source25VAuxVoltage","1号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.1","sts1_outputVoltage","1号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.1","sts1_outputCurrent","1号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.1","sts1_outputFrequency","1号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.1","sts1_relay1Status","1号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.1","sts1_relay2Status","1号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.1","sts1_relay3Status","1号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.1","sts1_Communications","1号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
[]
["1","14.1.188.2","sts2_systemStatus","2号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","2","1,2,","警告,报警,"]
["2","14.1.188.2","sts2_systemSourcePhaseDiff","2号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.2","sts2_systemLoadRatio","2号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.2","sts2_source1Voltage","2号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.2","sts2_source1Frequency","2号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.2","sts2_source112VAuxVoltage","2号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.2","sts2_source15VAuxVoltage","2号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.2","sts2_source2Voltage","2号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.2","sts2_source2Frequency","2号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.2","sts2_source212VAuxVoltage","2号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.2","sts2_source25VAuxVoltage","2号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.2","sts2_outputVoltage","2号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.2","sts2_outputCurrent","2号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.2","sts2_outputFrequency","2号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.2","sts2_relay1Status","2号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.2","sts2_relay2Status","2号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.2","sts2_relay3Status","2号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.2","sts2_Communications","2号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
[]
["1","14.1.188.3","sts3_systemStatus","3号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","2","1,2,","警告,报警,"]
["2","14.1.188.3","sts3_systemSourcePhaseDiff","3号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.3","sts3_systemLoadRatio","3号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.3","sts3_source1Voltage","3号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.3","sts3_source1Frequency","3号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.3","sts3_source112VAuxVoltage","3号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.3","sts3_source15VAuxVoltage","3号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.3","sts3_source2Voltage","3号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.3","sts3_source2Frequency","3号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.3","sts3_source212VAuxVoltage","3号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.3","sts3_source25VAuxVoltage","3号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.3","sts3_outputVoltage","3号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.3","sts3_outputCurrent","3号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.3","sts3_outputFrequency","3号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.3","sts3_relay1Status","3号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.3","sts3_relay2Status","3号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.3","sts3_relay3Status","3号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.3","sts3_Communications","3号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
[]
["1","14.1.188.4","sts4_systemStatus","4号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","2","1,2,","警告,报警,"]
["2","14.1.188.4","sts4_systemSourcePhaseDiff","4号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.4","sts4_systemLoadRatio","4号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.4","sts4_source1Voltage","4号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.4","sts4_source1Frequency","4号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.4","sts4_source112VAuxVoltage","4号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.4","sts4_source15VAuxVoltage","4号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.4","sts4_source2Voltage","4号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.4","sts4_source2Frequency","4号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.4","sts4_source212VAuxVoltage","4号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.4","sts4_source25VAuxVoltage","4号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.4","sts4_outputVoltage","4号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.4","sts4_outputCurrent","4号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.4","sts4_outputFrequency","4号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.4","sts4_relay1Status","4号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.4","sts4_relay2Status","4号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.4","sts4_relay3Status","4号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.4","sts4_Communications","4号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
[]
["1","14.1.188.5","sts5_systemStatus","5号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","2","1,2,","警告,报警,"]
["2","14.1.188.5","sts5_systemSourcePhaseDiff","5号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.5","sts5_systemLoadRatio","5号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.5","sts5_source1Voltage","5号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.5","sts5_source1Frequency","5号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.5","sts5_source112VAuxVoltage","5号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.5","sts5_source15VAuxVoltage","5号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.5","sts5_source2Voltage","5号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.5","sts5_source2Frequency","5号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.5","sts5_source212VAuxVoltage","5号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.5","sts5_source25VAuxVoltage","5号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.5","sts5_outputVoltage","5号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.5","sts5_outputCurrent","5号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.5","sts5_outputFrequency","5号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.5","sts5_relay1Status","5号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.5","sts5_relay2Status","5号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.5","sts5_relay3Status","5号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.5","sts5_Communications","5号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
[]
["1","14.1.188.6","sts6_systemStatus","6号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","2","1,2,","警告,报警,"]
["2","14.1.188.6","sts6_systemSourcePhaseDiff","6号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.6","sts6_systemLoadRatio","6号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.6","sts6_source1Voltage","6号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.6","sts6_source1Frequency","6号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.6","sts6_source112VAuxVoltage","6号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.6","sts6_source15VAuxVoltage","6号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.6","sts6_source2Voltage","6号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.6","sts6_source2Frequency","6号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.6","sts6_source212VAuxVoltage","6号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.6","sts6_source25VAuxVoltage","6号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.6","sts6_outputVoltage","6号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.6","sts6_outputCurrent","6号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.6","sts6_outputFrequency","6号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.6","sts6_relay1Status","6号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.6","sts6_relay2Status","6号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.6","sts6_relay3Status","6号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.6","sts6_Communications","6号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
[]
["1","14.1.188.7","sts7_systemStatus","7号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","2","1,2,","警告,报警,"]
["2","14.1.188.7","sts7_systemSourcePhaseDiff","7号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.7","sts7_systemLoadRatio","7号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.7","sts7_source1Voltage","7号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.7","sts7_source1Frequency","7号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.7","sts7_source112VAuxVoltage","7号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.7","sts7_source15VAuxVoltage","7号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.7","sts7_source2Voltage","7号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.7","sts7_source2Frequency","7号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.7","sts7_source212VAuxVoltage","7号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.7","sts7_source25VAuxVoltage","7号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.7","sts7_outputVoltage","7号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.7","sts7_outputCurrent","7号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.7","sts7_outputFrequency","7号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.7","sts7_relay1Status","7号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.7","sts7_relay2Status","7号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.7","sts7_relay3Status","7号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.7","sts7_Communications","7号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
[]
["1","14.1.188.8","sts8_systemStatus","8号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","2","1,2,","警告,报警,"]
["2","14.1.188.8","sts8_systemSourcePhaseDiff","8号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.8","sts8_systemLoadRatio","8号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.8","sts8_source1Voltage","8号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.8","sts8_source1Frequency","8号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.8","sts8_source112VAuxVoltage","8号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.8","sts8_source15VAuxVoltage","8号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.8","sts8_source2Voltage","8号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.8","sts8_source2Frequency","8号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.8","sts8_source212VAuxVoltage","8号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.8","sts8_source25VAuxVoltage","8号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.8","sts8_outputVoltage","8号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.8","sts8_outputCurrent","8号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.8","sts8_outputFrequency","8号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.8","sts8_relay1Status","8号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.8","sts8_relay2Status","8号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.8","sts8_relay3Status","8号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.8","sts8_Communications","8号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
[]
["1","14.1.188.9","sts9_systemStatus","9号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","2","1,2,","警告,报警,"]
["2","14.1.188.9","sts9_systemSourcePhaseDiff","9号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.9","sts9_systemLoadRatio","9号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.9","sts9_source1Voltage","9号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.9","sts9_source1Frequency","9号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.9","sts9_source112VAuxVoltage","9号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.9","sts9_source15VAuxVoltage","9号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.9","sts9_source2Voltage","9号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.9","sts9_source2Frequency","9号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.9","sts9_source212VAuxVoltage","9号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.9","sts9_source25VAuxVoltage","9号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.9","sts9_outputVoltage","9号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.9","sts9_outputCurrent","9号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.9","sts9_outputFrequency","9号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.9","sts9_relay1Status","9号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.9","sts9_relay2Status","9号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.9","sts9_relay3Status","9号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.9","sts9_Communications","9号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
[]
["1","14.1.188.10","sts10_systemStatus","10号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","2","1,2,","警告,报警,"]
["2","14.1.188.10","sts10_systemSourcePhaseDiff","10号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.10","sts10_systemLoadRatio","10号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.10","sts10_source1Voltage","10号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.10","sts10_source1Frequency","10号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.10","sts10_source112VAuxVoltage","10号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.10","sts10_source15VAuxVoltage","10号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.10","sts10_source2Voltage","10号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.10","sts10_source2Frequency","10号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.10","sts10_source212VAuxVoltage","10号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.10","sts10_source25VAuxVoltage","10号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.10","sts10_outputVoltage","10号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.10","sts10_outputCurrent","10号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.10","sts10_outputFrequency","10号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.10","sts10_relay1Status","10号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.10","sts10_relay2Status","10号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.10","sts10_relay3Status","10号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.10","sts10_Communications","10号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]

{"sheet":"CSpreadSheetBackup","index":1,"n_rows":181,"n_cols":76,"rows_kept":181,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","14.1.188.1","sts1_systemStatus","1号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","14.1.188.1","sts1_systemSourcePhaseDiff","1号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.1","sts1_systemLoadRatio","1号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.1","sts1_source1Voltage","1号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.1","sts1_source1Frequency","1号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.1","sts1_source112VAuxVoltage","1号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.1","sts1_source15VAuxVoltage","1号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.1","sts1_source2Voltage","1号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.1","sts1_source2Frequency","1号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.1","sts1_source212VAuxVoltage","1号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.1","sts1_source25VAuxVoltage","1号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.1","sts1_outputVoltage","1号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.1","sts1_outputCurrent","1号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.1","sts1_outputFrequency","1号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.1","sts1_relay1Status","1号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.1","sts1_relay2Status","1号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.1","sts1_relay3Status","1号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.1","sts1_Communications","1号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["1","14.1.188.2","sts2_systemStatus","2号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","14.1.188.2","sts2_systemSourcePhaseDiff","2号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.2","sts2_systemLoadRatio","2号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.2","sts2_source1Voltage","2号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.2","sts2_source1Frequency","2号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.2","sts2_source112VAuxVoltage","2号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.2","sts2_source15VAuxVoltage","2号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.2","sts2_source2Voltage","2号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.2","sts2_source2Frequency","2号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.2","sts2_source212VAuxVoltage","2号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.2","sts2_source25VAuxVoltage","2号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.2","sts2_outputVoltage","2号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.2","sts2_outputCurrent","2号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.2","sts2_outputFrequency","2号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.2","sts2_relay1Status","2号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.2","sts2_relay2Status","2号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.2","sts2_relay3Status","2号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.2","sts2_Communications","2号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["1","14.1.188.3","sts3_systemStatus","3号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","14.1.188.3","sts3_systemSourcePhaseDiff","3号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.3","sts3_systemLoadRatio","3号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.3","sts3_source1Voltage","3号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.3","sts3_source1Frequency","3号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.3","sts3_source112VAuxVoltage","3号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.3","sts3_source15VAuxVoltage","3号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.3","sts3_source2Voltage","3号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.3","sts3_source2Frequency","3号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.3","sts3_source212VAuxVoltage","3号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.3","sts3_source25VAuxVoltage","3号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.3","sts3_outputVoltage","3号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.3","sts3_outputCurrent","3号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.3","sts3_outputFrequency","3号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.3","sts3_relay1Status","3号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.3","sts3_relay2Status","3号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.3","sts3_relay3Status","3号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.3","sts3_Communications","3号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["1","14.1.188.4","sts4_systemStatus","4号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","14.1.188.4","sts4_systemSourcePhaseDiff","4号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.4","sts4_systemLoadRatio","4号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.4","sts4_source1Voltage","4号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.4","sts4_source1Frequency","4号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.4","sts4_source112VAuxVoltage","4号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.4","sts4_source15VAuxVoltage","4号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.4","sts4_source2Voltage","4号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.4","sts4_source2Frequency","4号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.4","sts4_source212VAuxVoltage","4号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.4","sts4_source25VAuxVoltage","4号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.4","sts4_outputVoltage","4号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.4","sts4_outputCurrent","4号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.4","sts4_outputFrequency","4号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.4","sts4_relay1Status","4号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.4","sts4_relay2Status","4号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.4","sts4_relay3Status","4号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.4","sts4_Communications","4号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["1","14.1.188.5","sts5_systemStatus","5号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","14.1.188.5","sts5_systemSourcePhaseDiff","5号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.5","sts5_systemLoadRatio","5号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.5","sts5_source1Voltage","5号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.5","sts5_source1Frequency","5号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.5","sts5_source112VAuxVoltage","5号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.5","sts5_source15VAuxVoltage","5号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.5","sts5_source2Voltage","5号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.5","sts5_source2Frequency","5号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.5","sts5_source212VAuxVoltage","5号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.5","sts5_source25VAuxVoltage","5号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.5","sts5_outputVoltage","5号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.5","sts5_outputCurrent","5号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.5","sts5_outputFrequency","5号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.5","sts5_relay1Status","5号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.5","sts5_relay2Status","5号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.5","sts5_relay3Status","5号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.5","sts5_Communications","5号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["1","14.1.188.6","sts6_systemStatus","6号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","14.1.188.6","sts6_systemSourcePhaseDiff","6号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.6","sts6_systemLoadRatio","6号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.6","sts6_source1Voltage","6号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.6","sts6_source1Frequency","6号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.6","sts6_source112VAuxVoltage","6号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.6","sts6_source15VAuxVoltage","6号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.6","sts6_source2Voltage","6号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.6","sts6_source2Frequency","6号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.6","sts6_source212VAuxVoltage","6号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.6","sts6_source25VAuxVoltage","6号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.6","sts6_outputVoltage","6号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.6","sts6_outputCurrent","6号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.6","sts6_outputFrequency","6号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.6","sts6_relay1Status","6号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.6","sts6_relay2Status","6号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.6","sts6_relay3Status","6号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.6","sts6_Communications","6号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["1","14.1.188.7","sts7_systemStatus","7号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","14.1.188.7","sts7_systemSourcePhaseDiff","7号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.7","sts7_systemLoadRatio","7号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.7","sts7_source1Voltage","7号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.7","sts7_source1Frequency","7号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.7","sts7_source112VAuxVoltage","7号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.7","sts7_source15VAuxVoltage","7号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.7","sts7_source2Voltage","7号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.7","sts7_source2Frequency","7号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.7","sts7_source212VAuxVoltage","7号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.7","sts7_source25VAuxVoltage","7号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.7","sts7_outputVoltage","7号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.7","sts7_outputCurrent","7号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.7","sts7_outputFrequency","7号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.7","sts7_relay1Status","7号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.7","sts7_relay2Status","7号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.7","sts7_relay3Status","7号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.7","sts7_Communications","7号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["1","14.1.188.8","sts8_systemStatus","8号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","14.1.188.8","sts8_systemSourcePhaseDiff","8号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.8","sts8_systemLoadRatio","8号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.8","sts8_source1Voltage","8号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.8","sts8_source1Frequency","8号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.8","sts8_source112VAuxVoltage","8号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.8","sts8_source15VAuxVoltage","8号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.8","sts8_source2Voltage","8号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.8","sts8_source2Frequency","8号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.8","sts8_source212VAuxVoltage","8号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.8","sts8_source25VAuxVoltage","8号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.8","sts8_outputVoltage","8号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.8","sts8_outputCurrent","8号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.8","sts8_outputFrequency","8号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.8","sts8_relay1Status","8号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.8","sts8_relay2Status","8号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.8","sts8_relay3Status","8号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.8","sts8_Communications","8号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["1","14.1.188.9","sts9_systemStatus","9号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","14.1.188.9","sts9_systemSourcePhaseDiff","9号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.9","sts9_systemLoadRatio","9号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.9","sts9_source1Voltage","9号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.9","sts9_source1Frequency","9号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.9","sts9_source112VAuxVoltage","9号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.9","sts9_source15VAuxVoltage","9号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.9","sts9_source2Voltage","9号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.9","sts9_source2Frequency","9号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.9","sts9_source212VAuxVoltage","9号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.9","sts9_source25VAuxVoltage","9号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.9","sts9_outputVoltage","9号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.9","sts9_outputCurrent","9号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.9","sts9_outputFrequency","9号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.9","sts9_relay1Status","9号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.9","sts9_relay2Status","9号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.9","sts9_relay3Status","9号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.9","sts9_Communications","9号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["1","14.1.188.10","sts10_systemStatus","10号STS系统状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","10","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","14.1.188.10","sts10_systemSourcePhaseDiff","10号STS输入源相位差","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","14.1.188.10","sts10_systemLoadRatio","10号STS负载率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.1.3.0","public","0","0","0","0","0","0","0","0","0","%","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","14.1.188.10","sts10_source1Voltage","10号STS源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","14.1.188.10","sts10_source1Frequency","10号STS源1频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","14.1.188.10","sts10_source112VAuxVoltage","10号STS 12伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","14.1.188.10","sts10_source15VAuxVoltage","10号STS 15伏辅助电源1电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.2.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","14.1.188.10","sts10_source2Voltage","10号STS源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","14.1.188.10","sts10_source2Frequency","10号STS源2频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.2.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","14.1.188.10","sts10_source212VAuxVoltage","10号STS 12伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.3.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","14.1.188.10","sts10_source25VAuxVoltage","10号STS 15伏辅助电源2电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.3.4.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","14.1.188.10","sts10_outputVoltage","10号STS输出电压","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.1.0","public","0","0","0","0","0","0","0","0","0","V","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","14.1.188.10","sts10_outputCurrent","10号STS输出电流","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.2.0","public","0","0","0","0","0","0","0","0","0","A","900","0.1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","14.1.188.10","sts10_outputFrequency","10号STS输出频率","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.4.3.0","public","0","0","0","0","0","0","0","0","0","Hz","900","0.01","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","14.1.188.10","sts10_relay1Status","10号STS继电器1状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","14.1.188.10","sts10_relay2Status","10号STS继电器2状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","14.1.188.10","sts10_relay3Status","10号STS继电器3状态","1","0","0","1","0",null,null,"0","60","720","1","1.3.6.1.4.1.13400.2.17.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"900","1","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","14.1.188.10","sts10_Communications","10号STS通信状态","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","38",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]