{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["变量dat文件","CSpreadSheetBackup"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":109,"n_cols":76,"rows_kept":109,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","4.15.27.1","RM_1_BypassVoltPh_A","1号UPS旁路A相电压","4","2","1","3","1",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","4.15.27.1","RM_1_BypassVoltPh_B","1号UPS旁路B相电压","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","4.15.27.1","RM_1_BypassVoltPh_C","1号UPS旁路C相电压","4","2","1","3","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","4.15.27.1","RM_1_BypassCurrPh_A","1号UPS旁路A相电流","4","2","1","3","4",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","4.15.27.1","RM_1_BypassCurrPh_B","1号UPS旁路B相电流","4","2","1","3","5",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","4.15.27.1","RM_1_BypassCurrPh_C","1号UPS旁路C相电流","4","2","1","3","6",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","4.15.27.1","RM_1_BypassFreqPh_A","1号UPS旁路A相频率","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","4.15.27.1","RM_1_BypassFreqPh_B","1号UPS旁路B相频率","4","2","1","3","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","4.15.27.1","RM_1_BypassFreqPh_C","1号UPS旁路C相频率","4","2","1","3","9",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","4.15.27.1","RM_1_InputVoltPh_A","1号UPSA相输入电压","4","2","1","3","13",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","4.15.27.1","RM_1_InputVoltPh_B","1号UPSB相输入电压","4","2","1","3","14",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","4.15.27.1","RM_1_InputVoltPh_C","1号UPSC相输入电压","4","2","1","3","15",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","4.15.27.1","RM_1_InputCurrPh_A","1号UPSA相输入电流","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","4.15.27.1","RM_1_InputCurrPh_B","1号UPSB相输入电流","4","2","1","3","17",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","4.15.27.1","RM_1_InputCurrPh_C","1号UPSC相输入电流","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","4.15.27.1","RM_1_InputFreqPh_A","1号UPSA相输入频率","4","2","1","3","19",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","4.15.27.1","RM_1_InputFreqPh_B","1号UPSB相输入频率","4","2","1","3","20",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","4.15.27.1","RM_1_InputFreqPh_C","1号UPSC相输入频率","4","2","1","3","21",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","4.15.27.1","RM_1_OutputVoltPh_A","1号UPSA相输出电压","4","2","1","3","25",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","4.15.27.1","RM_1_OutputVoltPh_B","1号UPSB相输出电压","4","2","1","3","26",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","4.15.27.1","RM_1_OutputVoltPh_C","1号UPSC相输出电压","4","2","1","3","27",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","4.15.27.1","RM_1_OutputCurrPh_A","1号UPSA相输出电流","4","2","1","3","28",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","4.15.27.1","RM_1_OutputCurrPh_B","1号UPSB相输出电流","4","2","1","3","29",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","4.15.27.1","RM_1_OutputCurrPh_C","1号UPSC相输出电流","4","2","1","3","30",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","4.15.27.1","RM_1_OutputFreqPh_A","1号UPSA相输出频率","4","2","1","3","31",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","4.15.27.1","RM_1_OutputFreqPh_B","1号UPSB相输出频率","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","4.15.27.1","RM_1_OutputFreqPh_C","1号UPSC相输出频率","4","2","1","3","33",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","4.15.27.1","RM_1_OutputKWPh_A","1号UPSA相输出有功功率","4","2","1","3","40",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","kw","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","4.15.27.1","RM_1_OutputKWPh_B","1号UPSB相输出有功功率","4","2","1","3","41",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","kw","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","4.15.27.1","RM_1_OutputKWPh_C","1号UPSC相输出有功功率","4","2","1","3","42",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","kw","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","4.15.27.1","RM_1_OutputLoadPh_A","1号UPSA相输出负载","4","2","1","3","46",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","4.15.27.1","RM_1_OutputLoadPh_B","1号UPSB相输出负载","4","2","1","3","47",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","4.15.27.1","RM_1_OutputLoadPh_C","1号UPSC相输出负载","4","2","1","3","48",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","4.15.27.1","RM_1_EnvTemperature","1号UPS环境温度","4","2","1","3","49",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","4.15.27.1","RM_1_BatteryVoltPositive","1号UPS电池正电压","4","2","1","3","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["36","4.15.27.1","RM_1_BatteryVoltNegative","1号UPS电池负电压","4","2","1","3","51",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["37","4.15.27.1","RM_1_BatteryCurrPositive","1号UPS电池正电流","4","2","1","3","52",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["38","4.15.27.1","RM_1_BatteryCurrNegative","1号UPS电池负电流","4","2","1","3","53",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["39","4.15.27.1","RM_1_BatteryTemperature","1号UPS电池温度","4","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["40","4.15.27.1","RM_1_BatteryRemainTime","1号UPS电池剩余时间","4","2","1","3","55",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Min","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["41","4.15.27.1","RM_1_BatteryCapacity","1号UPS电池电量","4","2","1","3","56",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["42","4.15.27.1","RM_1_LoadOnSource","1号UPS源输出状态","4","2","1","4","81",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","2","1,2,","UPS供电,旁路供电"]
["43","4.15.27.1","RM_1_BatteryStatus","1号UPS电池状态","4","2","1","4","82",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["44","4.15.27.1","RM_1_BatteryConnectStatus","1号UPS电池连接状态","4","2","1","4","83",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","电池未接"]
["45","4.15.27.1","RM_1_GenteratorInput","1号UPS发电机接入状态","4","2","1","4","87",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","发电机未接"]
["46","4.15.27.1","RM_1_InputFail","1号UPS输入故障","4","2","1","4","88",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","故障"]
["47","4.15.27.1","RM_1_BypassVoltFail","1号UPS旁路电压故障","4","2","1","4","90",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","故障"]
["48","4.15.27.1","RM_1_BypassFail","1号UPS旁路故障","4","2","1","4","91",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","故障"]
["49","4.15.27.1","RM_1_BypassOverLoad","1号UPS旁路过载","4","2","1","4","92",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","过载"]
["50","4.15.27.1","RM_1_BypassUntrack","1号UPS旁路不工作","4","2","1","4","94",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","不工作"]
["51","4.15.27.1","RM_1_OutputShorted","1号UPS输出短路","4","2","1","4","96",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","短路"]
["52","4.15.27.1","RM_1_BatteryVoltLow","1号UPS电池低压","4","2","1","4","107",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","低电压"]
["53","4.15.27.1","RM_1_BatteryReverse","1号UPS电池接反","4","2","1","4","108",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","接反"]
["1","4.15.27.1","RM_1_Communications","1号UPS通信状态","1000","0","0","1","0","","","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断开,"]
["1","4.15.27.2","RM_2_BypassVoltPh_A","2号UPS旁路A相电压","4","2","1","3","1",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","4.15.27.2","RM_2_BypassVoltPh_B","2号UPS旁路B相电压","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","4.15.27.2","RM_2_BypassVoltPh_C","2号UPS旁路C相电压","4","2","1","3","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","4.15.27.2","RM_2_BypassCurrPh_A","2号UPS旁路A相电流","4","2","1","3","4",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","4.15.27.2","RM_2_BypassCurrPh_B","2号UPS旁路B相电流","4","2","1","3","5",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","4.15.27.2","RM_2_BypassCurrPh_C","2号UPS旁路C相电流","4","2","1","3","6",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","4.15.27.2","RM_2_BypassFreqPh_A","2号UPS旁路A相频率","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","4.15.27.2","RM_2_BypassFreqPh_B","2号UPS旁路B相频率","4","2","1","3","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","4.15.27.2","RM_2_BypassFreqPh_C","2号UPS旁路C相频率","4","2","1","3","9",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","4.15.27.2","RM_2_InputVoltPh_A","2号UPSA相输入电压","4","2","1","3","13",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","4.15.27.2","RM_2_InputVoltPh_B","2号UPSB相输入电压","4","2","1","3","14",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","4.15.27.2","RM_2_InputVoltPh_C","2号UPSC相输入电压","4","2","1","3","15",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","4.15.27.2","RM_2_InputCurrPh_A","2号UPSA相输入电流","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","4.15.27.2","RM_2_InputCurrPh_B","2号UPSB相输入电流","4","2","1","3","17",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","4.15.27.2","RM_2_InputCurrPh_C","2号UPSC相输入电流","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","4.15.27.2","RM_2_InputFreqPh_A","2号UPSA相输入频率","4","2","1","3","19",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","4.15.27.2","RM_2_InputFreqPh_B","2号UPSB相输入频率","4","2","1","3","20",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","4.15.27.2","RM_2_InputFreqPh_C","2号UPSC相输入频率","4","2","1","3","21",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","4.15.27.2","RM_2_OutputVoltPh_A","2号UPSA相输出电压","4","2","1","3","25",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","4.15.27.2","RM_2_OutputVoltPh_B","2号UPSB相输出电压","4","2","1","3","26",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","4.15.27.2","RM_2_OutputVoltPh_C","2号UPSC相输出电压","4","2","1","3","27",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","4.15.27.2","RM_2_OutputCurrPh_A","2号UPSA相输出电流","4","2","1","3","28",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","4.15.27.2","RM_2_OutputCurrPh_B","2号UPSB相输出电流","4","2","1","3","29",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","4.15.27.2","RM_2_OutputCurrPh_C","2号UPSC相输出电流","4","2","1","3","30",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","4.15.27.2","RM_2_OutputFreqPh_A","2号UPSA相输出频率","4","2","1","3","31",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","4.15.27.2","RM_2_OutputFreqPh_B","2号UPSB相输出频率","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","4.15.27.2","RM_2_OutputFreqPh_C","2号UPSC相输出频率","4","2","1","3","33",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","4.15.27.2","RM_2_OutputKWPh_A","2号UPSA相输出有功功率","4","2","1","3","40",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","kw","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","4.15.27.2","RM_2_OutputKWPh_B","2号UPSB相输出有功功率","4","2","1","3","41",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","kw","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","4.15.27.2","RM_2_OutputKWPh_C","2号UPSC相输出有功功率","4","2","1","3","42",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","kw","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","4.15.27.2","RM_2_OutputLoadPh_A","2号UPSA相输出负载","4","2","1","3","46",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","4.15.27.2","RM_2_OutputLoadPh_B","2号UPSB相输出负载","4","2","1","3","47",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","4.15.27.2","RM_2_OutputLoadPh_C","2号UPSC相输出负载","4","2","1","3","48",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","4.15.27.2","RM_2_EnvTemperature","2号UPS环境温度","4","2","1","3","49",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","4.15.27.2","RM_2_BatteryVoltPositive","2号UPS电池正电压","4","2","1","3","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["36","4.15.27.2","RM_2_BatteryVoltNegative","2号UPS电池负电压","4","2","1","3","51",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["37","4.15.27.2","RM_2_BatteryCurrPositive","2号UPS电池正电流","4","2","1","3","52",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["38","4.15.27.2","RM_2_BatteryCurrNegative","2号UPS电池负电流","4","2","1","3","53",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["39","4.15.27.2","RM_2_BatteryTemperature","2号UPS电池温度","4","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["40","4.15.27.2","RM_2_BatteryRemainTime","2号UPS电池剩余时间","4","2","1","3","55",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Min","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["41","4.15.27.2","RM_2_BatteryCapacity","2号UPS电池电量","4","2","1","3","56",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["42","4.15.27.2","RM_2_LoadOnSource","2号UPS源输出状态","4","2","1","4","81",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","2","1,2,","UPS供电,旁路供电"]
["43","4.15.27.2","RM_2_BatteryStatus","2号UPS电池状态","4","2","1","4","82",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["44","4.15.27.2","RM_2_BatteryConnectStatus","2号UPS电池连接状态","4","2","1","4","83",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","电池未接"]
["45","4.15.27.2","RM_2_GenteratorInput","2号UPS发电机接入状态","4","2","1","4","87",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","发电机未接"]
["46","4.15.27.2","RM_2_InputFail","2号UPS输入故障","4","2","1","4","88",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","故障"]
["47","4.15.27.2","RM_2_BypassVoltFail","2号UPS旁路电压故障","4","2","1","4","90",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","故障"]
["48","4.15.27.2","RM_2_BypassFail","2号UPS旁路故障","4","2","1","4","91",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","故障"]
["49","4.15.27.2","RM_2_BypassOverLoad","2号UPS旁路过载","4","2","1","4","92",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","过载"]
["50","4.15.27.2","RM_2_BypassUntrack","2号UPS旁路不工作","4","2","1","4","94",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","不工作"]
["51","4.15.27.2","RM_2_OutputShorted","2号UPS输出短路","4","2","1","4","96",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","短路"]
["52","4.15.27.2","RM_2_BatteryVoltLow","2号UPS电池低压","4","2","1","4","107",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","低电压"]
["53","4.15.27.2","RM_2_BatteryReverse","2号UPS电池接反","4","2","1","4","108",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","接反"]
["1","4.15.27.2","RM_2_Communications","2号UPS通信状态","1000","0","0","1","0","","","0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","137",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断开,"]

{"sheet":"CSpreadSheetBackup","index":1,"n_rows":109,"n_cols":76,"rows_kept":109,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","4.15.27.1","RM_1_BypassVoltPh_A","1号UPS旁路A相电压","4","2","1","3","1",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","4.15.27.1","RM_1_BypassVoltPh_B","1号UPS旁路B相电压","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","4.15.27.1","RM_1_BypassVoltPh_C","1号UPS旁路C相电压","4","2","1","3","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","4.15.27.1","RM_1_BypassCurrPh_A","1号UPS旁路A相电流","4","2","1","3","4",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","4.15.27.1","RM_1_BypassCurrPh_B","1号UPS旁路B相电流","4","2","1","3","5",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","4.15.27.1","RM_1_BypassCurrPh_C","1号UPS旁路C相电流","4","2","1","3","6",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","4.15.27.1","RM_1_BypassFreqPh_A","1号UPS旁路A相频率","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","4.15.27.1","RM_1_BypassFreqPh_B","1号UPS旁路B相频率","4","2","1","3","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","4.15.27.1","RM_1_BypassFreqPh_C","1号UPS旁路C相频率","4","2","1","3","9",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","4.15.27.1","RM_1_InputVoltPh_A","1号UPSA相输入电压","4","2","1","3","13",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","4.15.27.1","RM_1_InputVoltPh_B","1号UPSB相输入电压","4","2","1","3","14",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","4.15.27.1","RM_1_InputVoltPh_C","1号UPSC相输入电压","4","2","1","3","15",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","4.15.27.1","RM_1_InputCurrPh_A","1号UPSA相输入电流","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","4.15.27.1","RM_1_InputCurrPh_B","1号UPSB相输入电流","4","2","1","3","17",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","4.15.27.1","RM_1_InputCurrPh_C","1号UPSC相输入电流","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","4.15.27.1","RM_1_InputFreqPh_A","1号UPSA相输入频率","4","2","1","3","19",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","4.15.27.1","RM_1_InputFreqPh_B","1号UPSB相输入频率","4","2","1","3","20",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","4.15.27.1","RM_1_InputFreqPh_C","1号UPSC相输入频率","4","2","1","3","21",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","4.15.27.1","RM_1_OutputVoltPh_A","1号UPSA相输出电压","4","2","1","3","25",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","4.15.27.1","RM_1_OutputVoltPh_B","1号UPSB相输出电压","4","2","1","3","26",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","4.15.27.1","RM_1_OutputVoltPh_C","1号UPSC相输出电压","4","2","1","3","27",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","4.15.27.1","RM_1_OutputCurrPh_A","1号UPSA相输出电流","4","2","1","3","28",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","4.15.27.1","RM_1_OutputCurrPh_B","1号UPSB相输出电流","4","2","1","3","29",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","4.15.27.1","RM_1_OutputCurrPh_C","1号UPSC相输出电流","4","2","1","3","30",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","4.15.27.1","RM_1_OutputFreqPh_A","1号UPSA相输出频率","4","2","1","3","31",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","4.15.27.1","RM_1_OutputFreqPh_B","1号UPSB相输出频率","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","4.15.27.1","RM_1_OutputFreqPh_C","1号UPSC相输出频率","4","2","1","3","33",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","4.15.27.1","RM_1_OutputKWPh_A","1号UPSA相输出有功功率","4","2","1","3","40",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","kw","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","4.15.27.1","RM_1_OutputKWPh_B","1号UPSB相输出有功功率","4","2","1","3","41",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","kw","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","4.15.27.1","RM_1_OutputKWPh_C","1号UPSC相输出有功功率","4","2","1","3","42",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","kw","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","4.15.27.1","RM_1_OutputLoadPh_A","1号UPSA相输出负载","4","2","1","3","46",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","4.15.27.1","RM_1_OutputLoadPh_B","1号UPSB相输出负载","4","2","1","3","47",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","4.15.27.1","RM_1_OutputLoadPh_C","1号UPSC相输出负载","4","2","1","3","48",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","4.15.27.1","RM_1_EnvTemperature","1号UPS环境温度","4","2","1","3","49",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","4.15.27.1","RM_1_BatteryVoltPositive","1号UPS电池正电压","4","2","1","3","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["36","4.15.27.1","RM_1_BatteryVoltNegative","1号UPS电池负电压","4","2","1","3","51",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["37","4.15.27.1","RM_1_BatteryCurrPositive","1号UPS电池正电流","4","2","1","3","52",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["38","4.15.27.1","RM_1_BatteryCurrNegative","1号UPS电池负电流","4","2","1","3","53",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["39","4.15.27.1","RM_1_BatteryTemperature","1号UPS电池温度","4","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["40","4.15.27.1","RM_1_BatteryRemainTime","1号UPS电池剩余时间","4","2","1","3","55",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Min","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["41","4.15.27.1","RM_1_BatteryCapacity","1号UPS电池电量","4","2","1","3","56",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["42","4.15.27.1","RM_1_LoadOnSource","1号UPS源输出状态","4","1","1","4","81",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","2","1,2,","UPS供电,旁路供电"]
["43","4.15.27.1","RM_1_BatteryStatus","1号UPS电池状态","4","1","1","4","82",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["44","4.15.27.1","RM_1_BatteryConnectStatus","1号UPS电池连接状态","4","1","1","4","83",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","电池未接"]
["45","4.15.27.1","RM_1_GenteratorInput","1号UPS发电机接入状态","4","1","1","4","87",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","发电机未接"]
["46","4.15.27.1","RM_1_InputFail","1号UPS输入故障","4","1","1","4","88",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","故障"]
["47","4.15.27.1","RM_1_BypassVoltFail","1号UPS旁路电压故障","4","1","1","4","90",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","故障"]
["48","4.15.27.1","RM_1_BypassFail","1号UPS旁路故障","4","1","1","4","91",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","故障"]
["49","4.15.27.1","RM_1_BypassOverLoad","1号UPS旁路过载","4","1","1","4","92",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","过载"]
["50","4.15.27.1","RM_1_BypassUntrack","1号UPS旁路不工作","4","1","1","4","94",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","不工作"]
["51","4.15.27.1","RM_1_OutputShorted","1号UPS输出短路","4","1","1","4","96",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","短路"]
["52","4.15.27.1","RM_1_BatteryVoltLow","1号UPS电池低压","4","1","1","4","107",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","低电压"]
["53","4.15.27.1","RM_1_BatteryReverse","1号UPS电池接反","4","1","1","4","108",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","接反"]
["54","4.15.27.1","RM_1_Communications","1号UPS通信状态","4","1","1","0","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","断开"]
["1","4.15.27.2","RM_2_BypassVoltPh_A","2号UPS旁路A相电压","4","2","1","3","1",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","4.15.27.2","RM_2_BypassVoltPh_B","2号UPS旁路B相电压","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","4.15.27.2","RM_2_BypassVoltPh_C","2号UPS旁路C相电压","4","2","1","3","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","4.15.27.2","RM_2_BypassCurrPh_A","2号UPS旁路A相电流","4","2","1","3","4",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","4.15.27.2","RM_2_BypassCurrPh_B","2号UPS旁路B相电流","4","2","1","3","5",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","4.15.27.2","RM_2_BypassCurrPh_C","2号UPS旁路C相电流","4","2","1","3","6",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","4.15.27.2","RM_2_BypassFreqPh_A","2号UPS旁路A相频率","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","4.15.27.2","RM_2_BypassFreqPh_B","2号UPS旁路B相频率","4","2","1","3","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","4.15.27.2","RM_2_BypassFreqPh_C","2号UPS旁路C相频率","4","2","1","3","9",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","4.15.27.2","RM_2_InputVoltPh_A","2号UPSA相输入电压","4","2","1","3","13",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","4.15.27.2","RM_2_InputVoltPh_B","2号UPSB相输入电压","4","2","1","3","14",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","4.15.27.2","RM_2_InputVoltPh_C","2号UPSC相输入电压","4","2","1","3","15",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","4.15.27.2","RM_2_InputCurrPh_A","2号UPSA相输入电流","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","4.15.27.2","RM_2_InputCurrPh_B","2号UPSB相输入电流","4","2","1","3","17",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","4.15.27.2","RM_2_InputCurrPh_C","2号UPSC相输入电流","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","4.15.27.2","RM_2_InputFreqPh_A","2号UPSA相输入频率","4","2","1","3","19",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","4.15.27.2","RM_2_InputFreqPh_B","2号UPSB相输入频率","4","2","1","3","20",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","4.15.27.2","RM_2_InputFreqPh_C","2号UPSC相输入频率","4","2","1","3","21",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","4.15.27.2","RM_2_OutputVoltPh_A","2号UPSA相输出电压","4","2","1","3","25",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","4.15.27.2","RM_2_OutputVoltPh_B","2号UPSB相输出电压","4","2","1","3","26",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","4.15.27.2","RM_2_OutputVoltPh_C","2号UPSC相输出电压","4","2","1","3","27",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","4.15.27.2","RM_2_OutputCurrPh_A","2号UPSA相输出电流","4","2","1","3","28",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","4.15.27.2","RM_2_OutputCurrPh_B","2号UPSB相输出电流","4","2","1","3","29",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","4.15.27.2","RM_2_OutputCurrPh_C","2号UPSC相输出电流","4","2","1","3","30",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","4.15.27.2","RM_2_OutputFreqPh_A","2号UPSA相输出频率","4","2","1","3","31",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","4.15.27.2","RM_2_OutputFreqPh_B","2号UPSB相输出频率","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","4.15.27.2","RM_2_OutputFreqPh_C","2号UPSC相输出频率","4","2","1","3","33",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","4.15.27.2","RM_2_OutputKWPh_A","2号UPSA相输出有功功率","4","2","1","3","40",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","kw","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","4.15.27.2","RM_2_OutputKWPh_B","2号UPSB相输出有功功率","4","2","1","3","41",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","kw","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","4.15.27.2","RM_2_OutputKWPh_C","2号UPSC相输出有功功率","4","2","1","3","42",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","kw","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","4.15.27.2","RM_2_OutputLoadPh_A","2号UPSA相输出负载","4","2","1","3","46",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","4.15.27.2","RM_2_OutputLoadPh_B","2号UPSB相输出负载","4","2","1","3","47",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","4.15.27.2","RM_2_OutputLoadPh_C","2号UPSC相输出负载","4","2","1","3","48",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","4.15.27.2","RM_2_EnvTemperature","2号UPS环境温度","4","2","1","3","49",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","4.15.27.2","RM_2_BatteryVoltPositive","2号UPS电池正电压","4","2","1","3","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["36","4.15.27.2","RM_2_BatteryVoltNegative","2号UPS电池负电压","4","2","1","3","51",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["37","4.15.27.2","RM_2_BatteryCurrPositive","2号UPS电池正电流","4","2","1","3","52",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["38","4.15.27.2","RM_2_BatteryCurrNegative","2号UPS电池负电流","4","2","1","3","53",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","A","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["39","4.15.27.2","RM_2_BatteryTemperature","2号UPS电池温度","4","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["40","4.15.27.2","RM_2_BatteryRemainTime","2号UPS电池剩余时间","4","2","1","3","55",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Min","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","999999","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["41","4.15.27.2","RM_2_BatteryCapacity","2号UPS电池电量","4","2","1","3","56",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["42","4.15.27.2","RM_2_LoadOnSource","2号UPS源输出状态","4","1","1","4","81",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","2","1,2,","UPS供电,旁路供电"]
["43","4.15.27.2","RM_2_BatteryStatus","2号UPS电池状态","4","1","1","4","82",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["44","4.15.27.2","RM_2_BatteryConnectStatus","2号UPS电池连接状态","4","1","1","4","83",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","电池未接"]
["45","4.15.27.2","RM_2_GenteratorInput","2号UPS发电机接入状态","4","1","1","4","87",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","0,","发电机未接"]
["46","4.15.27.2","RM_2_InputFail","2号UPS输入故障","4","1","1","4","88",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","故障"]
["47","4.15.27.2","RM_2_BypassVoltFail","2号UPS旁路电压故障","4","1","1","4","90",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","故障"]
["48","4.15.27.2","RM_2_BypassFail","2号UPS旁路故障","4","1","1","4","91",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","故障"]
["49","4.15.27.2","RM_2_BypassOverLoad","2号UPS旁路过载","4","1","1","4","92",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","过载"]
["50","4.15.27.2","RM_2_BypassUntrack","2号UPS旁路不工作","4","1","1","4","94",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","不工作"]
["51","4.15.27.2","RM_2_OutputShorted","2号UPS输出短路","4","1","1","4","96",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","短路"]
["52","4.15.27.2","RM_2_BatteryVoltLow","2号UPS电池低压","4","1","1","4","107",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","低电压"]
["53","4.15.27.2","RM_2_BatteryReverse","2号UPS电池接反","4","1","1","4","108",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","接反"]
["54","4.15.27.2","RM_2_Communications","2号UPS通信状态","4","1","1","0","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.000000000","3","0","1","1","0","0","0","0","107",null,null,"0","0","0",{"$nulls":10},"0","0","9","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","断开"]